## Utility Admin (hidden)
The workbook is currently configured for: |  |  | PPL | PPL Electric
Incentive Manager |  |  |  |  | Workbook Headers (Named Range 'Logo') | Report Logos (Named Range 'Report Logo')
Utility | $/kWh | $/kW |  |  | PPL Logo | PPL Logo
PPL | 0.2 | 0 | PPL Electric
PECO | 0.2 | 0 | PECO
First Energy | 0.04 | 250 | FirstEnergy Pennsylvania
Per-Unit Incentive Rates by Utility Client
Utility | Measure | Per Unit Rate
PECO | Smart Thermostats | 15 |  |  | PECO Logo | PECO Logo
PECO | HVAC Tune-Up: < 1 Ton | 60
PECO | HVAC Tune-Up: 1-5 Tons | 75
PECO | HVAC Tune-Up: 5-20 Tons | 1250
FirstEnergy | Smart Thermostats | 50
Incentive Caps
80% | % Total Project Cost
500000 | Total Dollar Amount
[5 empty] | First Energy Logo | First Energy Logo

## Instructions
PPL Electric Estimator for HVAC Measures
Measure Description
This estimator will be used to estimate energy and demand savings for the following HVAC and Building Shell measures
| 1. HVAC Systems: |  | Replacement of Air Cooled, Water Cooled or Evaporatively Cooled ACs, Split and Packaged Terminal Air Conditioners or Heat Pumps, and Air-Source Heat Pumps with higher efficiency units that exceed requirements of 2018 IECC.
| 2. Electric Chillers: |  | Replacement of Air-Cooled and Water-Cooled Chillers with higher efficiency chillers that exceed requirements of 2018 IECC.
| 3. Water-Source or Geothermal Heat Pumps: |  | Installation of Water Source (<65,000 BTU/hr) or Geothermal Heat Pumps (<135,000 BTU/hr), that exceed the efficiency of similarly sized Air Source Heat Pumps (New Construction) or existing Water-Source/Geothermal Heat Pumps.
| 3. Ductless Mini-Split Heat Pumps <5.4 tons: |  | Replacing existing electric resistance, lower efficiency Ductless Heat Pumps, PTHP, PTACs, Central Air conditioning with Ductless Mini-Split Heat Pumps meeting ENERGY STAR Requirements
| 5. Fuel Switching: |  | Replacing Electric Baseboard, electric furnace, PTHPs, or ASHPs <225,000 BTU/hr with Oil Furnace, Gas Furnace or Boiler that meets ENERGY STAR requirements
| 6. Refrigerant Charge Correction: |  | Savings from correcting refrigerant charge for Commercial and Industrial Air Conditioning units or Heat Pumps (< 20 tons capacity)
| 4. Guest Room Occupancy Controls: |  | This measure applies to the installation of control systems in hotel or motel guest rooms which automatically adjust heating/cooling temperature set-points and turn off equipment when guest rooms are unoccupied.
| 7. Room Air Conditioners: |  | Replacing lower efficiency Room Air Conditioners with higher efficiency units that meet ENERGY STAR Requirements
| 5. Air Side Economizers: |  | Savings from installation of dual enthalpy economizers on HVAC systems without an economizer control.
| 10. Ceiling and Wall Insulation: |  | Installation of higher efficiency ceiling and wall insulation.
| 6. High-Volume Low-Speed Fans: |  | This measure applies to the installation of high-volume low-speed (HVLS) circulating fans to replace conventional circulating fans.
The Savings methodologies, constants, default inputs and eligibility requirements for all measures are from Pennsylvania Public Utility Commission, Technical Reference Manual, February 2021 Revision.
Input Instructions
Use the color coded reference cells. Only yellow cells need input.
Requires Input
Doesn't need an Input
Output Cell
Use the Minimum Efficiency Requirements sheet to ensure the installed equipment efficiency exceeds program requirements.
Default values for some constants are provided in dropdown lists in case the actual values cannot be collected.
Refer to the PA TRM 2026 for detailed information on calculations or inputs.
Glossary of Inputs
| Equipment ID | Name of the unit for identification purposes
| Project Type | End of Useful Life or New Construction, Retrofit or Early Replacement
| Project Cost | Total of material and labor cost
| Standard/Non Standard Size | For PTACs and PTHPs: Non-Standard size units are generally for early replacements and are labeled as "Manufactured for nonstandard size applications only: not to be installed in new construction projects". Nonstandard size units have have an external wall opening of less than 16 in. high or less than 42 in. wide and having a cross-sectional area less than 670 in. Standard size units are generally for New Construction projects, and are for standard size wall openings.
| Rated Cooling Capacity (BTU/hr) | BTUcool/hr, Rated cooling capacity of the energy efficient unit
| Rated Heating Capacity (BTU/hr) | Rated heating capacity of the energy efficient unit
| Does the Unit have Electric Resistance Heating? | Yes/No check to see if units have Electric Resistance heat. Baseline efficiency values may change based on this inputs.
| IEER | Integrated energy efficiency ratio of the baseline or efficient unit. For ASHPs and Air cooled Air conditioners > 65,000BTU/hr, and Water cooled and Evaporatively Cooled Air Condtioners
| EER | Energy efficiency ratio of the baseline or efficient unit. For ASHPs and Air cooled Air conditioners < 65,000BTU/hr, this is calculated as 11.3/13* SEER
| SEER | Seasonal energy efficiency ratio of the baseline or efficient unit, for ASHPs and Air cooled Air conditioners < 65,000BTU/hr.
| COP | Coefficient of Performance of the baseline or efficient unit, for ASHPs > 65,000 BTU/hr, PTHPs, and geothermal or water source heat pumps
| HSPF | Heating seasonal performance factor of the baseline or efficient unit, for ASHPs < 65,000 BTU/hr
| CEER | Combined energy efficiency ratio for Room Air Conditioners
| IPLV | Integrated Part Load Value for baseline or efficient unit
| Full Load kW/ton | Design Rated Efficiency for baseline or efficient unit
| Remaining Useful Life (in years) | For Early Replacement projects - based on nameplate age of the unit.
| Motor Size (HP) | Horsepower of retrofit case ground loop pump motor
| Motor Efficiency | Efficiency of ground loop pump motor
| Pump Efficiency | Efficiency of ground loop pump at design point
| % Refrigerant Charge Corrected | % of total refrigerant charge added or removed from the AC unit
| Expansion Valve | Type of Expansion Valve on AC unit - Thermal Expansion (TXV) or Fixed Orifice
| AFUE | Annual Fuel Utilization Efficiency rating of the fossil fuel unit (oil or gas furnace, boiler)
| Blower Motor HP | Horsepower of fossil fuel equipment blower motor
| Blower Motor Efficiency (%) | Efficiency of fossil fuel equipment blower motor
| Area Served (sq.ft.) | Area of conditioned space served by controlled unit (for economizers)
| R-Value | R-value of wall or ceiling
Glossary of Outputs
| Existing Annual kWh Consumption | Calculated Baseline Annual Energy Consumption of the Equipment
| Existing Annual Peak kW | Calculated Baseline Peak Demand of the Equipment
| Proposed Annual kWh Consumption | Calculated Proposed Annual Energy Consumption of the Equipment
| Proposed Annual Peak kW | Calculated Proposed Peak Demand of the Equipment
| Annual kWh Savings | Calculated Annual Energy Savings from the measure
| Annual kWh Savings (%) | Calculated Annual Energy Savings from the measure as a percent of existing consumption
| Peak kW Savings | Calculated Annual Peak Demand Reduction from the measure
| Peak kW Savings (%) | Calculated Annual Peak Demand Reduction from the measure as a percent of existing peak demand
| Incremental Measure Cost | Difference between baseline and proposed costs
| Electric Cost Savings | Annual Electric cost Savings from implementing the measure
| Incentive | Calculated Incentive
Note: This estimator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this estimator is deemed acceptable for the PPL Electric Business Efficiency Program. However, the assumptions used by the applicant to estimate the annual savings will be reviewed by the Program Team, which is solely responsible for the final determination of the annual energy savings to be used in estimating the incentive amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities. For any questions, or assistance using this estimator, please call 1-866-432-5501 or email us at pplbusiness@clearesult.com.

## Methodology (hidden)
Savings Methodologies
HVAC Systems | Ductless Mini-Splits | Nomenclature
Eligibility: New equipment must exceed the efficiency requirements of IECC 2009 and serve comfort cooling purposes only. For one to one replacement of Air Conditioning (includes central AC, air-cooled/water-cooled/evaporatively cooled DX, split systems, and packaged terminal AC) and Air Source and Packaged Terminal Heat Pump Systems. Savings Methodology: | Eligibility: For installation of ENERGY STAR ductless mini split heat pumps replacing an existing electric resistance, a lower-efficiency ductless heat pump system, a ducted heat pump, packaged terminal heat pump (PTHP), electric furnace, or a non-electric fuel-based system. The baseline cooling system could be a standard efficiency heat pump system, central air conditioning system, packaged terminal air conditioner (PTAC), or room air conditioner. The DHP could be a new device in an existing space, a new device in a new space, or could replace an existing heating/cooling device. The DHP systems could be installed as a single-zone system (one indoor unit, one outdoor unit) or a multi-zone system (multiple indoor units, one outdoor unit). Comfort Cooling Applications only. Savings Methodology: | Term | Values
|  | BTUcool/hr, Rated cooling capacity of the energy efficient unit | Nameplate data (AHRI or AHAM)
|  | BTUheat/hr, Rated heating capacity of the energy efficient unit | Nameplate data (AHRI or AHAM)
|  | IEERbase, Integrated energy efficiency ratio of the baseline unit. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | IEERee, Integrated energy efficiency ratio of the energy efficient unit. | Nameplate data (AHRI or AHAM)
|  | EERbase, Energy efficiency ratio of the baseline unit. For air-source AC and ASHP units < 65,000 BTU/hr SEER should be used for cooling savings | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | EERee, Energy efficiency ratio of the energy efficient unit. For air-source AC and ASHP units < 65,000 BTU/hr SEER should be used for cooling savings. | Nameplate data (AHRI or AHAM)
|  | SEERbase, Seasonal energy efficiency ratio of the baseline unit. For units > 65,000 BTU/hr , EER should be used for cooling savings. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | SEERee, Seasonal energy efficiency ratio of the energy efficient unit. For units > 65,000 BTU/hr , EER should be used for cooling savings. | Nameplate data (AHRI or AHAM)
|  | COPbase, Coefficient of performance of the baseline unit. For ASHP units < 65,000BTU/hr , HSPF should be used for heating savings. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | COPee, Coefficient of performance of the efficient unit. For ASHP units < 65,000BTU/hr , HSPF should be used for heating savings. | Nameplate data (AHRI or AHAM)
|  | HSPFbase , Heating seasonal performance factor of the baseline unit. For units > 65,000 BTU/hr, COP should be used for heating savings. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | HSPFee, Heating seasonal performance factor of the energy efficiency unit. For units > 65,000 BTU/hr, COP should be used for heating savings. | Nameplate data (AHRI or AHAM)
|  | CF , Demand Coincidence Factor | EDC Data Gathering. Defaults available.
|  | EFLHcool, Equivalent Full Load Hours for the cooling season – The kWh during the entire operating season divided by the kW at design conditions. | EDC Data Gathering. Defaults available.
|  | EFLHheat, Equivalent Full Load Hours for the heating season – The kWh during the entire operating season divided by the kW at design conditions. | EDC Data Gathering. Defaults available.
|  | Tonsee, The capacity of the chiller at site design conditions accepted by the program | Nameplate data (AHRI or AHAM)
|  | kW/tonbase, Design Rated Efficiency of the baseline chiller. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | kW/tonee, Design Rated Efficiency of the energy efficient chiller from the manufacturer data and equipment ratings in accordance with ARI Standards. | Nameplate data (AHRI or AHAM)
C
Chiller Systems | Refrigerant Charge Correction
Eligibility: New equipment must exceed the efficiency requirements of IECC 2009. Equipment can be installed in a new application or can replace equipment which has failed or which is expected to fail imminently. New equipment must be a single chiller serving a single comfort cooling load. All other chiller applications, including chiller plants having multiple chillers or serving multiple loads, and chillers used for process cooling must submitted as custom. Projects must be submitted as custom if equipment is replacing a different equipment type, if equipment being replaced is fully operational, or if an existing chiller is being retrofit with a variable speed drive. Savings Methodology: | Eligibility: This protocol is applicable for small commercial and industrial customers, and applies to documented tune-ups for package or split systems up to 20 tons. Comfort Cooling applications only. Savings Methodology: | IPLVbase, Integrated Part Load Value of the baseline unit. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | IPLVee, Integrated Part Load Value of the efficient unit. | Nameplate data (AHRI or AHAM)
|  | CFpump, Demand Coincidence Factor for ground source loop pump | If unit runs 24/7/365, CF=1.0; If unit runs only with heat pump unit compressor, defaults available
|  | HPbasemotor, Horsepower of base case ground loop pump motor | Nameplate data
|  | LFbase, Load factor of the base case ground loop pump motor; ratio of the peak running load to the nameplate rating of the pump motor. | Based on spot metering and nameplate. Default = 0.75
|  | , efficiency of base case ground loop pump motor | Nameplate data. If unknown, assume the federal minimum efficiency requirements
|  | , efficiency of base case ground loop pump at design point | Nameplate data. If unknown, assume the federal minimum efficiency requirements
|  | HOURSbasepump, Run hours of base case ground loop pump motor | Based on Logging, BMS data or Modeling. Else EFLHcool + EFLHheat default values
|  | HPeemotor, Horsepower of retrofit case ground loop pump motor | Nameplate data
|  | Lfee , Load factor of the retrofit case ground loop pump motor; Ratio of the peak running load to the nameplate rating of the pump motor. | Based on spot metering and nameplate. Default = 0.75
|  | , efficiency of retrofit case ground loop pump motor | Nameplate data. If unknown, assume the federal minimum efficiency requirements
Insulation |  | , efficiency of retrofit case ground loop pump at design point | Nameplate data. If unknown, assume the federal minimum efficiency requirements
Eligibility: This measure applies to non-residential buildings or common areas in multifamily complexes heated and/or cooled using electricity. Existing construction buildings are required to meet or exceed the code requirement. New construction buildings must exceed the code requirement. Eligibility may vary by PA EDC; savings from chiller-cooled buildings are not included. Savings Methodology: |  | HOURSeepump, Run hours of retrofit case ground loop pump motor | Based on Logging, BMS data or Modeling. Else EFLHcool + EFLHheat default values
|  | CAPYcool, The cooling capacity of the indoor unit, given in Btu/hr as appropriate for the calculation. This protocol is limited to units < 65,000 Btu/hr (5.4 tons) | Nameplate data
|  | CAPYheat, The heating capacity of the indoor unit, given in Btu/hr as appropriate for the calculation. | Nameplate data
|  | HSPFb, Heating Seasonal Performance Factor, heating efficiency of the installed DHP | Varies based on baseline equipment type. Defaults available.
|  | SEERb, Seasonal Energy Efficiency Ratio cooling efficiency of baseline unit | Varies based on baseline equipment type. Defaults available.
|  | HSPFe, Heating Seasonal Performance Factor, heating efficiency of the installed DHP | Nameplate data
|  | SEERe, Seasonal Energy Efficiency Ratio cooling efficiency of the installed DHP | Nameplate data
|  | BTUfuel/hr, Rated heating capacity of the new fossil fuel unit | Nameplate data (AHRI or AHAM)
|  | BTUheat/hr, Rated heating capacity of the existing electric unit | Nameplate data (AHRI or AHAM) - default set to BTUfuel/hr
Ground and Water Source Heat Pumps | ENERGY STAR Room Air Conditioners | AFUEfuel, Annual Fuel Utilization Efficiency rating of the fossil fuel unit | Nameplate data (AHRI or AHAM) - default to ENERGY STAR minimums
Eligibility: New equipment must exceed the efficiency requirements of the IECC 2009. To be eligible, equipment must be of one of the following type and size: • Water source heat pump systems < 65,000 Btu/hr • Ground water source heat pumps < 135,000 Btu/hr • Ground source heat pumps < 135,000 Btu/hr. The new heat pump must be of the same type as the replaced system and must be used for comfort cooling/heating purposes. Heat pump systems coupled with non-heat pump systems such as chillers, rooftop AC units, boilers, or cooling towers must be submitted as custom. Projects must be submitted as custom if equipment is replacing a different equipment type, if equipment is installed in a new application, if equipment being replaced is still operational, or if the heat pump is used for process cooling/heating. Savings Methodology:There are three primary components that must be accounted for in the energy and demand calculations. The first component is the heat pump unit energy and power, the second is the circulating pump in the ground/water loop system energy and power, and the third is the well pump in the ground/water loop system energy and power. For projects where the retrofit system is similar to the baseline system, such as a standard efficiency ground source system replaced with a high efficiency ground source system, the pump energy is expected to be the same for both conditions and does not need to be calculated. The kWh savings should be calculated using the basic equations below. For baseline units rated in both EER and IEER, use IEER in place of EER where listed in energy savings calculations below. | Eligibility: For one to one replacement of standard-efficiency room air conditioners with ENERGY STAR room air conditioners. Comfort cooling applications only. Savings Methodology: | HPmotor, Gas furnace blower motor horsepower | Nameplate data. Default: 1/2HP for furnace
|  | , Efficiency of furnace blower motor | Nameplate data. Default: 0.5 for furnace
|  | RCF, COP Degradation Factor for Cooling | Defaults based on % charge added or removed
|  | CEERbase, EERbase - Efficiency rating of the baseline unit | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | CEERee, EERee - Efficiency rating of the efficient unit | Nameplate data (AHRI or AHAM)
|  | CAPY, Cooling capacity of controlled unit in tons | EDC data gathering
|  | ESF, Energy savings factor | Defaults based on operating hours, location etc.
|  | DSF, Demand savings factor | Defaults based on operating hours, location etc.
|  | SF , Savings factor; Annual cooling load savings per unit area of conditioned space in the building when compared with a baseline HVAC system with no economizer. | 0.002
|  | AREA , Area of conditioned space served by controlled unit | EDC data gathering
|  | FCHr, Free cooling hours with outdoor temperature between 60 F and 70 F. Typical operating hour conditions are defined below with standard climate zones for PA. | Defaults based on location
|  | Eff, Efficiency of existing HVAC equipment. Depending on the size and age, this will either be the SEER, IEER, or EER (use EER only if SEER or IEER are not available) | EDC data gathering. Defaults values from ASHRAE 90.1 - 2007
| Guest Room Occupancy Sensors | HDD, Heating degree days with 65 degree base | Calculated for different PA weather stations in TRM
| Eligibility: For one to one replacement of standard-efficiency room air conditioners with ENERGY STAR room air conditioners. Comfort cooling applications only. Savings Methodology: For hotel and motel guest rooms where manual heating/cooling temperature set-point and fan On/Off/Auto thermostat controls are replaced by energy management thermostats controls of the heating/cooling temperature set-points and operation state based on occupancy modes. | CDD, Cooling degree days with a 65 degree base | Calculated for different PA weather stations in TRM
|  | A_ceiling, Area of the ceiling/attic insulation that was installed | EDC data gathering
|  | A_wall, Area of the wall insulation that was installed | EDC data gathering
|  | Ceiling Ri, the R-value of the ceiling insulation and support structure before the additional insulation is installed | Defaults in TRM for NC buildings, or when existing value is uknown.
|  | Wall Ri, the R-value of the wall insulation and support structure before the additional insulation is installed | Defaults in TRM for NC buildings, or when existing value is uknown.
|  | Ceiling Rf, Total R-value of all ceiling/attic insulation after the additional insulation is installed | EDC data gathering
|  | WallRf, Total R-value of all wall insulation after the additional insulation is installed | EDC data gathering
Economizers
Eligibility: For HVAC equipment with no economizer installed or with a non-functional/disabled economizer. Efficient condition is an HVAC unit with an economizer and dual enthalpy (differential) control. Comfort cooling applications only. Savings Methodology:
Fuel Switching
Eligibility: This protocol excludes water source, ground source, and groundwater source heat pumps. The baseline for this measure is an existing commercial facility with an electric primary heating source. The heating source can be electric baseboards, packaged terminal heat pump (PTHP) units, electric furnace, or electric air source heat pump. The retrofit condition for this measure is the installation of a new standard efficiency natural gas, propane, or oil furnace or boiler. This algorithm does not apply to combination space and water heating units. This protocol applies to measures with input rating of less than 225,000 BTU/hr. Savings Methodology:

## Zip Code Lookup Table (hidden)
ZCTA | Climate Region | Reference Location
15001 | H | Pittsburgh
15003 | H | Pittsburgh
15004 | H | Pittsburgh
15005 | H | Pittsburgh
15006 | H | Pittsburgh
15007 | H | Pittsburgh
15009 | H | Pittsburgh
15010 | H | Pittsburgh
15012 | H | Pittsburgh
15014 | H | Pittsburgh
15015 | H | Pittsburgh
15017 | H | Pittsburgh
15018 | H | Pittsburgh
15019 | H | Pittsburgh
15020 | H | Pittsburgh
15021 | H | Pittsburgh
15022 | H | Pittsburgh
15024 | H | Pittsburgh
15025 | H | Pittsburgh
15026 | H | Pittsburgh
15027 | H | Pittsburgh
15028 | H | Pittsburgh
15030 | H | Pittsburgh
15031 | H | Pittsburgh
15032 | H | Pittsburgh
15033 | H | Pittsburgh
15034 | H | Pittsburgh
15035 | H | Pittsburgh
15036 | H | Pittsburgh
15037 | H | Pittsburgh
15038 | H | Pittsburgh
15042 | H | Pittsburgh
15043 | H | Pittsburgh
15044 | H | Pittsburgh
15045 | H | Pittsburgh
15046 | H | Pittsburgh
15047 | H | Pittsburgh
15049 | H | Pittsburgh
15050 | H | Pittsburgh
15051 | H | Pittsburgh
15052 | H | Pittsburgh
15053 | H | Pittsburgh
15054 | H | Pittsburgh
15055 | H | Pittsburgh
15056 | H | Pittsburgh
15057 | H | Pittsburgh
15059 | H | Pittsburgh
15060 | H | Pittsburgh
15061 | H | Pittsburgh
15062 | H | Pittsburgh
15063 | H | Pittsburgh
15064 | H | Pittsburgh
15065 | H | Pittsburgh
15066 | H | Pittsburgh
15067 | H | Pittsburgh
15068 | H | Pittsburgh
15069 | H | Pittsburgh
15071 | H | Pittsburgh
15072 | H | Pittsburgh
15074 | H | Pittsburgh
15075 | H | Pittsburgh
15076 | H | Pittsburgh
15077 | H | Pittsburgh
15078 | H | Pittsburgh
15081 | H | Pittsburgh
15082 | H | Pittsburgh
15083 | H | Pittsburgh
15084 | H | Pittsburgh
15085 | H | Pittsburgh
15086 | H | Pittsburgh
15087 | H | Pittsburgh
15088 | H | Pittsburgh
15089 | H | Pittsburgh
15090 | H | Pittsburgh
15091 | H | Pittsburgh
15095 | H | Pittsburgh
15096 | H | Pittsburgh
15101 | H | Pittsburgh
15102 | H | Pittsburgh
15104 | H | Pittsburgh
15106 | H | Pittsburgh
15108 | H | Pittsburgh
15110 | H | Pittsburgh
15112 | H | Pittsburgh
15116 | H | Pittsburgh
15120 | H | Pittsburgh
15122 | H | Pittsburgh
15123 | H | Pittsburgh
15126 | H | Pittsburgh
15127 | H | Pittsburgh
15129 | H | Pittsburgh
15130 | H | Pittsburgh
15131 | H | Pittsburgh
15132 | H | Pittsburgh
15133 | H | Pittsburgh
15134 | H | Pittsburgh
15135 | H | Pittsburgh
15136 | H | Pittsburgh
15137 | H | Pittsburgh
15139 | H | Pittsburgh
15140 | H | Pittsburgh
15142 | H | Pittsburgh
15143 | H | Pittsburgh
15144 | H | Pittsburgh
15145 | H | Pittsburgh
15146 | H | Pittsburgh
15147 | H | Pittsburgh
15148 | H | Pittsburgh
15189 | H | Pittsburgh
15201 | H | Pittsburgh
15202 | H | Pittsburgh
15203 | H | Pittsburgh
15204 | H | Pittsburgh
15205 | H | Pittsburgh
15206 | H | Pittsburgh
15207 | H | Pittsburgh
15208 | H | Pittsburgh
15209 | H | Pittsburgh
15210 | H | Pittsburgh
15211 | H | Pittsburgh
15212 | H | Pittsburgh
15213 | H | Pittsburgh
15214 | H | Pittsburgh
15215 | H | Pittsburgh
15216 | H | Pittsburgh
15217 | H | Pittsburgh
15218 | H | Pittsburgh
15219 | H | Pittsburgh
15220 | H | Pittsburgh
15221 | H | Pittsburgh
15222 | H | Pittsburgh
15223 | H | Pittsburgh
15224 | H | Pittsburgh
15225 | H | Pittsburgh
15226 | H | Pittsburgh
15227 | H | Pittsburgh
15228 | H | Pittsburgh
15229 | H | Pittsburgh
15230 | H | Pittsburgh
15231 | H | Pittsburgh
15232 | H | Pittsburgh
15233 | H | Pittsburgh
15234 | H | Pittsburgh
15235 | H | Pittsburgh
15236 | H | Pittsburgh
15237 | H | Pittsburgh
15238 | H | Pittsburgh
15239 | H | Pittsburgh
15240 | H | Pittsburgh
15241 | H | Pittsburgh
15242 | H | Pittsburgh
15243 | H | Pittsburgh
15244 | H | Pittsburgh
15250 | H | Pittsburgh
15251 | H | Pittsburgh
15252 | H | Pittsburgh
15253 | H | Pittsburgh
15254 | H | Pittsburgh
15255 | H | Pittsburgh
15257 | H | Pittsburgh
15258 | H | Pittsburgh
15259 | H | Pittsburgh
15260 | H | Pittsburgh
15261 | H | Pittsburgh
15262 | H | Pittsburgh
15263 | H | Pittsburgh
15264 | H | Pittsburgh
15265 | H | Pittsburgh
15267 | H | Pittsburgh
15268 | H | Pittsburgh
15270 | H | Pittsburgh
15272 | H | Pittsburgh
15274 | H | Pittsburgh
15275 | H | Pittsburgh
15276 | H | Pittsburgh
15277 | H | Pittsburgh
15278 | H | Pittsburgh
15279 | H | Pittsburgh
15281 | H | Pittsburgh
15282 | H | Pittsburgh
15283 | H | Pittsburgh
15285 | H | Pittsburgh
15286 | H | Pittsburgh
15290 | H | Pittsburgh
15295 | H | Pittsburgh
15301 | H | Pittsburgh
15310 | H | Pittsburgh
15311 | H | Pittsburgh
15312 | H | Pittsburgh
15313 | H | Pittsburgh
15314 | H | Pittsburgh
15315 | H | Pittsburgh
15316 | H | Pittsburgh
15317 | H | Pittsburgh
15320 | H | Pittsburgh
15321 | H | Pittsburgh
15322 | H | Pittsburgh
15323 | H | Pittsburgh
15324 | H | Pittsburgh
15325 | H | Pittsburgh
15327 | H | Pittsburgh
15329 | H | Pittsburgh
15330 | H | Pittsburgh
15331 | H | Pittsburgh
15332 | H | Pittsburgh
15333 | H | Pittsburgh
15334 | H | Pittsburgh
15336 | H | Pittsburgh
15337 | H | Pittsburgh
15338 | H | Pittsburgh
15339 | H | Pittsburgh
15340 | H | Pittsburgh
15341 | H | Pittsburgh
15342 | H | Pittsburgh
15344 | H | Pittsburgh
15345 | H | Pittsburgh
15346 | H | Pittsburgh
15347 | H | Pittsburgh
15348 | H | Pittsburgh
15349 | H | Pittsburgh
15350 | H | Pittsburgh
15351 | H | Pittsburgh
15352 | H | Pittsburgh
15353 | H | Pittsburgh
15354 | H | Pittsburgh
15357 | H | Pittsburgh
15358 | H | Pittsburgh
15359 | H | Pittsburgh
15360 | H | Pittsburgh
15361 | H | Pittsburgh
15362 | H | Pittsburgh
15363 | H | Pittsburgh
15364 | H | Pittsburgh
15365 | H | Pittsburgh
15366 | H | Pittsburgh
15367 | H | Pittsburgh
15368 | H | Pittsburgh
15370 | H | Pittsburgh
15376 | H | Pittsburgh
15377 | H | Pittsburgh
15378 | H | Pittsburgh
15379 | H | Pittsburgh
15380 | H | Pittsburgh
15401 | H | Pittsburgh
15410 | H | Pittsburgh
15411 | H | Pittsburgh
15412 | H | Pittsburgh
15413 | H | Pittsburgh
15415 | H | Pittsburgh
15416 | H | Pittsburgh
15417 | H | Pittsburgh
15419 | H | Pittsburgh
15420 | H | Pittsburgh
15421 | H | Pittsburgh
15422 | H | Pittsburgh
15423 | H | Pittsburgh
15424 | H | Pittsburgh
15425 | H | Pittsburgh
15427 | H | Pittsburgh
15428 | H | Pittsburgh
15429 | H | Pittsburgh
15430 | H | Pittsburgh
15431 | H | Pittsburgh
15432 | H | Pittsburgh
15433 | H | Pittsburgh
15434 | H | Pittsburgh
15435 | H | Pittsburgh
15436 | H | Pittsburgh
15437 | H | Pittsburgh
15438 | H | Pittsburgh
15439 | H | Pittsburgh
15440 | H | Pittsburgh
15442 | H | Pittsburgh
15443 | H | Pittsburgh
15444 | H | Pittsburgh
15445 | H | Pittsburgh
15446 | H | Pittsburgh
15447 | H | Pittsburgh
15448 | H | Pittsburgh
15449 | H | Pittsburgh
15450 | H | Pittsburgh
15451 | H | Pittsburgh
15454 | H | Pittsburgh
15455 | H | Pittsburgh
15456 | H | Pittsburgh
15458 | H | Pittsburgh
15459 | H | Pittsburgh
15460 | H | Pittsburgh
15461 | H | Pittsburgh
15462 | H | Pittsburgh
15463 | H | Pittsburgh
15464 | H | Pittsburgh
15465 | H | Pittsburgh
15466 | H | Pittsburgh
15467 | H | Pittsburgh
15468 | H | Pittsburgh
15469 | H | Pittsburgh
15470 | H | Pittsburgh
15472 | H | Pittsburgh
15473 | H | Pittsburgh
15474 | H | Pittsburgh
15475 | H | Pittsburgh
15476 | H | Pittsburgh
15477 | H | Pittsburgh
15478 | H | Pittsburgh
15479 | H | Pittsburgh
15480 | H | Pittsburgh
15482 | H | Pittsburgh
15483 | H | Pittsburgh
15484 | H | Pittsburgh
15485 | H | Pittsburgh
15486 | H | Pittsburgh
15488 | H | Pittsburgh
15489 | H | Pittsburgh
15490 | H | Pittsburgh
15492 | H | Pittsburgh
15501 | H | Pittsburgh
15502 | H | Pittsburgh
15510 | H | Pittsburgh
15520 | H | Pittsburgh
15521 | H | Pittsburgh
15522 | H | Pittsburgh
15530 | H | Pittsburgh
15531 | H | Pittsburgh
15532 | H | Pittsburgh
15533 | H | Pittsburgh
15534 | H | Pittsburgh
15535 | H | Pittsburgh
15536 | E | Harrisburg
15537 | H | Pittsburgh
15538 | H | Pittsburgh
15539 | H | Pittsburgh
15540 | H | Pittsburgh
15541 | H | Pittsburgh
15542 | H | Pittsburgh
15544 | H | Pittsburgh
15545 | H | Pittsburgh
15546 | H | Pittsburgh
15547 | H | Pittsburgh
15548 | H | Pittsburgh
15549 | H | Pittsburgh
15550 | H | Pittsburgh
15551 | H | Pittsburgh
15552 | H | Pittsburgh
15553 | H | Pittsburgh
15554 | H | Pittsburgh
15555 | H | Pittsburgh
15557 | H | Pittsburgh
15558 | H | Pittsburgh
15559 | H | Pittsburgh
15560 | H | Pittsburgh
15561 | H | Pittsburgh
15562 | H | Pittsburgh
15563 | H | Pittsburgh
15564 | H | Pittsburgh
15565 | H | Pittsburgh
15601 | H | Pittsburgh
15605 | H | Pittsburgh
15606 | H | Pittsburgh
15610 | H | Pittsburgh
15611 | H | Pittsburgh
15612 | H | Pittsburgh
15613 | H | Pittsburgh
15615 | H | Pittsburgh
15616 | H | Pittsburgh
15617 | H | Pittsburgh
15618 | H | Pittsburgh
15619 | H | Pittsburgh
15620 | H | Pittsburgh
15621 | H | Pittsburgh
15622 | H | Pittsburgh
15623 | H | Pittsburgh
15624 | H | Pittsburgh
15625 | H | Pittsburgh
15626 | H | Pittsburgh
15627 | H | Pittsburgh
15628 | H | Pittsburgh
15629 | H | Pittsburgh
15631 | H | Pittsburgh
15632 | H | Pittsburgh
15633 | H | Pittsburgh
15634 | H | Pittsburgh
15635 | H | Pittsburgh
15636 | H | Pittsburgh
15637 | H | Pittsburgh
15638 | H | Pittsburgh
15639 | H | Pittsburgh
15640 | H | Pittsburgh
15641 | H | Pittsburgh
15642 | H | Pittsburgh
15644 | H | Pittsburgh
15646 | H | Pittsburgh
15647 | H | Pittsburgh
15650 | H | Pittsburgh
15655 | H | Pittsburgh
15656 | H | Pittsburgh
15658 | H | Pittsburgh
15660 | H | Pittsburgh
15661 | H | Pittsburgh
15662 | H | Pittsburgh
15663 | H | Pittsburgh
15664 | H | Pittsburgh
15665 | H | Pittsburgh
15666 | H | Pittsburgh
15668 | H | Pittsburgh
15670 | H | Pittsburgh
15671 | H | Pittsburgh
15672 | H | Pittsburgh
15673 | H | Pittsburgh
15674 | H | Pittsburgh
15675 | H | Pittsburgh
15676 | H | Pittsburgh
15677 | H | Pittsburgh
15678 | H | Pittsburgh
15679 | H | Pittsburgh
15680 | H | Pittsburgh
15681 | H | Pittsburgh
15682 | H | Pittsburgh
15683 | H | Pittsburgh
15684 | H | Pittsburgh
15685 | H | Pittsburgh
15686 | H | Pittsburgh
15687 | H | Pittsburgh
15688 | H | Pittsburgh
15689 | H | Pittsburgh
15690 | H | Pittsburgh
15691 | H | Pittsburgh
15692 | H | Pittsburgh
15693 | H | Pittsburgh
15695 | H | Pittsburgh
15696 | H | Pittsburgh
15697 | H | Pittsburgh
15698 | H | Pittsburgh
15701 | H | Pittsburgh
15705 | H | Pittsburgh
15710 | H | Pittsburgh
15711 | I | Erie
15712 | H | Pittsburgh
15713 | H | Pittsburgh
15714 | H | Pittsburgh
15715 | I | Erie
15716 | H | Pittsburgh
15717 | H | Pittsburgh
15720 | H | Pittsburgh
15721 | G | Bradford
15722 | H | Pittsburgh
15723 | H | Pittsburgh
15724 | H | Pittsburgh
15725 | H | Pittsburgh
15727 | H | Pittsburgh
15728 | H | Pittsburgh
15729 | H | Pittsburgh
15730 | I | Erie
15731 | H | Pittsburgh
15732 | H | Pittsburgh
15733 | I | Erie
15734 | H | Pittsburgh
15736 | H | Pittsburgh
15737 | H | Pittsburgh
15738 | H | Pittsburgh
15739 | H | Pittsburgh
15740 | I | Erie
15741 | H | Pittsburgh
15742 | H | Pittsburgh
15744 | I | Erie
15745 | H | Pittsburgh
15746 | H | Pittsburgh
15747 | H | Pittsburgh
15748 | H | Pittsburgh
15750 | H | Pittsburgh
15752 | H | Pittsburgh
15753 | G | Bradford
15754 | H | Pittsburgh
15756 | H | Pittsburgh
15757 | G | Bradford
15758 | H | Pittsburgh
15759 | H | Pittsburgh
15760 | H | Pittsburgh
15761 | H | Pittsburgh
15762 | H | Pittsburgh
15763 | H | Pittsburgh
15764 | I | Erie
15765 | H | Pittsburgh
15767 | I | Erie
15770 | I | Erie
15771 | H | Pittsburgh
15772 | H | Pittsburgh
15773 | H | Pittsburgh
15774 | H | Pittsburgh
15775 | H | Pittsburgh
15776 | I | Erie
15777 | H | Pittsburgh
15778 | I | Erie
15779 | H | Pittsburgh
15780 | I | Erie
15781 | I | Erie
15783 | H | Pittsburgh
15784 | I | Erie
15801 | G | Bradford
15821 | G | Bradford
15822 | G | Bradford
15823 | G | Bradford
15824 | I | Erie
15825 | I | Erie
15827 | G | Bradford
15828 | I | Erie
15829 | I | Erie
15831 | G | Bradford
15832 | G | Bradford
15834 | G | Bradford
15840 | I | Erie
15841 | G | Bradford
15845 | G | Bradford
15846 | G | Bradford
15847 | I | Erie
15848 | G | Bradford
15849 | G | Bradford
15851 | I | Erie
15853 | G | Bradford
15856 | G | Bradford
15857 | G | Bradford
15860 | I | Erie
15861 | G | Bradford
15863 | I | Erie
15864 | I | Erie
15865 | I | Erie
15866 | G | Bradford
15868 | G | Bradford
15870 | G | Bradford
15901 | H | Pittsburgh
15902 | H | Pittsburgh
15904 | H | Pittsburgh
15905 | H | Pittsburgh
15906 | H | Pittsburgh
15907 | H | Pittsburgh
15909 | H | Pittsburgh
15915 | H | Pittsburgh
15920 | H | Pittsburgh
15921 | H | Pittsburgh
15922 | H | Pittsburgh
15923 | H | Pittsburgh
15924 | H | Pittsburgh
15925 | H | Pittsburgh
15926 | H | Pittsburgh
15927 | H | Pittsburgh
15928 | H | Pittsburgh
15929 | H | Pittsburgh
15930 | H | Pittsburgh
15931 | H | Pittsburgh
15934 | H | Pittsburgh
15935 | H | Pittsburgh
15936 | H | Pittsburgh
15937 | H | Pittsburgh
15938 | H | Pittsburgh
15940 | H | Pittsburgh
15942 | H | Pittsburgh
15943 | H | Pittsburgh
15944 | H | Pittsburgh
15945 | H | Pittsburgh
15946 | H | Pittsburgh
15948 | H | Pittsburgh
15949 | H | Pittsburgh
15951 | H | Pittsburgh
15952 | H | Pittsburgh
15953 | H | Pittsburgh
15954 | H | Pittsburgh
15955 | H | Pittsburgh
15956 | H | Pittsburgh
15957 | H | Pittsburgh
15958 | H | Pittsburgh
15959 | H | Pittsburgh
15960 | H | Pittsburgh
15961 | H | Pittsburgh
15962 | H | Pittsburgh
15963 | H | Pittsburgh
16001 | H | Pittsburgh
16002 | H | Pittsburgh
16003 | H | Pittsburgh
16016 | H | Pittsburgh
16017 | H | Pittsburgh
16018 | H | Pittsburgh
16020 | H | Pittsburgh
16021 | H | Pittsburgh
16022 | H | Pittsburgh
16023 | H | Pittsburgh
16024 | H | Pittsburgh
16025 | H | Pittsburgh
16027 | H | Pittsburgh
16028 | H | Pittsburgh
16029 | H | Pittsburgh
16030 | H | Pittsburgh
16033 | H | Pittsburgh
16034 | H | Pittsburgh
16035 | H | Pittsburgh
16036 | I | Erie
16037 | H | Pittsburgh
16038 | H | Pittsburgh
16039 | H | Pittsburgh
16040 | H | Pittsburgh
16041 | H | Pittsburgh
16045 | H | Pittsburgh
16046 | H | Pittsburgh
16048 | H | Pittsburgh
16049 | H | Pittsburgh
16050 | H | Pittsburgh
16051 | H | Pittsburgh
16052 | H | Pittsburgh
16053 | H | Pittsburgh
16054 | I | Erie
16055 | H | Pittsburgh
16056 | H | Pittsburgh
16057 | H | Pittsburgh
16058 | H | Pittsburgh
16059 | H | Pittsburgh
16061 | H | Pittsburgh
16063 | H | Pittsburgh
16066 | H | Pittsburgh
16101 | H | Pittsburgh
16102 | H | Pittsburgh
16103 | H | Pittsburgh
16105 | H | Pittsburgh
16107 | H | Pittsburgh
16108 | H | Pittsburgh
16110 | I | Erie
16111 | I | Erie
16112 | H | Pittsburgh
16113 | I | Erie
16114 | I | Erie
16115 | H | Pittsburgh
16116 | H | Pittsburgh
16117 | H | Pittsburgh
16120 | H | Pittsburgh
16121 | I | Erie
16123 | H | Pittsburgh
16124 | I | Erie
16125 | I | Erie
16127 | I | Erie
16130 | I | Erie
16131 | I | Erie
16132 | H | Pittsburgh
16133 | I | Erie
16134 | I | Erie
16136 | H | Pittsburgh
16137 | I | Erie
16140 | H | Pittsburgh
16141 | H | Pittsburgh
16142 | H | Pittsburgh
16143 | H | Pittsburgh
16145 | I | Erie
16146 | I | Erie
16148 | I | Erie
16150 | I | Erie
16151 | I | Erie
16153 | I | Erie
16154 | I | Erie
16155 | H | Pittsburgh
16156 | H | Pittsburgh
16157 | H | Pittsburgh
16159 | I | Erie
16160 | H | Pittsburgh
16161 | I | Erie
16172 | H | Pittsburgh
16201 | H | Pittsburgh
16210 | H | Pittsburgh
16211 | H | Pittsburgh
16212 | H | Pittsburgh
16213 | I | Erie
16214 | I | Erie
16215 | H | Pittsburgh
16217 | I | Erie
16218 | H | Pittsburgh
16220 | I | Erie
16221 | I | Erie
16222 | H | Pittsburgh
16223 | H | Pittsburgh
16224 | I | Erie
16225 | I | Erie
16226 | H | Pittsburgh
16228 | H | Pittsburgh
16229 | H | Pittsburgh
16230 | I | Erie
16232 | I | Erie
16233 | I | Erie
16234 | I | Erie
16235 | I | Erie
16236 | H | Pittsburgh
16238 | H | Pittsburgh
16239 | I | Erie
16240 | I | Erie
16242 | I | Erie
16244 | H | Pittsburgh
16245 | H | Pittsburgh
16246 | H | Pittsburgh
16248 | I | Erie
16249 | H | Pittsburgh
16250 | H | Pittsburgh
16253 | H | Pittsburgh
16254 | I | Erie
16255 | I | Erie
16256 | H | Pittsburgh
16257 | I | Erie
16258 | I | Erie
16259 | H | Pittsburgh
16260 | I | Erie
16261 | H | Pittsburgh
16262 | H | Pittsburgh
16263 | H | Pittsburgh
16301 | I | Erie
16311 | I | Erie
16312 | I | Erie
16313 | I | Erie
16314 | I | Erie
16316 | I | Erie
16317 | I | Erie
16319 | I | Erie
16321 | I | Erie
16322 | I | Erie
16323 | I | Erie
16326 | I | Erie
16327 | I | Erie
16328 | I | Erie
16329 | I | Erie
16331 | I | Erie
16332 | I | Erie
16333 | G | Bradford
16334 | I | Erie
16335 | I | Erie
16340 | I | Erie
16341 | I | Erie
16342 | I | Erie
16343 | I | Erie
16344 | I | Erie
16345 | I | Erie
16346 | I | Erie
16347 | I | Erie
16350 | I | Erie
16351 | I | Erie
16352 | I | Erie
16353 | I | Erie
16354 | I | Erie
16360 | I | Erie
16361 | I | Erie
16362 | I | Erie
16364 | I | Erie
16365 | I | Erie
16366 | I | Erie
16367 | I | Erie
16368 | I | Erie
16369 | I | Erie
16370 | I | Erie
16371 | I | Erie
16372 | I | Erie
16373 | I | Erie
16374 | I | Erie
16375 | I | Erie
16388 | I | Erie
16401 | I | Erie
16402 | I | Erie
16403 | I | Erie
16404 | I | Erie
16405 | I | Erie
16406 | I | Erie
16407 | I | Erie
16410 | I | Erie
16411 | I | Erie
16412 | I | Erie
16413 | I | Erie
16415 | I | Erie
16416 | I | Erie
16417 | I | Erie
16420 | I | Erie
16421 | I | Erie
16422 | I | Erie
16423 | I | Erie
16424 | I | Erie
16426 | I | Erie
16427 | I | Erie
16428 | I | Erie
16430 | I | Erie
16432 | I | Erie
16433 | I | Erie
16434 | I | Erie
16435 | I | Erie
16436 | I | Erie
16438 | I | Erie
16440 | I | Erie
16441 | I | Erie
16442 | I | Erie
16443 | I | Erie
16444 | I | Erie
16475 | I | Erie
16501 | I | Erie
16502 | I | Erie
16503 | I | Erie
16504 | I | Erie
16505 | I | Erie
16506 | I | Erie
16507 | I | Erie
16508 | I | Erie
16509 | I | Erie
16510 | I | Erie
16511 | I | Erie
16512 | I | Erie
16514 | I | Erie
16515 | I | Erie
16522 | I | Erie
16530 | I | Erie
16531 | I | Erie
16532 | I | Erie
16533 | I | Erie
16534 | I | Erie
16538 | I | Erie
16541 | I | Erie
16544 | I | Erie
16546 | I | Erie
16550 | I | Erie
16553 | I | Erie
16554 | I | Erie
16563 | I | Erie
16565 | I | Erie
16601 | H | Pittsburgh
16602 | H | Pittsburgh
16603 | H | Pittsburgh
16611 | F | Williamsport
16613 | H | Pittsburgh
16616 | G | Bradford
16617 | H | Pittsburgh
16619 | H | Pittsburgh
16620 | G | Bradford
16621 | F | Williamsport
16622 | F | Williamsport
16623 | F | Williamsport
16624 | H | Pittsburgh
16625 | H | Pittsburgh
16627 | G | Bradford
16629 | H | Pittsburgh
16630 | H | Pittsburgh
16631 | H | Pittsburgh
16633 | H | Pittsburgh
16634 | F | Williamsport
16635 | H | Pittsburgh
16636 | H | Pittsburgh
16637 | H | Pittsburgh
16638 | F | Williamsport
16639 | H | Pittsburgh
16640 | H | Pittsburgh
16641 | H | Pittsburgh
16644 | H | Pittsburgh
16645 | G | Bradford
16646 | H | Pittsburgh
16647 | F | Williamsport
16648 | H | Pittsburgh
16650 | H | Pittsburgh
16651 | G | Bradford
16652 | F | Williamsport
16654 | F | Williamsport
16655 | H | Pittsburgh
16656 | G | Bradford
16657 | F | Williamsport
16659 | H | Pittsburgh
16660 | H | Pittsburgh
16661 | G | Bradford
16662 | H | Pittsburgh
16663 | G | Bradford
16664 | H | Pittsburgh
16665 | H | Pittsburgh
16666 | G | Bradford
16667 | H | Pittsburgh
16668 | H | Pittsburgh
16669 | F | Williamsport
16670 | H | Pittsburgh
16671 | G | Bradford
16672 | H | Pittsburgh
16673 | H | Pittsburgh
16674 | F | Williamsport
16675 | H | Pittsburgh
16677 | F | Williamsport
16678 | H | Pittsburgh
16679 | H | Pittsburgh
16680 | G | Bradford
16681 | G | Bradford
16682 | H | Pittsburgh
16683 | F | Williamsport
16684 | G | Bradford
16685 | F | Williamsport
16686 | H | Pittsburgh
16689 | E | Harrisburg
16691 | E | Harrisburg
16692 | G | Bradford
16693 | H | Pittsburgh
16694 | F | Williamsport
16695 | H | Pittsburgh
16698 | G | Bradford
16699 | H | Pittsburgh
16701 | G | Bradford
16720 | G | Bradford
16724 | G | Bradford
16725 | G | Bradford
16726 | G | Bradford
16727 | G | Bradford
16728 | G | Bradford
16729 | G | Bradford
16730 | G | Bradford
16731 | G | Bradford
16732 | G | Bradford
16733 | G | Bradford
16734 | G | Bradford
16735 | G | Bradford
16738 | G | Bradford
16740 | G | Bradford
16743 | G | Bradford
16744 | G | Bradford
16745 | G | Bradford
16746 | G | Bradford
16748 | G | Bradford
16749 | G | Bradford
16750 | G | Bradford
16801 | F | Williamsport
16802 | F | Williamsport
16803 | F | Williamsport
16804 | F | Williamsport
16805 | F | Williamsport
16820 | F | Williamsport
16821 | G | Bradford
16822 | F | Williamsport
16823 | F | Williamsport
16825 | G | Bradford
16826 | F | Williamsport
16827 | F | Williamsport
16828 | F | Williamsport
16829 | F | Williamsport
16830 | G | Bradford
16832 | F | Williamsport
16833 | G | Bradford
16834 | G | Bradford
16835 | F | Williamsport
16836 | G | Bradford
16837 | G | Bradford
16838 | G | Bradford
16839 | G | Bradford
16840 | G | Bradford
16841 | F | Williamsport
16843 | G | Bradford
16844 | F | Williamsport
16845 | G | Bradford
16847 | G | Bradford
16848 | F | Williamsport
16849 | G | Bradford
16850 | G | Bradford
16851 | F | Williamsport
16852 | F | Williamsport
16853 | F | Williamsport
16854 | F | Williamsport
16855 | G | Bradford
16856 | G | Bradford
16858 | G | Bradford
16859 | F | Williamsport
16860 | F | Williamsport
16861 | G | Bradford
16863 | G | Bradford
16864 | G | Bradford
16865 | F | Williamsport
16866 | F | Williamsport
16868 | F | Williamsport
16870 | F | Williamsport
16871 | F | Williamsport
16872 | F | Williamsport
16873 | G | Bradford
16874 | F | Williamsport
16875 | F | Williamsport
16876 | G | Bradford
16877 | F | Williamsport
16878 | G | Bradford
16879 | G | Bradford
16881 | G | Bradford
16882 | F | Williamsport
16901 | G | Bradford
16910 | B | Scranton
16911 | G | Bradford
16912 | G | Bradford
16914 | B | Scranton
16915 | G | Bradford
16917 | G | Bradford
16918 | G | Bradford
16920 | G | Bradford
16921 | G | Bradford
16922 | G | Bradford
16923 | G | Bradford
16925 | B | Scranton
16926 | B | Scranton
16927 | G | Bradford
16928 | G | Bradford
16929 | G | Bradford
16930 | G | Bradford
16932 | G | Bradford
16933 | G | Bradford
16935 | G | Bradford
16936 | G | Bradford
16937 | G | Bradford
16938 | G | Bradford
16939 | G | Bradford
16940 | G | Bradford
16941 | G | Bradford
16942 | G | Bradford
16943 | G | Bradford
16945 | B | Scranton
16946 | G | Bradford
16947 | B | Scranton
16948 | G | Bradford
16950 | G | Bradford
17001 | E | Harrisburg
17002 | F | Williamsport
17003 | D | Philadelphia
17004 | F | Williamsport
17005 | F | Williamsport
17006 | F | Williamsport
17007 | E | Harrisburg
17008 | E | Harrisburg
17009 | F | Williamsport
17010 | D | Philadelphia
17011 | E | Harrisburg
17012 | E | Harrisburg
17013 | E | Harrisburg
17014 | F | Williamsport
17015 | E | Harrisburg
17016 | D | Philadelphia
17017 | F | Williamsport
17018 | F | Williamsport
17019 | E | Harrisburg
17020 | F | Williamsport
17021 | F | Williamsport
17022 | D | Philadelphia
17023 | F | Williamsport
17024 | F | Williamsport
17025 | E | Harrisburg
17026 | D | Philadelphia
17027 | E | Harrisburg
17028 | F | Williamsport
17029 | F | Williamsport
17030 | F | Williamsport
17032 | F | Williamsport
17033 | F | Williamsport
17034 | F | Williamsport
17035 | F | Williamsport
17036 | F | Williamsport
17037 | F | Williamsport
17038 | D | Philadelphia
17039 | D | Philadelphia
17040 | F | Williamsport
17041 | D | Philadelphia
17042 | D | Philadelphia
17043 | E | Harrisburg
17044 | F | Williamsport
17045 | F | Williamsport
17046 | D | Philadelphia
17047 | F | Williamsport
17048 | F | Williamsport
17049 | F | Williamsport
17050 | E | Harrisburg
17051 | F | Williamsport
17052 | F | Williamsport
17053 | F | Williamsport
17054 | F | Williamsport
17055 | E | Harrisburg
17056 | F | Williamsport
17057 | F | Williamsport
17058 | F | Williamsport
17059 | F | Williamsport
17060 | F | Williamsport
17061 | F | Williamsport
17062 | F | Williamsport
17063 | F | Williamsport
17064 | D | Philadelphia
17065 | E | Harrisburg
17066 | F | Williamsport
17067 | D | Philadelphia
17068 | F | Williamsport
17069 | F | Williamsport
17070 | E | Harrisburg
17071 | F | Williamsport
17072 | E | Harrisburg
17073 | D | Philadelphia
17074 | F | Williamsport
17075 | F | Williamsport
17076 | F | Williamsport
17077 | D | Philadelphia
17078 | D | Philadelphia
17080 | F | Williamsport
17081 | E | Harrisburg
17082 | F | Williamsport
17083 | D | Philadelphia
17084 | F | Williamsport
17085 | D | Philadelphia
17086 | F | Williamsport
17087 | D | Philadelphia
17088 | D | Philadelphia
17089 | E | Harrisburg
17090 | F | Williamsport
17091 | D | Philadelphia
17093 | E | Harrisburg
17094 | F | Williamsport
17097 | F | Williamsport
17098 | F | Williamsport
17099 | F | Williamsport
17101 | F | Williamsport
17102 | F | Williamsport
17103 | F | Williamsport
17104 | F | Williamsport
17105 | E | Harrisburg
17106 | E | Harrisburg
17107 | E | Harrisburg
17108 | E | Harrisburg
17109 | F | Williamsport
17110 | F | Williamsport
17111 | F | Williamsport
17112 | F | Williamsport
17113 | F | Williamsport
17120 | F | Williamsport
17121 | E | Harrisburg
17122 | E | Harrisburg
17123 | E | Harrisburg
17124 | E | Harrisburg
17125 | E | Harrisburg
17126 | E | Harrisburg
17127 | E | Harrisburg
17128 | E | Harrisburg
17129 | E | Harrisburg
17130 | E | Harrisburg
17140 | E | Harrisburg
17177 | E | Harrisburg
17201 | E | Harrisburg
17202 | E | Harrisburg
17210 | E | Harrisburg
17211 | H | Pittsburgh
17212 | E | Harrisburg
17213 | F | Williamsport
17214 | E | Harrisburg
17215 | E | Harrisburg
17217 | E | Harrisburg
17219 | E | Harrisburg
17220 | E | Harrisburg
17221 | E | Harrisburg
17222 | E | Harrisburg
17223 | E | Harrisburg
17224 | E | Harrisburg
17225 | E | Harrisburg
17228 | E | Harrisburg
17229 | E | Harrisburg
17231 | E | Harrisburg
17232 | E | Harrisburg
17233 | E | Harrisburg
17235 | E | Harrisburg
17236 | E | Harrisburg
17237 | E | Harrisburg
17238 | E | Harrisburg
17239 | F | Williamsport
17240 | E | Harrisburg
17241 | E | Harrisburg
17243 | F | Williamsport
17244 | E | Harrisburg
17246 | E | Harrisburg
17247 | E | Harrisburg
17249 | F | Williamsport
17250 | E | Harrisburg
17251 | E | Harrisburg
17252 | E | Harrisburg
17253 | F | Williamsport
17254 | E | Harrisburg
17255 | F | Williamsport
17256 | E | Harrisburg
17257 | E | Harrisburg
17260 | F | Williamsport
17261 | E | Harrisburg
17262 | E | Harrisburg
17263 | E | Harrisburg
17264 | F | Williamsport
17265 | E | Harrisburg
17266 | E | Harrisburg
17267 | E | Harrisburg
17268 | E | Harrisburg
17270 | E | Harrisburg
17271 | E | Harrisburg
17272 | E | Harrisburg
17301 | E | Harrisburg
17302 | E | Harrisburg
17303 | E | Harrisburg
17304 | E | Harrisburg
17306 | E | Harrisburg
17307 | E | Harrisburg
17309 | E | Harrisburg
17310 | E | Harrisburg
17311 | E | Harrisburg
17312 | E | Harrisburg
17313 | E | Harrisburg
17314 | E | Harrisburg
17315 | E | Harrisburg
17316 | E | Harrisburg
17317 | E | Harrisburg
17318 | E | Harrisburg
17319 | E | Harrisburg
17320 | E | Harrisburg
17321 | E | Harrisburg
17322 | E | Harrisburg
17323 | E | Harrisburg
17324 | E | Harrisburg
17325 | E | Harrisburg
17326 | E | Harrisburg
17327 | E | Harrisburg
17329 | E | Harrisburg
17331 | E | Harrisburg
17332 | E | Harrisburg
17333 | E | Harrisburg
17334 | E | Harrisburg
17337 | E | Harrisburg
17339 | E | Harrisburg
17340 | E | Harrisburg
17342 | E | Harrisburg
17343 | E | Harrisburg
17344 | E | Harrisburg
17345 | E | Harrisburg
17347 | E | Harrisburg
17349 | E | Harrisburg
17350 | E | Harrisburg
17352 | E | Harrisburg
17353 | E | Harrisburg
17354 | E | Harrisburg
17355 | E | Harrisburg
17356 | E | Harrisburg
17358 | E | Harrisburg
17360 | E | Harrisburg
17361 | E | Harrisburg
17362 | E | Harrisburg
17363 | E | Harrisburg
17364 | E | Harrisburg
17365 | E | Harrisburg
17366 | E | Harrisburg
17368 | E | Harrisburg
17370 | E | Harrisburg
17371 | E | Harrisburg
17372 | E | Harrisburg
17375 | E | Harrisburg
17401 | E | Harrisburg
17402 | E | Harrisburg
17403 | E | Harrisburg
17404 | E | Harrisburg
17405 | E | Harrisburg
17406 | E | Harrisburg
17407 | E | Harrisburg
17408 | E | Harrisburg
17415 | E | Harrisburg
17501 | D | Philadelphia
17502 | D | Philadelphia
17503 | D | Philadelphia
17504 | D | Philadelphia
17505 | D | Philadelphia
17506 | D | Philadelphia
17507 | D | Philadelphia
17508 | D | Philadelphia
17509 | D | Philadelphia
17512 | D | Philadelphia
17516 | D | Philadelphia
17517 | D | Philadelphia
17518 | D | Philadelphia
17519 | D | Philadelphia
17520 | D | Philadelphia
17521 | D | Philadelphia
17522 | D | Philadelphia
17527 | D | Philadelphia
17528 | D | Philadelphia
17529 | D | Philadelphia
17532 | D | Philadelphia
17533 | D | Philadelphia
17534 | D | Philadelphia
17535 | D | Philadelphia
17536 | D | Philadelphia
17537 | D | Philadelphia
17538 | D | Philadelphia
17540 | D | Philadelphia
17543 | D | Philadelphia
17545 | D | Philadelphia
17547 | D | Philadelphia
17549 | D | Philadelphia
17550 | D | Philadelphia
17551 | D | Philadelphia
17552 | D | Philadelphia
17554 | D | Philadelphia
17555 | D | Philadelphia
17557 | D | Philadelphia
17560 | D | Philadelphia
17562 | D | Philadelphia
17563 | D | Philadelphia
17564 | D | Philadelphia
17565 | D | Philadelphia
17566 | D | Philadelphia
17567 | D | Philadelphia
17568 | D | Philadelphia
17569 | D | Philadelphia
17570 | D | Philadelphia
17572 | D | Philadelphia
17573 | D | Philadelphia
17575 | D | Philadelphia
17576 | D | Philadelphia
17577 | D | Philadelphia
17578 | D | Philadelphia
17579 | D | Philadelphia
17580 | D | Philadelphia
17581 | D | Philadelphia
17582 | D | Philadelphia
17583 | D | Philadelphia
17584 | D | Philadelphia
17585 | D | Philadelphia
17601 | D | Philadelphia
17602 | D | Philadelphia
17603 | D | Philadelphia
17604 | D | Philadelphia
17605 | D | Philadelphia
17606 | D | Philadelphia
17607 | D | Philadelphia
17608 | D | Philadelphia
17611 | D | Philadelphia
17622 | D | Philadelphia
17699 | D | Philadelphia
17701 | F | Williamsport
17702 | F | Williamsport
17703 | F | Williamsport
17705 | F | Williamsport
17720 | F | Williamsport
17721 | F | Williamsport
17722 | F | Williamsport
17723 | F | Williamsport
17724 | B | Scranton
17726 | F | Williamsport
17727 | F | Williamsport
17728 | F | Williamsport
17729 | F | Williamsport
17730 | F | Williamsport
17731 | B | Scranton
17735 | B | Scranton
17737 | F | Williamsport
17738 | F | Williamsport
17739 | F | Williamsport
17740 | F | Williamsport
17742 | F | Williamsport
17744 | F | Williamsport
17745 | F | Williamsport
17747 | F | Williamsport
17748 | F | Williamsport
17749 | F | Williamsport
17750 | F | Williamsport
17751 | F | Williamsport
17752 | F | Williamsport
17754 | F | Williamsport
17756 | F | Williamsport
17758 | B | Scranton
17759 | F | Williamsport
17760 | F | Williamsport
17762 | F | Williamsport
17763 | F | Williamsport
17764 | F | Williamsport
17765 | G | Bradford
17767 | F | Williamsport
17768 | B | Scranton
17769 | F | Williamsport
17771 | F | Williamsport
17772 | F | Williamsport
17773 | F | Williamsport
17774 | F | Williamsport
17776 | F | Williamsport
17777 | F | Williamsport
17778 | F | Williamsport
17779 | F | Williamsport
17801 | F | Williamsport
17810 | F | Williamsport
17812 | F | Williamsport
17813 | F | Williamsport
17814 | F | Williamsport
17815 | F | Williamsport
17820 | F | Williamsport
17821 | F | Williamsport
17822 | F | Williamsport
17823 | F | Williamsport
17824 | F | Williamsport
17827 | F | Williamsport
17829 | F | Williamsport
17830 | F | Williamsport
17831 | F | Williamsport
17832 | F | Williamsport
17833 | F | Williamsport
17834 | F | Williamsport
17835 | F | Williamsport
17836 | F | Williamsport
17837 | F | Williamsport
17839 | F | Williamsport
17840 | F | Williamsport
17841 | F | Williamsport
17842 | F | Williamsport
17843 | F | Williamsport
17844 | F | Williamsport
17845 | F | Williamsport
17846 | F | Williamsport
17847 | F | Williamsport
17850 | F | Williamsport
17851 | F | Williamsport
17853 | F | Williamsport
17855 | F | Williamsport
17856 | F | Williamsport
17857 | F | Williamsport
17858 | F | Williamsport
17859 | F | Williamsport
17860 | F | Williamsport
17861 | F | Williamsport
17862 | F | Williamsport
17864 | F | Williamsport
17865 | F | Williamsport
17866 | F | Williamsport
17867 | F | Williamsport
17868 | F | Williamsport
17870 | F | Williamsport
17872 | F | Williamsport
17876 | F | Williamsport
17877 | F | Williamsport
17878 | F | Williamsport
17880 | F | Williamsport
17881 | F | Williamsport
17882 | F | Williamsport
17883 | F | Williamsport
17884 | F | Williamsport
17885 | F | Williamsport
17886 | F | Williamsport
17887 | F | Williamsport
17888 | F | Williamsport
17889 | F | Williamsport
17901 | C | Allentown
17920 | F | Williamsport
17921 | C | Allentown
17922 | C | Allentown
17923 | C | Allentown
17925 | C | Allentown
17929 | C | Allentown
17930 | C | Allentown
17931 | C | Allentown
17932 | C | Allentown
17933 | C | Allentown
17934 | C | Allentown
17935 | C | Allentown
17936 | C | Allentown
17938 | C | Allentown
17941 | C | Allentown
17942 | C | Allentown
17943 | C | Allentown
17944 | C | Allentown
17945 | F | Williamsport
17946 | C | Allentown
17948 | C | Allentown
17949 | C | Allentown
17951 | C | Allentown
17952 | C | Allentown
17953 | C | Allentown
17954 | C | Allentown
17957 | C | Allentown
17959 | C | Allentown
17960 | C | Allentown
17961 | C | Allentown
17963 | C | Allentown
17964 | C | Allentown
17965 | C | Allentown
17966 | C | Allentown
17967 | C | Allentown
17968 | C | Allentown
17970 | C | Allentown
17972 | C | Allentown
17974 | C | Allentown
17976 | C | Allentown
17978 | C | Harrisburg
17979 | C | Allentown
17980 | C | Allentown
17981 | C | Allentown
17982 | C | Allentown
17983 | C | Allentown
17985 | C | Allentown
18001 | C | Allentown
18002 | C | Allentown
18003 | C | Allentown
18010 | C | Allentown
18011 | C | Allentown
18012 | C | Allentown
18013 | C | Allentown
18014 | C | Allentown
18015 | C | Allentown
18016 | C | Allentown
18017 | C | Allentown
18018 | C | Allentown
18020 | C | Allentown
18025 | C | Allentown
18030 | C | Allentown
18031 | C | Allentown
18032 | C | Allentown
18034 | C | Allentown
18035 | C | Allentown
18036 | C | Allentown
18037 | C | Allentown
18038 | C | Allentown
18039 | D | Philadelphia
18040 | C | Allentown
18041 | D | Philadelphia
18042 | C | Allentown
18043 | C | Allentown
18044 | C | Allentown
18045 | C | Allentown
18046 | C | Allentown
18049 | C | Allentown
18050 | C | Allentown
18051 | C | Allentown
18052 | C | Allentown
18053 | C | Allentown
18054 | D | Philadelphia
18055 | C | Allentown
18056 | D | Philadelphia
18058 | B | Scranton
18059 | C | Allentown
18060 | C | Allentown
18062 | C | Allentown
18063 | C | Allentown
18064 | C | Allentown
18065 | C | Allentown
18066 | C | Allentown
18067 | C | Allentown
18068 | C | Allentown
18069 | C | Allentown
18070 | D | Philadelphia
18071 | C | Allentown
18072 | C | Allentown
18073 | D | Philadelphia
18074 | D | Philadelphia
18076 | D | Philadelphia
18077 | D | Philadelphia
18078 | C | Allentown
18079 | C | Allentown
18080 | C | Allentown
18081 | D | Philadelphia
18083 | C | Allentown
18084 | D | Philadelphia
18085 | C | Allentown
18086 | C | Allentown
18087 | C | Allentown
18088 | C | Allentown
18091 | C | Allentown
18092 | C | Allentown
18098 | C | Allentown
18099 | C | Allentown
18101 | C | Allentown
18102 | C | Allentown
18103 | C | Allentown
18104 | C | Allentown
18105 | C | Allentown
18106 | C | Allentown
18109 | C | Allentown
18175 | C | Allentown
18195 | C | Allentown
18201 | B | Scranton
18202 | B | Scranton
18210 | C | Allentown
18211 | C | Allentown
18212 | C | Allentown
18214 | C | Allentown
18216 | C | Allentown
18218 | C | Allentown
18219 | B | Scranton
18220 | C | Allentown
18221 | B | Scranton
18222 | B | Scranton
18223 | B | Scranton
18224 | B | Scranton
18225 | B | Scranton
18229 | C | Allentown
18230 | C | Allentown
18231 | C | Allentown
18232 | C | Allentown
18234 | B | Scranton
18235 | C | Allentown
18237 | C | Allentown
18239 | B | Scranton
18240 | C | Allentown
18241 | C | Allentown
18242 | C | Allentown
18244 | C | Allentown
18245 | C | Allentown
18246 | B | Scranton
18247 | B | Scranton
18248 | C | Allentown
18249 | B | Scranton
18250 | C | Allentown
18251 | B | Scranton
18252 | C | Allentown
18254 | C | Allentown
18255 | C | Allentown
18256 | B | Scranton
18301 | B | Scranton
18302 | B | Scranton
18320 | B | Scranton
18321 | B | Scranton
18322 | B | Scranton
18323 | B | Scranton
18324 | B | Scranton
18325 | B | Scranton
18326 | B | Scranton
18327 | B | Scranton
18328 | B | Scranton
18330 | B | Scranton
18331 | B | Scranton
18332 | B | Scranton
18333 | B | Scranton
18334 | B | Scranton
18335 | B | Scranton
18336 | B | Scranton
18337 | B | Scranton
18340 | B | Scranton
18341 | B | Scranton
18342 | B | Scranton
18343 | C | Allentown
18344 | B | Scranton
18346 | B | Scranton
18347 | B | Scranton
18348 | B | Scranton
18349 | B | Scranton
18350 | B | Scranton
18351 | C | Allentown
18352 | B | Scranton
18353 | B | Scranton
18354 | B | Scranton
18355 | B | Scranton
18356 | B | Scranton
18357 | B | Scranton
18360 | B | Scranton
18370 | B | Scranton
18371 | B | Scranton
18372 | B | Scranton
18373 | B | Scranton
18401 | A | Binghamton
18403 | B | Scranton
18405 | A | Binghamton
18407 | B | Scranton
18410 | B | Scranton
18411 | B | Scranton
18413 | A | Binghamton
18414 | B | Scranton
18415 | A | Binghamton
18416 | B | Scranton
18417 | A | Binghamton
18419 | B | Scranton
18420 | B | Scranton
18421 | A | Binghamton
18424 | B | Scranton
18425 | B | Scranton
18426 | B | Scranton
18427 | A | Binghamton
18428 | B | Scranton
18430 | A | Binghamton
18431 | A | Binghamton
18433 | B | Scranton
18434 | B | Scranton
18435 | B | Scranton
18436 | A | Binghamton
18437 | A | Binghamton
18438 | A | Binghamton
18439 | A | Binghamton
18440 | B | Scranton
18441 | A | Binghamton
18443 | A | Binghamton
18444 | B | Scranton
18445 | A | Binghamton
18446 | B | Scranton
18447 | B | Scranton
18448 | B | Scranton
18449 | A | Binghamton
18451 | B | Scranton
18452 | B | Scranton
18453 | A | Binghamton
18454 | B | Scranton
18455 | A | Binghamton
18456 | A | Binghamton
18457 | B | Scranton
18458 | B | Scranton
18459 | A | Binghamton
18460 | A | Binghamton
18461 | A | Binghamton
18462 | A | Binghamton
18463 | A | Binghamton
18464 | B | Scranton
18465 | A | Binghamton
18466 | B | Scranton
18469 | A | Binghamton
18470 | A | Binghamton
18471 | B | Scranton
18472 | A | Binghamton
18473 | A | Binghamton
18501 | B | Scranton
18502 | B | Scranton
18503 | B | Scranton
18504 | B | Scranton
18505 | B | Scranton
18507 | B | Scranton
18508 | B | Scranton
18509 | B | Scranton
18510 | B | Scranton
18512 | B | Scranton
18514 | B | Scranton
18515 | B | Scranton
18517 | B | Scranton
18518 | B | Scranton
18519 | B | Scranton
18522 | B | Scranton
18540 | B | Scranton
18577 | B | Scranton
18601 | B | Scranton
18602 | B | Scranton
18603 | F | Williamsport
18610 | B | Scranton
18611 | B | Scranton
18612 | B | Scranton
18614 | B | Scranton
18615 | B | Scranton
18616 | B | Scranton
18617 | B | Scranton
18618 | B | Scranton
18619 | B | Scranton
18621 | B | Scranton
18622 | B | Scranton
18623 | B | Scranton
18624 | C | Allentown
18625 | B | Scranton
18626 | B | Scranton
18627 | B | Scranton
18628 | B | Scranton
18629 | B | Scranton
18630 | B | Scranton
18631 | F | Williamsport
18632 | B | Scranton
18634 | B | Scranton
18635 | B | Scranton
18636 | B | Scranton
18640 | B | Scranton
18641 | B | Scranton
18642 | B | Scranton
18643 | B | Scranton
18644 | B | Scranton
18651 | B | Scranton
18653 | B | Scranton
18654 | B | Scranton
18655 | B | Scranton
18656 | B | Scranton
18657 | B | Scranton
18660 | B | Scranton
18661 | B | Scranton
18690 | B | Scranton
18701 | B | Scranton
18702 | B | Scranton
18703 | B | Scranton
18704 | B | Scranton
18705 | B | Scranton
18706 | B | Scranton
18707 | B | Scranton
18708 | B | Scranton
18709 | B | Scranton
18710 | B | Scranton
18711 | B | Scranton
18761 | B | Scranton
18762 | B | Scranton
18763 | B | Scranton
18764 | B | Scranton
18765 | B | Scranton
18766 | B | Scranton
18767 | B | Scranton
18768 | B | Scranton
18769 | B | Scranton
18773 | B | Scranton
18774 | B | Scranton
18801 | A | Binghamton
18810 | B | Scranton
18812 | A | Binghamton
18813 | A | Binghamton
18814 | B | Scranton
18815 | B | Scranton
18816 | A | Binghamton
18817 | B | Scranton
18818 | A | Binghamton
18820 | A | Binghamton
18821 | A | Binghamton
18822 | A | Binghamton
18823 | A | Binghamton
18824 | A | Binghamton
18825 | A | Binghamton
18826 | A | Binghamton
18827 | A | Binghamton
18828 | A | Binghamton
18829 | B | Scranton
18830 | A | Binghamton
18831 | B | Scranton
18832 | B | Scranton
18833 | B | Scranton
18834 | A | Binghamton
18837 | B | Scranton
18840 | B | Scranton
18842 | A | Binghamton
18843 | A | Binghamton
18844 | A | Binghamton
18845 | B | Scranton
18846 | B | Scranton
18847 | A | Binghamton
18848 | B | Scranton
18850 | B | Scranton
18851 | B | Scranton
18853 | B | Scranton
18854 | B | Scranton
18901 | D | Philadelphia
18902 | D | Philadelphia
18910 | D | Philadelphia
18911 | D | Philadelphia
18912 | D | Philadelphia
18913 | D | Philadelphia
18914 | D | Philadelphia
18915 | D | Philadelphia
18916 | D | Philadelphia
18917 | D | Philadelphia
18918 | D | Philadelphia
18920 | D | Philadelphia
18921 | D | Philadelphia
18922 | D | Philadelphia
18923 | D | Philadelphia
18924 | D | Philadelphia
18925 | D | Philadelphia
18926 | D | Philadelphia
18927 | D | Philadelphia
18928 | D | Philadelphia
18929 | D | Philadelphia
18930 | D | Philadelphia
18931 | D | Philadelphia
18932 | D | Philadelphia
18933 | D | Philadelphia
18934 | D | Philadelphia
18935 | D | Philadelphia
18936 | D | Philadelphia
18938 | D | Philadelphia
18940 | D | Philadelphia
18942 | D | Philadelphia
18943 | D | Philadelphia
18944 | D | Philadelphia
18946 | D | Philadelphia
18947 | D | Philadelphia
18949 | D | Philadelphia
18950 | D | Philadelphia
18951 | D | Philadelphia
18953 | D | Philadelphia
18954 | D | Philadelphia
18955 | D | Philadelphia
18956 | D | Philadelphia
18957 | D | Philadelphia
18958 | D | Philadelphia
18960 | D | Philadelphia
18962 | D | Philadelphia
18963 | D | Philadelphia
18964 | D | Philadelphia
18966 | D | Philadelphia
18968 | D | Philadelphia
18969 | D | Philadelphia
18970 | D | Philadelphia
18971 | D | Philadelphia
18972 | D | Philadelphia
18974 | D | Philadelphia
18976 | D | Philadelphia
18977 | D | Philadelphia
18979 | D | Philadelphia
18980 | D | Philadelphia
18981 | D | Philadelphia
18991 | D | Philadelphia
19001 | D | Philadelphia
19002 | D | Philadelphia
19003 | D | Philadelphia
19004 | D | Philadelphia
19006 | D | Philadelphia
19007 | D | Philadelphia
19008 | D | Philadelphia
19009 | D | Philadelphia
19010 | D | Philadelphia
19012 | D | Philadelphia
19013 | D | Philadelphia
19014 | D | Philadelphia
19015 | D | Philadelphia
19016 | D | Philadelphia
19017 | D | Philadelphia
19018 | D | Philadelphia
19019 | D | Philadelphia
19020 | D | Philadelphia
19021 | D | Philadelphia
19022 | D | Philadelphia
19023 | D | Philadelphia
19025 | D | Philadelphia
19026 | D | Philadelphia
19027 | D | Philadelphia
19028 | D | Philadelphia
19029 | D | Philadelphia
19030 | D | Philadelphia
19031 | D | Philadelphia
19032 | D | Philadelphia
19033 | D | Philadelphia
19034 | D | Philadelphia
19035 | D | Philadelphia
19036 | D | Philadelphia
19037 | D | Philadelphia
19038 | D | Philadelphia
19039 | D | Philadelphia
19040 | D | Philadelphia
19041 | D | Philadelphia
19043 | D | Philadelphia
19044 | D | Philadelphia
19046 | D | Philadelphia
19047 | D | Philadelphia
19048 | D | Philadelphia
19049 | D | Philadelphia
19050 | D | Philadelphia
19052 | D | Philadelphia
19053 | D | Philadelphia
19054 | D | Philadelphia
19055 | D | Philadelphia
19056 | D | Philadelphia
19057 | D | Philadelphia
19058 | D | Philadelphia
19059 | D | Philadelphia
19060 | D | Philadelphia
19061 | D | Philadelphia
19063 | D | Philadelphia
19064 | D | Philadelphia
19065 | D | Philadelphia
19066 | D | Philadelphia
19067 | D | Philadelphia
19070 | D | Philadelphia
19072 | D | Philadelphia
19073 | D | Philadelphia
19074 | D | Philadelphia
19075 | D | Philadelphia
19076 | D | Philadelphia
19078 | D | Philadelphia
19079 | D | Philadelphia
19080 | D | Philadelphia
19081 | D | Philadelphia
19082 | D | Philadelphia
19083 | D | Philadelphia
19085 | D | Philadelphia
19086 | D | Philadelphia
19087 | D | Philadelphia
19088 | D | Philadelphia
19089 | D | Philadelphia
19090 | D | Philadelphia
19091 | D | Philadelphia
19092 | D | Philadelphia
19093 | D | Philadelphia
19094 | D | Philadelphia
19095 | D | Philadelphia
19096 | D | Philadelphia
19098 | D | Philadelphia
19099 | D | Philadelphia
19101 | D | Philadelphia
19102 | D | Philadelphia
19103 | D | Philadelphia
19104 | D | Philadelphia
19105 | D | Philadelphia
19106 | D | Philadelphia
19107 | D | Philadelphia
19108 | D | Philadelphia
19109 | D | Philadelphia
19110 | D | Philadelphia
19111 | D | Philadelphia
19112 | D | Philadelphia
19113 | D | Philadelphia
19114 | D | Philadelphia
19115 | D | Philadelphia
19116 | D | Philadelphia
19118 | D | Philadelphia
19119 | D | Philadelphia
19120 | D | Philadelphia
19121 | D | Philadelphia
19122 | D | Philadelphia
19123 | D | Philadelphia
19124 | D | Philadelphia
19125 | D | Philadelphia
19126 | D | Philadelphia
19127 | D | Philadelphia
19128 | D | Philadelphia
19129 | D | Philadelphia
19130 | D | Philadelphia
19131 | D | Philadelphia
19132 | D | Philadelphia
19133 | D | Philadelphia
19134 | D | Philadelphia
19135 | D | Philadelphia
19136 | D | Philadelphia
19137 | D | Philadelphia
19138 | D | Philadelphia
19139 | D | Philadelphia
19140 | D | Philadelphia
19141 | D | Philadelphia
19142 | D | Philadelphia
19143 | D | Philadelphia
19144 | D | Philadelphia
19145 | D | Philadelphia
19146 | D | Philadelphia
19147 | D | Philadelphia
19148 | D | Philadelphia
19149 | D | Philadelphia
19150 | D | Philadelphia
19151 | D | Philadelphia
19152 | D | Philadelphia
19153 | D | Philadelphia
19154 | D | Philadelphia
19155 | D | Philadelphia
19160 | D | Philadelphia
19161 | D | Philadelphia
19162 | D | Philadelphia
19170 | D | Philadelphia
19171 | D | Philadelphia
19172 | D | Philadelphia
19173 | D | Philadelphia
19175 | D | Philadelphia
19176 | D | Philadelphia
19177 | D | Philadelphia
19178 | D | Philadelphia
19179 | D | Philadelphia
19181 | D | Philadelphia
19182 | D | Philadelphia
19183 | D | Philadelphia
19184 | D | Philadelphia
19185 | D | Philadelphia
19187 | D | Philadelphia
19188 | D | Philadelphia
19190 | D | Philadelphia
19191 | D | Philadelphia
19192 | D | Philadelphia
19193 | D | Philadelphia
19194 | D | Philadelphia
19195 | D | Philadelphia
19196 | D | Philadelphia
19197 | D | Philadelphia
19244 | D | Philadelphia
19255 | D | Philadelphia
19301 | D | Philadelphia
19310 | D | Philadelphia
19311 | D | Philadelphia
19312 | D | Philadelphia
19316 | D | Philadelphia
19317 | D | Philadelphia
19318 | D | Philadelphia
19319 | D | Philadelphia
19320 | D | Philadelphia
19330 | D | Philadelphia
19331 | D | Philadelphia
19333 | D | Philadelphia
19335 | D | Philadelphia
19339 | D | Philadelphia
19340 | D | Philadelphia
19341 | D | Philadelphia
19342 | D | Philadelphia
19343 | D | Philadelphia
19344 | D | Philadelphia
19345 | D | Philadelphia
19346 | D | Philadelphia
19347 | D | Philadelphia
19348 | D | Philadelphia
19350 | D | Philadelphia
19351 | D | Philadelphia
19352 | D | Philadelphia
19353 | D | Philadelphia
19354 | D | Philadelphia
19355 | D | Philadelphia
19357 | D | Philadelphia
19358 | D | Philadelphia
19360 | D | Philadelphia
19362 | D | Philadelphia
19363 | D | Philadelphia
19365 | D | Philadelphia
19366 | D | Philadelphia
19367 | D | Philadelphia
19369 | D | Philadelphia
19371 | D | Philadelphia
19372 | D | Philadelphia
19373 | D | Philadelphia
19374 | D | Philadelphia
19375 | D | Philadelphia
19376 | D | Philadelphia
19380 | D | Philadelphia
19381 | D | Philadelphia
19382 | D | Philadelphia
19383 | D | Philadelphia
19388 | D | Philadelphia
19390 | D | Philadelphia
19395 | D | Philadelphia
19397 | D | Philadelphia
19398 | D | Philadelphia
19399 | D | Philadelphia
19401 | D | Philadelphia
19403 | D | Philadelphia
19404 | D | Philadelphia
19405 | D | Philadelphia
19406 | D | Philadelphia
19407 | D | Philadelphia
19408 | D | Philadelphia
19409 | D | Philadelphia
19415 | D | Philadelphia
19420 | D | Philadelphia
19421 | D | Philadelphia
19422 | D | Philadelphia
19423 | D | Philadelphia
19424 | D | Philadelphia
19425 | D | Philadelphia
19426 | D | Philadelphia
19428 | D | Philadelphia
19429 | D | Philadelphia
19430 | D | Philadelphia
19432 | D | Philadelphia
19435 | D | Philadelphia
19436 | D | Philadelphia
19437 | D | Philadelphia
19438 | D | Philadelphia
19440 | D | Philadelphia
19441 | D | Philadelphia
19442 | D | Philadelphia
19443 | D | Philadelphia
19444 | D | Philadelphia
19446 | D | Philadelphia
19450 | D | Philadelphia
19451 | D | Philadelphia
19453 | D | Philadelphia
19454 | D | Philadelphia
19455 | D | Philadelphia
19456 | D | Philadelphia
19457 | D | Philadelphia
19460 | D | Philadelphia
19462 | D | Philadelphia
19464 | D | Philadelphia
19465 | D | Philadelphia
19468 | D | Philadelphia
19470 | D | Philadelphia
19472 | D | Philadelphia
19473 | D | Philadelphia
19474 | D | Philadelphia
19475 | D | Philadelphia
19477 | D | Philadelphia
19478 | D | Philadelphia
19480 | D | Philadelphia
19481 | D | Philadelphia
19482 | D | Philadelphia
19483 | D | Philadelphia
19484 | D | Philadelphia
19485 | D | Philadelphia
19486 | D | Philadelphia
19487 | D | Philadelphia
19488 | D | Philadelphia
19489 | D | Philadelphia
19490 | D | Philadelphia
19492 | D | Philadelphia
19493 | D | Philadelphia
19494 | D | Philadelphia
19495 | D | Philadelphia
19496 | D | Philadelphia
19501 | D | Philadelphia
19503 | D | Philadelphia
19504 | D | Philadelphia
19505 | D | Philadelphia
19506 | D | Philadelphia
19507 | D | Philadelphia
19508 | D | Philadelphia
19510 | D | Philadelphia
19511 | D | Philadelphia
19512 | D | Philadelphia
19516 | D | Philadelphia
19518 | D | Philadelphia
19519 | D | Philadelphia
19520 | D | Philadelphia
19522 | D | Philadelphia
19523 | D | Philadelphia
19525 | D | Philadelphia
19526 | D | Philadelphia
19529 | D | Philadelphia
19530 | D | Philadelphia
19533 | D | Philadelphia
19534 | D | Philadelphia
19535 | D | Philadelphia
19536 | D | Philadelphia
19538 | D | Philadelphia
19539 | D | Philadelphia
19540 | D | Philadelphia
19541 | D | Philadelphia
19542 | D | Philadelphia
19543 | D | Philadelphia
19544 | D | Philadelphia
19545 | D | Philadelphia
19547 | D | Philadelphia
19548 | D | Philadelphia
19549 | C | Allentown
19550 | D | Philadelphia
19551 | D | Philadelphia
19554 | D | Philadelphia
19555 | D | Philadelphia
19557 | D | Philadelphia
19559 | D | Philadelphia
19560 | D | Philadelphia
19562 | D | Philadelphia
19564 | D | Philadelphia
19565 | D | Philadelphia
19567 | D | Philadelphia
19601 | D | Philadelphia
19602 | D | Philadelphia
19603 | D | Philadelphia
19604 | D | Philadelphia
19605 | D | Philadelphia
19606 | D | Philadelphia
19607 | D | Philadelphia
19608 | D | Philadelphia
19609 | D | Philadelphia
19610 | D | Philadelphia
19611 | D | Philadelphia
19612 | D | Philadelphia
19640 | D | Philadelphia

## Version Log (hidden)
Version Log
Original Author: |  | Alex Nissley | QA/QC Engineer(s): | Tom Cosgro, Nick Momenee | Current Version: | 5
Primary Developer: |  | Andy Jester | Senior Engineer Approval: | Tom Cosgro | Date: | 2026-06-01
Version | Date | Reason for Change | Change Description | Contact, Department
5 | 2026-06-01 | Phase V Launch

## Measure List (hidden)
Row | Measure | Measure Details | Quantity |  | Project Cost | Energy Savings (kWh) | Demand Savings (kW) | Utility Cost Savings ($) | Incentive ($) | Cost to Customer
2 | Air Source Heat Pumps | Case ID: Heat Pump size: btu(s) | 0 | ASHP | #DIV/0! |  |  | 0 |  | #DIV/0!
3 | Air Source Heat Pumps | Case ID: Heat Pump size: btu(s) | 0 | ASHP | #DIV/0! |  |  | 0 |  | #DIV/0!
4 | Air Source Heat Pumps | Case ID: Heat Pump size: btu(s) | 0 | ASHP | #DIV/0! |  |  | 0 |  | #DIV/0!
5 | Air Source Heat Pumps | Case ID: Heat Pump size: btu(s) | 0 | ASHP | #DIV/0! |  |  | 0 |  | #DIV/0!
6 | Air Source Heat Pumps | Case ID: Heat Pump size: btu(s) | 0 | ASHP | #DIV/0! |  |  | 0 |  | #DIV/0!
7 | Air Source Heat Pumps | Case ID: Heat Pump size: btu(s) | 0 | ASHP | #DIV/0! |  |  | 0 |  | #DIV/0!
8 | Air Source Heat Pumps | Case ID: Heat Pump size: btu(s) | 0 | ASHP | #DIV/0! |  |  | 0 |  | #DIV/0!
9 | Air Source Heat Pumps | Case ID: Heat Pump size: btu(s) | 0 | ASHP | #DIV/0! |  |  | 0 |  | #DIV/0!
10 | Air Source Heat Pumps | Case ID: Heat Pump size: btu(s) | 0 | ASHP | #DIV/0! |  |  | 0 |  | #DIV/0!
11 | Air Source Heat Pumps | Case ID: Heat Pump size: btu(s) | 0 | ASHP | #DIV/0! |  |  | 0 |  | #DIV/0!
12 | Ductless Mini Splits | Case ID: Cooling Capacity: BTU/hr | 0 | Zones | #DIV/0! |  |  | 0 |  | #DIV/0!
13 | Ductless Mini Splits | Case ID: Cooling Capacity: BTU/hr | 0 | Zones | #DIV/0! |  |  | 0 |  | #DIV/0!
14 | Ductless Mini Splits | Case ID: Cooling Capacity: BTU/hr | 0 | Zones | #DIV/0! |  |  | 0 |  | #DIV/0!
15 | Ductless Mini Splits | Case ID: Cooling Capacity: BTU/hr | 0 | Zones | #DIV/0! |  |  | 0 |  | #DIV/0!
16 | Ductless Mini Splits | Case ID: Cooling Capacity: BTU/hr | 0 | Zones | #DIV/0! |  |  | 0 |  | #DIV/0!
17 | Ductless Mini Splits | Case ID: Cooling Capacity: BTU/hr | 0 | Zones | #DIV/0! |  |  | 0 |  | #DIV/0!
18 | Ductless Mini Splits | Case ID: Cooling Capacity: BTU/hr | 0 | Zones | #DIV/0! |  |  | 0 |  | #DIV/0!
19 | Ductless Mini Splits | Case ID: Cooling Capacity: BTU/hr | 0 | Zones | #DIV/0! |  |  | 0 |  | #DIV/0!
20 | Ductless Mini Splits | Case ID: Cooling Capacity: BTU/hr | 0 | Zones | #DIV/0! |  |  | 0 |  | #DIV/0!
21 | Ductless Mini Splits | Case ID: Cooling Capacity: BTU/hr | 0 | Zones | #DIV/0! |  |  | 0 |  | #DIV/0!
22 | Smart Thermostat | Thermostat ID: Thermostat Location: | 0 | thermostats | #DIV/0! |  |  | 0 |  | #DIV/0!
23 | Smart Thermostat | Thermostat ID: Thermostat Location: | 0 | thermostats | #DIV/0! |  |  | 0 |  | #DIV/0!
24 | Smart Thermostat | Thermostat ID: Thermostat Location: | 0 | thermostats | #DIV/0! |  |  | 0 |  | #DIV/0!
25 | Smart Thermostat | Thermostat ID: Thermostat Location: | 0 | thermostats | #DIV/0! |  |  | 0 |  | #DIV/0!
26 | Smart Thermostat | Thermostat ID: Thermostat Location: | 0 | thermostats | #DIV/0! |  |  | 0 |  | #DIV/0!
27 | Smart Thermostat | Thermostat ID: Thermostat Location: | 0 | thermostats | #DIV/0! |  |  | 0 |  | #DIV/0!
28 | Smart Thermostat | Thermostat ID: Thermostat Location: | 0 | thermostats | #DIV/0! |  |  | 0 |  | #DIV/0!
29 | Smart Thermostat | Thermostat ID: Thermostat Location: | 0 | thermostats | #DIV/0! |  |  | 0 |  | #DIV/0!
30 | Smart Thermostat | Thermostat ID: Thermostat Location: | 0 | thermostats | #DIV/0! |  |  | 0 |  | #DIV/0!
31 | Smart Thermostat | Thermostat ID: Thermostat Location: | 0 | thermostats | #DIV/0! |  |  | 0 |  | #DIV/0!
32 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
33 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
34 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
35 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
36 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
37 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
38 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
39 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
40 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
41 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
42 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
43 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
44 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
45 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
46 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
47 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
48 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
49 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
50 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!
51 | HVAC Tune Up | Equipment ID: Cooling Capacity: Equipment Type: | 0 | tune ups | #DIV/0! |  |  | 0 |  | #DIV/0!

## Inputs & Summary
|  |  |  | Version: | 5
|  |  |  | Last Updated: | 2026-06-01 | HIDE
Project Name |  | Measure Name | Savings |  | Incentive | Uncapped Incentive
Installation Date |  |  | kW | kWh
Site Address |  | HVAC Systems | 0 | 0 | 0 | 0
Site Zip Code* |  | Ductless Mini Splits | 0 | 0 | 0 | 0
Building Type* |  | HVAC Tune Up | 0 | 0 | 0 | 0
Total Project Cost* |  | Smart Thermostat | 0 | 0 | 0 | 0
|  | Total | 0 | 0 | 0 | 0
Electricity Consumption Rate [$/kWh]
Electricity Demand Charge [$/kW]
Utility Rate Code* | Small Business (GS1 & GS3 Rate Codes)

## Efficiency Tables (hidden)
Efficiency Tables
yChiller_Type | Path A or Path B | Chiller Capacity (Tons) | yChiller_MinCapacity | yChiller_MaxCapacity | yIPLV_base | ykWperton_base | yChiller_EER_base
Air Cooled Chiller | Path A (Full-Load Optimized Applications) | <150 tons | 0 | 150 | 13.7 |  | 10.1
Air Cooled Chiller | Path A (Full-Load Optimized Applications) | >= 150 tons | 150 | 10000 | 14 |  | 10.1
Water Cooled Chiller: Positive Displacement or Reciprocating | Path A (Full-Load Optimized Applications) | <75 tons | 0 | 75 | 0.6 | 0.75
Water Cooled Chiller: Positive Displacement or Reciprocating | Path A (Full-Load Optimized Applications) | >=75 tons and <150 tons | 75 | 150 | 0.56 | 0.72
Water Cooled Chiller: Positive Displacement or Reciprocating | Path A (Full-Load Optimized Applications) | >=150 tons and <300 tons | 150 | 300 | 0.54 | 0.66
Water Cooled Chiller: Positive Displacement or Reciprocating | Path A (Full-Load Optimized Applications) | >=300 tons and <600 tons | 300 | 600 | 0.52 | 0.61
Water Cooled Chiller: Positive Displacement or Reciprocating | Path A (Full-Load Optimized Applications) | >=600 tons | 600 | 10000 | 0.5 | 0.56
Water Cooled Chiller: Centrifugal | Path A (Full-Load Optimized Applications) | <150 tons | 0 | 150 | 0.55 | 0.61
Water Cooled Chiller: Centrifugal | Path A (Full-Load Optimized Applications) | >=150 tons and <300 tons | 150 | 300 | 0.55 | 0.61
Water Cooled Chiller: Centrifugal | Path A (Full-Load Optimized Applications) | >=300 tons and <400 tons | 300 | 400 | 0.52 | 0.56
Water Cooled Chiller: Centrifugal | Path A (Full-Load Optimized Applications) | >=400 tons and <600 tons | 400 | 600 | 0.5 | 0.56
Water Cooled Chiller: Centrifugal | Path A (Full-Load Optimized Applications) | >=600 tons | 600 | 10000 | 0.5 | 0.56
Air Cooled Chiller | Path B (Part-Load Optimized Applications) | <150 tons | 0 | 150 | 15.8 |  | 9.7
Air Cooled Chiller | Path B (Part-Load Optimized Applications) | >= 150 tons | 150 | 10000 | 16.1 |  | 9.7
Water Cooled Chiller: Positive Displacement or Reciprocating | Path B (Part-Load Optimized Applications) | <75 tons | 0 | 75 | 0.5 | 0.78
Water Cooled Chiller: Positive Displacement or Reciprocating | Path B (Part-Load Optimized Applications) | >=75 tons and <150 tons | 75 | 150 | 0.49 | 0.75 |  |  |  | AC units will <65,000 Btu/h will index single package efficiencies from the yHVAC_Type table Split System is selected on HVAC systems tab. Split system efficiencies are on the table below.
Water Cooled Chiller: Positive Displacement or Reciprocating | Path B (Part-Load Optimized Applications) | >=150 tons and <300 tons | 150 | 300 | 0.44 | 0.68
Water Cooled Chiller: Positive Displacement or Reciprocating | Path B (Part-Load Optimized Applications) | >=300 tons and <600 tons | 300 | 600 | 0.41 | 0.625
Water Cooled Chiller: Positive Displacement or Reciprocating | Path B (Part-Load Optimized Applications) | >=600 tons | 600 | 10000 | 0.38 | 0.585
Water Cooled Chiller: Centrifugal | Path B (Part-Load Optimized Applications) | <150 tons | 0 | 150 | 0.44 | 0.695
Water Cooled Chiller: Centrifugal | Path B (Part-Load Optimized Applications) | >=150 tons and <300 tons | 150 | 300 | 0.4 | 0.635
Water Cooled Chiller: Centrifugal | Path B (Part-Load Optimized Applications) | >=300 tons and <400 tons | 300 | 400 | 0.39 | 0.595
Water Cooled Chiller: Centrifugal | Path B (Part-Load Optimized Applications) | >=400 tons and <600 tons | 400 | 600 | 0.38 | 0.585
Water Cooled Chiller: Centrifugal | Path B (Part-Load Optimized Applications) | >=600 tons | 600 | 10000 | 0.38 | 0.585
yHVAC_Type | yER_Existence | Installed Rated Cooling Capacity (Btu/hr) | yHVAC_MinCapacity | yHVAC_MaxCapacity | yIEER_base | yEER_base | ySEER2_base | yCOP_base | yHSPF2_base |  | yEER2_base | ySEER2_base | yHSPF2_base
Air-Source Air Conditioners | Yes | <65,000 BTU/hr | 0 | 65000 |  | 11.6477 | 13.4 |  |  | Split AC <65000 | 11.6477 | 13.4
Air-Source Air Conditioners | Yes | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 14.8 | 11.7 |  |  |  | Split HP <65000 | 12.43 | 14.3 | 7.5 | 12.9 | 11.2 | 1.9 | 0.5 | 0
Air-Source Air Conditioners | Yes | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 14.2 | 11.4 | [7 empty] | 12.4 | 11 | 1.8 | 0.4 | 0
Air-Source Air Conditioners | Yes | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 13.2 | 10.4 | [7 empty] | 11.6 | 10 | 1.6 | 0.4 | 0
Air-Source Air Conditioners | Yes | >= 760,000 Btu/hr | 760000 | 100000000 | 12.5 | 9.7 | [7 empty] | 11.2 | 9.7 | 1.3 | 0 | 0
Air-Source Air Conditioners | No | <65,000 BTU/hr | 0 | 65000 |  | 11.6477 | 13.4 | [7 empty] | 12.1692 | 0 | -0.52154 | 13.4
Air-Source Air Conditioners | No | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 14.6 | 11.5 | [7 empty] | 12.7 | 11 | 1.9 | 0.5 | 0
Air-Source Air Conditioners | No | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 14 | 11.2 | [7 empty] | 12.2 | 10.8 | 1.8 | 0.4 | 0
Air-Source Air Conditioners | No | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 13 | 10.2 | [7 empty] | 11.4 | 9.8 | 1.6 | 0.4 | 0
Air-Source Air Conditioners | No | >= 760,000 Btu/hr | 760000 | 100000000 | 12.3 | 9.5 | [7 empty] | 11 | 9.5 | 1.3 | 0 | 0
Air-Source Heat Pumps | Yes | <65,000 BTU/hr | 0 | 65000 |  | 11.6477 | 13.4 |  | 6.7 | [5 empty] | 12.1692 | 0 | -0.52154 | 13.4
Air-Source Heat Pumps | Yes | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 14.1 |  |  | 3.4 | [5 empty] | 12.2 | 11 | 1.9 | -11 | 0
Air-Source Heat Pumps | Yes | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 13.5 |  |  | 3.3 | [5 empty] | 11.6 | 10.6 | 1.9 | -10.6 | 0
Air-Source Heat Pumps | Yes | >= 240,000 Btu/hr | 240000 | 100000000 | 12.5 |  |  | 3.2 | [5 empty] | 10.6 | 9.5 | 1.9 | -9.5 | 0
Air-Source Heat Pumps | No | <65,000 BTU/hr | 0 | 65000 |  | 11.6477 | 13.4 |  | 6.7 | [5 empty] | 12.1692 | 0 | -0.52154 | 13.4
Air-Source Heat Pumps | No | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 13.9 |  |  | 3.4 | [5 empty] | 12 | 10.8 | 1.9 | -10.8 | 0
Air-Source Heat Pumps | No | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 13.3 |  |  | 3.3 | [5 empty] | 11.4 | 10.4 | 1.9 | -10.4 | 0
Air-Source Heat Pumps | No | >= 240,000 Btu/hr | 240000 | 100000000 | 12.3 |  |  | 3.2 | [5 empty] | 10.4 | 9.3 | 1.9 | -9.3 | 0
Water-Cooled Air Conditioners | Yes | < 65,000 Btu/hr | 0 | 65000 | 12.3 | 12.1 | [7 empty] | 12.3 | 12.1 | 0 | 0 | 0
Water-Cooled Air Conditioners | Yes | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 13.9 | 12.1 | [7 empty] | 13.9 | 12.1 | 0 | 0 | 0
Water-Cooled Air Conditioners | Yes | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 13.9 | 12.5 | [7 empty] | 13.9 | 12.5 | 0 | 0 | 0
Water-Cooled Air Conditioners | Yes | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 13.6 | 12.4 | [7 empty] | 13.6 | 12.4 | 0 | 0 | 0
Water-Cooled Air Conditioners | Yes | >= 760,000 Btu/hr | 760000 | 100000000 | 13.5 | 12.2 | [7 empty] | 13.5 | 12.2 | 0 | 0 | 0
Water-Cooled Air Conditioners | No | < 65,000 Btu/hr | 0 | 65000 | 12.3 | 11.9 | [7 empty] | 12.3 | 12.1 | 0 | -0.2 | 0
Water-Cooled Air Conditioners | No | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 13.7 | 11.9 | [7 empty] | 13.7 | 11.9 | 0 | 0 | 0
Water-Cooled Air Conditioners | No | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 13.7 | 12.3 | [7 empty] | 13.7 | 12.3 | 0 | 0 | 0
Water-Cooled Air Conditioners | No | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 13.4 | 12.2 | [7 empty] | 13.4 | 12.2 | 0 | 0 | 0
Water-Cooled Air Conditioners | No | >= 760,000 Btu/hr | 760000 | 100000000 | 13.3 | 12 | [7 empty] | 13.3 | 12 | 0 | 0 | 0
Evaporatively-Cooled Air Conditioners | Yes | < 65,000 Btu/hr | 0 | 65000 | 12.3 | 12.1 | [7 empty] | 12.3 | 12.1 | 0 | 0 | 0
Evaporatively-Cooled Air Conditioners | Yes | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 12.3 | 12.1 | [7 empty] | 12.3 | 12.1 | 0 | 0 | 0
Evaporatively-Cooled Air Conditioners | Yes | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 12.2 | 12 | [7 empty] | 12.2 | 12 | 0 | 0 | 0
Evaporatively-Cooled Air Conditioners | Yes | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 12.1 | 11.9 | [7 empty] | 12.1 | 11.9 | 0 | 0 | 0
Evaporatively-Cooled Air Conditioners | Yes | >= 760,000 Btu/hr | 760000 | 100000000 | 11.9 | 11.7 | [7 empty] | 11.9 | 11.7 | 0 | 0 | 0
Evaporatively-Cooled Air Conditioners | No | < 65,000 Btu/hr | 0 | 65000 | 12.3 | 11.9 | [7 empty] | 12.3 | 12.1 | 0 | -0.2 | 0
Evaporatively-Cooled Air Conditioners | No | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 12.1 | 11.9 | [7 empty] | 12.1 | 11.9 | 0 | 0 | 0
Evaporatively-Cooled Air Conditioners | No | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 12 | 11.8 | [7 empty] | 12 | 11.8 | 0 | 0 | 0
Evaporatively-Cooled Air Conditioners | No | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 11.9 | 11.7 | [7 empty] | 11.9 | 11.7 | 0 | 0 | 0
Evaporatively-Cooled Air Conditioners | No | >= 760,000 Btu/hr | 760000 | 100000000 | 11.7 | 11.5 | [7 empty] | 11.7 | 11.5 | 0 | 0 | 0
PTAC/PTHP | Std/Non-Std | yEER_PT_a | yEER_PT_b | yCOP_PT_a | yCOP_PT_b
PTAC | Non-Standard | 10.9 | 0.213 | NA | NA
PTAC | Standard | 14 | 0.3 | NA | NA
PTHP | Non-Standard | 10.8 | 0.213 | 2.9 | 0.026
PTHP | Standard | 14 | 0.3 | 3.7 | 0.052
DHP Heating Baseline | yHSPF_DHPbase
DHP / Split System ASHP | 7.5
Single Package ASHP | 6.7
Electric Resistance | 2.9
Electric Furnace | 2.7
New Space/No existing heat/Non-electric Heat | 2.9
DHP Cooling Baseline | ySEER2_DHPbase | ySEER_DHPbase
DHP / Split System ASHP | 14.3
Single Package ASHP | 13.4
Room Air Conditoner | 11.4359 | 11.4
New Space/No existing cooling | 11.4359 | 11.4
|  | Installed Capacity | Min | Max | COP | HSPF2
Air-Source Heat Pumps |  | <65,000 BTU/hr | 0 | 65000 | NA | 6.7
Air-Source Heat Pumps |  | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 3.4
Air-Source Heat Pumps |  | >= 135,000 Btu/hr | 135000 | 100000000 | 3.3
Electric Furnace/Baseboard Heating |  | All Sizes |  |  | 1
|  | All Sizes |  |  | 1
yGeothermal_EqptType | yER_Existence | Installed Rated Cooling Capacity (Btu/hr) | yHVAC_MinCapacity | yHVAC_MaxCapacity | yIEER_base | yEER_base | ySEER2_base | yCOP_base | yHSPF2_base
Groundwater Source Heat Pumps: Water-to-Air | Yes | <135,000 BTU/hr | 0 | 135000 |  | 18 |  | 3.7
Ground Source Heat Pumps: Brine-to-Air | Yes | <135,000 BTU/hr | 0 | 135000 |  | 14.1 |  | 3.2
Groundwater Source Heat Pumps: Water-to-Water | Yes | <135,000 BTU/hr | 0 | 135000 |  | 16.3 |  | 3.1
Ground Source Heat Pumps: Brine-to-Water | Yes | <135,000 BTU/hr | 0 | 135000 |  | 12.1 |  | 2.5
Groundwater Source Heat Pumps: Water-to-Air | No | <135,000 BTU/hr | 0 | 135000 |  | 18 |  | 3.7
Ground Source Heat Pumps: Brine-to-Air | No | <135,000 BTU/hr | 0 | 135000 |  | 14.1 |  | 3.2
Groundwater Source Heat Pumps: Water-to-Water | No | <135,000 BTU/hr | 0 | 135000 |  | 16.3 |  | 3.1
Ground Source Heat Pumps: Brine-to-Water | No | <135,000 BTU/hr | 0 | 135000 |  | 12.1 |  | 2.5
Air-Source Heat Pumps | Yes | <65,000 BTU/hr | 0 | 65000 |  |  | 13.4 |  | 6.7
Air-Source Heat Pumps | Yes | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 14.1 |  |  | 3.4
Air-Source Heat Pumps | Yes | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 13.5 |  |  | 3.3
Air-Source Heat Pumps | Yes | >= 240,000 Btu/hr and <760,000 Btu/hr | 240000 | 760000 | 12.5 |  |  | 3.2
Air-Source Heat Pumps | No | <65,000 BTU/hr | 0 | 65000 |  |  | 13.4 |  | 6.7
Air-Source Heat Pumps | No | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 13.9 |  |  | 3.4
Air-Source Heat Pumps | No | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 13.3 |  |  | 3.3
Air-Source Heat Pumps | No | >= 240,000 Btu/hr and <760,000 Btu/hr | 240000 | 760000 | 12.3 |  |  | 3.2
Equipment Type | yLouver_Existence | Installed Rated Cooling Capacity (Btu/hr) | yHVAC_MinCapacity | yHVAC_MaxCapacity | yCEER_base
Room Air Conditioners | With Louvered Sides | < 6,000 | 0 | 6000 | 13.1
Room Air Conditioners | With Louvered Sides | ≥ 6,000 and <8,000 | 6000 | 8000 | 13.7
Room Air Conditioners | With Louvered Sides | ≥ 8,000 and < 11,000 | 8000 | 11000 | 16
Room Air Conditioners | With Louvered Sides | ≥ 11,000 and < 14,000 | 11000 | 14000 | 16
Room Air Conditioners | With Louvered Sides | ≥ 14,000 and < 20,000 | 14000 | 20000 | 16
Room Air Conditioners | With Louvered Sides | ≥ 20,000 and < 28,000 | 20000 | 28000 | 13.8
Room Air Conditioners | With Louvered Sides | ≥ 28,000 | 28000 | 1000000 | 13.2
Room Air Conditioners | Without Louvered Sides | < 6,000 | 0 | 6000 | 12.8
Room Air Conditioners | Without Louvered Sides | ≥ 6,000 and <8,000 | 6000 | 8000 | 12.8
Room Air Conditioners | Without Louvered Sides | ≥ 8,000 and < 11,000 | 8000 | 11000 | 14.1
Room Air Conditioners | Without Louvered Sides | ≥ 11,000 and < 14,000 | 11000 | 14000 | 13.9
Room Air Conditioners | Without Louvered Sides | ≥ 14,000 and < 20,000 | 14000 | 20000 | 13.7
Room Air Conditioners | Without Louvered Sides | ≥ 20,000 and < 28,000 | 20000 | 28000 | 13.8
Room Air Conditioners | Without Louvered Sides | ≥ 28,000 | 28000 | 1000000 | 13.8
Reverse-Cycle Room Air Conditioners | With Louvered Sides | < 20,000 | 0 | 20000 | 14.4
Reverse-Cycle Room Air Conditioners | With Louvered Sides | ≥ 20,000 | 20000 | 1000000 | 13.7
Reverse-Cycle Room Air Conditioners | Without Louvered Sides | < 14,000 | 0 | 14000 | 13.7
Reverse-Cycle Room Air Conditioners | Without Louvered Sides | ≥ 14,000 | 14000 | 1000000 | 12.8
Casement-Only Room Air Conditioners |  | All Sizes | 0 | 1000000 | 13.9
Casement-Slider Room Air Conditioners |  | All Sizes | 0 | 1000000 | 15.3
Equipment Type | yAFUE
Gas Furnace | 95%
Oil Furnace | 85%
Gas/Propane Steam Boiler | 90%
Gas/Propane Hot Water Boiler | 90%
Oil Steam Boiler | 87%
Oil Hot Water Boiler | 87%
Equipment Type | Mounting Type | yUpflow/Downflow | yHVAC_MinCapacity | yHVAC_MaxCapacity | SCOP
Air-Cooled | Floor-Mounted | Upflow Ducted | 0 | 80000 | 2.67
Air-Cooled | Floor-Mounted | Upflow Ducted | 80000 | 295000 | 2.55
Air-Cooled | Floor-Mounted | Upflow Ducted | 295000 | 930000 | 2.33
Air-Cooled | Floor-Mounted | Downflow | 0 | 80000 | 2.7
Air-Cooled | Floor-Mounted | Downflow | 80000 | 295000 | 2.58
Air-Cooled | Floor-Mounted | Downflow | 295000 | 930000 | 2.36
Air-Cooled with Fluid Economizer | Floor-Mounted | Upflow Ducted | 0 | 80000 | 2.67
Air-Cooled with Fluid Economizer | Floor-Mounted | Upflow Ducted | 80000 | 295000 | 2.55
Air-Cooled with Fluid Economizer | Floor-Mounted | Upflow Ducted | 295000 | 930000 | 2.33
Air-Cooled with Fluid Economizer | Floor-Mounted | Downflow | 0 | 80000 | 2.7
Air-Cooled with Fluid Economizer | Floor-Mounted | Downflow | 80000 | 295000 | 2.58
Air-Cooled with Fluid Economizer | Floor-Mounted | Downflow | 295000 | 930000 | 2.36
Water-Cooled | Floor-Mounted | Upflow Ducted | 0 | 80000 | 2.79
Water-Cooled | Floor-Mounted | Upflow Ducted | 80000 | 295000 | 2.7
Water-Cooled | Floor-Mounted | Upflow Ducted | 295000 | 930000 | 2.64
Water-Cooled | Floor-Mounted | Downflow | 0 | 80000 | 2.82
Water-Cooled | Floor-Mounted | Downflow | 80000 | 295000 | 2.73
Water-Cooled | Floor-Mounted | Downflow | 295000 | 930000 | 2.67
Water-Cooled with Fluid Economizer | Floor-Mounted | Upflow Ducted | 0 | 80000 | 2.74
Water-Cooled with Fluid Economizer | Floor-Mounted | Upflow Ducted | 80000 | 295000 | 2.65
Water-Cooled with Fluid Economizer | Floor-Mounted | Upflow Ducted | 295000 | 930000 | 2.58
Water-Cooled with Fluid Economizer | Floor-Mounted | Downflow | 0 | 80000 | 2.77
Water-Cooled with Fluid Economizer | Floor-Mounted | Downflow | 80000 | 295000 | 2.68
Water-Cooled with Fluid Economizer | Floor-Mounted | Downflow | 295000 | 930000 | 2.61
Glycol-Cooled | Floor-Mounted | Upflow Ducted | 0 | 80000 | 2.53
Glycol-Cooled | Floor-Mounted | Upflow Ducted | 80000 | 295000 | 2.21
Glycol-Cooled | Floor-Mounted | Upflow Ducted | 295000 | 930000 | 2.18
Glycol-Cooled | Floor-Mounted | Downflow | 0 | 80000 | 2.56
Glycol-Cooled | Floor-Mounted | Downflow | 80000 | 295000 | 2.24
Glycol-Cooled | Floor-Mounted | Downflow | 295000 | 930000 | 2.21
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Upflow Ducted | 0 | 80000 | 2.48
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Upflow Ducted | 80000 | 295000 | 2.16
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Upflow Ducted | 295000 | 930000 | 2.12
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Downflow | 0 | 80000 | 2.51
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Downflow | 80000 | 295000 | 2.19
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Downflow | 295000 | 930000 | 2.15
Air-Cooled | Floor-Mounted | Upflow Non-Ducted | 0 | 65000 | 2.16
Air-Cooled | Floor-Mounted | Upflow Non-Ducted | 65000 | 240000 | 2.04
Air-Cooled | Floor-Mounted | Upflow Non-Ducted | 240000 | 760000 | 1.89
Air-Cooled | Floor-Mounted | Horizontal Flow | 0 | 65000 | 2.65
Air-Cooled | Floor-Mounted | Horizontal Flow | 65000 | 240000 | 2.55
Air-Cooled | Floor-Mounted | Horizontal Flow | 240000 | 760000 | 2.47
Air-Cooled with Fluid Economizer | Floor-Mounted | Upflow Non-Ducted | 0 | 65000 | 2.09
Air-Cooled with Fluid Economizer | Floor-Mounted | Upflow Non-Ducted | 65000 | 240000 | 1.99
Air-Cooled with Fluid Economizer | Floor-Mounted | Upflow Non-Ducted | 240000 | 760000 | 1.81
Air-Cooled with Fluid Economizer | Floor-Mounted | Horizontal Flow | 0 | 65000 | 2.65
Air-Cooled with Fluid Economizer | Floor-Mounted | Horizontal Flow | 65000 | 240000 | 2.55
Air-Cooled with Fluid Economizer | Floor-Mounted | Horizontal Flow | 240000 | 760000 | 2.47
Water-Cooled | Floor-Mounted | Upflow Non-Ducted | 0 | 65000 | 2.43
Water-Cooled | Floor-Mounted | Upflow Non-Ducted | 65000 | 240000 | 2.32
Water-Cooled | Floor-Mounted | Upflow Non-Ducted | 240000 | 760000 | 2.2
Water-Cooled | Floor-Mounted | Horizontal Flow | 0 | 65000 | 2.79
Water-Cooled | Floor-Mounted | Horizontal Flow | 65000 | 240000 | 2.68
Water-Cooled | Floor-Mounted | Horizontal Flow | 240000 | 760000 | 2.6
Water-Cooled with Fluid Economizer | Floor-Mounted | Upflow Non-Ducted | 0 | 65000 | 2.35
Water-Cooled with Fluid Economizer | Floor-Mounted | Upflow Non-Ducted | 65000 | 240000 | 2.24
Water-Cooled with Fluid Economizer | Floor-Mounted | Upflow Non-Ducted | 240000 | 760000 | 2.12
Water-Cooled with Fluid Economizer | Floor-Mounted | Horizontal Flow | 0 | 65000 | 2.71
Water-Cooled with Fluid Economizer | Floor-Mounted | Horizontal Flow | 65000 | 240000 | 2.6
Water-Cooled with Fluid Economizer | Floor-Mounted | Horizontal Flow | 240000 | 760000 | 2.54
Glycol-Cooled | Floor-Mounted | Upflow Non-Ducted | 0 | 65000 | 2.08
Glycol-Cooled | Floor-Mounted | Upflow Non-Ducted | 65000 | 240000 | 1.9
Glycol-Cooled | Floor-Mounted | Upflow Non-Ducted | 240000 | 760000 | 1.81
Glycol-Cooled | Floor-Mounted | Horizontal Flow | 0 | 65000 | 2.48
Glycol-Cooled | Floor-Mounted | Horizontal Flow | 65000 | 240000 | 2.18
Glycol-Cooled | Floor-Mounted | Horizontal Flow | 240000 | 760000 | 2.18
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Upflow Non-Ducted | 0 | 65000 | 2
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Upflow Non-Ducted | 65000 | 240000 | 1.82
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Upflow Non-Ducted | 240000 | 760000 | 1.73
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Horizontal Flow | 0 | 65000 | 2.44
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Horizontal Flow | 65000 | 240000 | 2.1
Glycol-Cooled with Fluid Economizer | Floor-Mounted | Horizontal Flow | 240000 | 760000 | 2.1
Air-Cooled with Free Air Discharge Condenser | Ceiling-Mounted | Upflow Ducted | 0 | 29000 | 2.05
Air-Cooled with Free Air Discharge Condenser | Ceiling-Mounted | Upflow Ducted | 29000 | 65000 | 2.02
Air-Cooled with Free Air Discharge Condenser | Ceiling-Mounted | Upflow Ducted | 65000 | 760000 | 1.92
Air-Cooled with Free Air Discharge Condenser | Ceiling-Mounted | Upflow Non-Ducted | 0 | 29000 | 2.08
Air-Cooled with Free Air Discharge Condenser | Ceiling-Mounted | Upflow Non-Ducted | 29000 | 65000 | 2.05
Air-Cooled with Free Air Discharge Condenser | Ceiling-Mounted | Upflow Non-Ducted | 65000 | 760000 | 1.94
Air-Cooled with Free Air Discharge Condenser and Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 0 | 29000 | 2.01
Air-Cooled with Free Air Discharge Condenser and Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 29000 | 65000 | 1.97
Air-Cooled with Free Air Discharge Condenser and Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 65000 | 760000 | 1.87
Air-Cooled with Free Air Discharge Condenser and Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 0 | 29000 | 2.04
Air-Cooled with Free Air Discharge Condenser and Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 29000 | 65000 | 2
Air-Cooled with Free Air Discharge Condenser and Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 65000 | 760000 | 1.89
Air-Cooled with Ducted Condenser | Ceiling-Mounted | Upflow Ducted | 0 | 29000 | 1.86
Air-Cooled with Ducted Condenser | Ceiling-Mounted | Upflow Ducted | 29000 | 65000 | 1.83
Air-Cooled with Ducted Condenser | Ceiling-Mounted | Upflow Ducted | 65000 | 760000 | 1.73
Air-Cooled with Ducted Condenser | Ceiling-Mounted | Upflow Non-Ducted | 0 | 29000 | 1.89
Air-Cooled with Ducted Condenser | Ceiling-Mounted | Upflow Non-Ducted | 29000 | 65000 | 1.86
Air-Cooled with Ducted Condenser | Ceiling-Mounted | Upflow Non-Ducted | 65000 | 760000 | 1.75
Air-Cooled with Fluid Economizer and Ducted Condenser | Ceiling-Mounted | Upflow Ducted | 0 | 29000 | 1.82
Air-Cooled with Fluid Economizer and Ducted Condenser | Ceiling-Mounted | Upflow Ducted | 29000 | 65000 | 1.78
Air-Cooled with Fluid Economizer and Ducted Condenser | Ceiling-Mounted | Upflow Ducted | 65000 | 760000 | 1.68
Air-Cooled with Fluid Economizer and Ducted Condenser | Ceiling-Mounted | Upflow Non-Ducted | 0 | 29000 | 1.85
Air-Cooled with Fluid Economizer and Ducted Condenser | Ceiling-Mounted | Upflow Non-Ducted | 29000 | 65000 | 1.81
Air-Cooled with Fluid Economizer and Ducted Condenser | Ceiling-Mounted | Upflow Non-Ducted | 65000 | 760000 | 1.7
Water-Cooled | Ceiling-Mounted | Upflow Ducted | 0 | 29000 | 2.38
Water-Cooled | Ceiling-Mounted | Upflow Ducted | 29000 | 65000 | 2.28
Water-Cooled | Ceiling-Mounted | Upflow Ducted | 65000 | 760000 | 2.18
Water-Cooled | Ceiling-Mounted | Upflow Non-Ducted | 0 | 29000 | 2.41
Water-Cooled | Ceiling-Mounted | Upflow Non-Ducted | 29000 | 65000 | 2.31
Water-Cooled | Ceiling-Mounted | Upflow Non-Ducted | 65000 | 760000 | 2.2
Water-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 0 | 29000 | 2.33
Water-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 29000 | 65000 | 2.23
Water-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 65000 | 760000 | 2.13
Water-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 0 | 29000 | 2.36
Water-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 29000 | 65000 | 2.26
Water-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 65000 | 760000 | 2.16
Glycol-Cooled | Ceiling-Mounted | Upflow Ducted | 0 | 29000 | 1.97
Glycol-Cooled | Ceiling-Mounted | Upflow Ducted | 29000 | 65000 | 1.93
Glycol-Cooled | Ceiling-Mounted | Upflow Ducted | 65000 | 760000 | 1.78
Glycol-Cooled | Ceiling-Mounted | Upflow Non-Ducted | 0 | 29000 | 2
Glycol-Cooled | Ceiling-Mounted | Upflow Non-Ducted | 29000 | 65000 | 1.98
Glycol-Cooled | Ceiling-Mounted | Upflow Non-Ducted | 65000 | 760000 | 1.81
Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 0 | 29000 | 1.92
Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 29000 | 65000 | 1.88
Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 65000 | 760000 | 1.73
Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 0 | 29000 | 1.95
Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 29000 | 65000 | 1.93
Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 65000 | 760000 | 1.76
High Volume Low Speed Fans | [5 empty] | High Volume Low Speed Fans
Fan Size (ft) | Watts (HVLS) | Watts (Conventional) | Wconv-WHVLS |  |  | Fan Size (ft) | Effee
≥ 8 and < 10 | 377 | 2227 | 1850 |  |  | ≥ 8 and < 10 | 116
≥ 10 and < 12 | 471 | 2784 | 2313 |  |  | ≥ 10 and < 12 | 144
≥ 12 and < 14 | 565 | 3341 | 2776 |  |  | ≥ 12 and < 14 | 152
≥ 14 and < 16 | 659 | 3898 | 3239 |  |  | ≥ 14 and < 16 | 165
≥ 16 and < 18 | 761 | 4497 | 3736 |  |  | ≥ 16 and < 18 | 206
≥ 18 and < 20 | 850 | 5026 | 4176 |  |  | ≥ 18 and < 20 | 230
≥ 20 and < 24 | 940 | 5555 | 4615 |  |  | ≥ 20 and < 24 | 257
≥ 24 | 1119 | 6613 | 5494 |  |  | ≥ 24 | 169
Smart Thermostat Tables
Baseline | Cooling ESF | Heating ESF
Manual | 6.9% | 6.5%
Conventional Programmable | 4.9% | 4.5%
Unknown | 6.2% | 5.8%
Equipment type | EER2 | SEER2 | HSPF2
Central AC | 11.1 | 13.2 | N/A
Air-Source Heat Pumps | 11.7 | 14.3 | 7.5
Groundwater Source Heat Pumps: Water-to-Air | 18 | N/A | 12.6
Ground Source Heat Pumps: Brine-to-Air | 14.1 | N/A | 10.9
Groundwater Source Heat Pumps: Water-to-Water | 16.3 | N/A | 10.6
Ground Source Heat Pumps: Brine-to-Water | 12.1 | N/A | 8.5
HVAC Tune Up
Tune-Up Component | ESF
Condenser Cleaning | 0.061
Evaporator Cleaning | 0.0022
Refrigerant Charge Correction (<=20%) | 0.0068
Refrigerant Charge Correction (>20%) | 0.0844
Condenser Cleaning, Evaporator Cleaning, Ref Charge Correction (<=20%) | 0.07
Condenser Cleaning, Evaporator Cleaning, Ref Charge Correction (>20%) | 0.1476
3-78: Duct Cooling Distribution Efficiency
Duct total leakage (%) | Duct system R-value | Restaurant | Retail | Other
2% | Uninsulated | 0.862 | 0.836 | 0.832
3% | Uninsulated | 0.86 | 0.835 | 0.831
4% | Uninsulated | 0.859 | 0.835 | 0.83
5% | Uninsulated | 0.857 | 0.834 | 0.828
6% | Uninsulated | 0.855 | 0.833 | 0.827
7% | Uninsulated | 0.854 | 0.832 | 0.826
8% | Uninsulated | 0.852 | 0.832 | 0.825
9% | Uninsulated | 0.851 | 0.831 | 0.823
10% | Uninsulated | 0.849 | 0.83 | 0.822
11% | Uninsulated | 0.847 | 0.83 | 0.821
12% | Uninsulated | 0.846 | 0.829 | 0.82
13% | Uninsulated | 0.844 | 0.828 | 0.818
14% | Uninsulated | 0.843 | 0.827 | 0.817
15% | Uninsulated | 0.841 | 0.827 | 0.816
16% | Uninsulated | 0.839 | 0.826 | 0.815
17% | Uninsulated | 0.838 | 0.825 | 0.813
18% | Uninsulated | 0.836 | 0.825 | 0.812
19% | Uninsulated | 0.835 | 0.824 | 0.811
20% | Uninsulated | 0.833 | 0.823 | 0.81
21% | Uninsulated | 0.831 | 0.822 | 0.808
22% | Uninsulated | 0.83 | 0.822 | 0.807
23% | Uninsulated | 0.828 | 0.821 | 0.806
24% | Uninsulated | 0.827 | 0.82 | 0.805
25% | Uninsulated | 0.825 | 0.82 | 0.803
26% | Uninsulated | 0.823 | 0.819 | 0.802
27% | Uninsulated | 0.822 | 0.818 | 0.801
28% | Uninsulated | 0.82 | 0.817 | 0.8
29% | Uninsulated | 0.819 | 0.817 | 0.798
30% | Uninsulated | 0.817 | 0.816 | 0.797
2% | R-6 | 0.965 | 0.97 | 0.943
3% | R-6 | 0.962 | 0.969 | 0.941
4% | R-6 | 0.96 | 0.968 | 0.939
5% | R-6 | 0.957 | 0.967 | 0.937
6% | R-6 | 0.954 | 0.966 | 0.936
7% | R-6 | 0.952 | 0.965 | 0.934
8% | R-6 | 0.949 | 0.964 | 0.932
9% | R-6 | 0.947 | 0.963 | 0.932
10% | R-6 | 0.944 | 0.961 | 0.928
11% | R-6 | 0.942 | 0.96 | 0.927
12% | R-6 | 0.939 | 0.959 | 0.925
13% | R-6 | 0.937 | 0.958 | 0.923
14% | R-6 | 0.934 | 0.957 | 0.921
15% | R-6 | 0.932 | 0.956 | 0.919
16% | R-6 | 0.929 | 0.955 | 0.917
17% | R-6 | 0.927 | 0.954 | 0.914
18% | R-6 | 0.924 | 0.953 | 0.913
19% | R-6 | 0.921 | 0.951 | 0.912
20% | R-6 | 0.919 | 0.95 | 0.91
21% | R-6 | 0.916 | 0.949 | 0.908
22% | R-6 | 0.914 | 0.948 | 0.906
23% | R-6 | 0.911 | 0.947 | 0.904
24% | R-6 | 0.909 | 0.946 | 0.902
25% | R-6 | 0.906 | 0.945 | 0.9
26% | R-6 | 0.904 | 0.944 | 0.899
27% | R-6 | 0.901 | 0.943 | 0.897
28% | R-6 | 0.899 | 0.941 | 0.895
29% | R-6 | 0.896 | 0.94 | 0.894
30% | R-6 | 0.894 | 0.939 | 0.892
3-79: Duct Heating Distribution Efficiency
Duct total leakage (%) | Duct system R-value | Restaurant | Retail | Other
2% | Uninsulated | 0.822 | 0.834 | 0.672
3% | Uninsulated | 0.818 | 0.83 | 0.668
4% | Uninsulated | 0.815 | 0.827 | 0.664
5% | Uninsulated | 0.811 | 0.823 | 0.659
6% | Uninsulated | 0.808 | 0.819 | 0.655
7% | Uninsulated | 0.804 | 0.816 | 0.651
8% | Uninsulated | 0.801 | 0.812 | 0.647
9% | Uninsulated | 0.798 | 0.809 | 0.643
10% | Uninsulated | 0.794 | 0.805 | 0.638
11% | Uninsulated | 0.791 | 0.801 | 0.634
12% | Uninsulated | 0.787 | 0.798 | 0.63
13% | Uninsulated | 0.784 | 0.794 | 0.626
14% | Uninsulated | 0.78 | 0.791 | 0.621
15% | Uninsulated | 0.777 | 0.787 | 0.617
16% | Uninsulated | 0.773 | 0.783 | 0.613
17% | Uninsulated | 0.77 | 0.78 | 0.609
18% | Uninsulated | 0.767 | 0.776 | 0.605
19% | Uninsulated | 0.763 | 0.773 | 0.6
20% | Uninsulated | 0.76 | 0.769 | 0.596
21% | Uninsulated | 0.756 | 0.765 | 0.592
22% | Uninsulated | 0.753 | 0.762 | 0.588
23% | Uninsulated | 0.749 | 0.758 | 0.583
24% | Uninsulated | 0.746 | 0.755 | 0.579
25% | Uninsulated | 0.742 | 0.751 | 0.575
26% | Uninsulated | 0.739 | 0.747 | 0.571
27% | Uninsulated | 0.736 | 0.744 | 0.567
28% | Uninsulated | 0.732 | 0.74 | 0.562
29% | Uninsulated | 0.729 | 0.737 | 0.558
30% | Uninsulated | 0.725 | 0.733 | 0.554
2% | R-6 | 0.925 | 0.931 | 0.822
3% | R-6 | 0.92 | 0.926 | 0.815
4% | R-6 | 0.915 | 0.921 | 0.809
5% | R-6 | 0.91 | 0.916 | 0.803
6% | R-6 | 0.905 | 0.911 | 0.796
7% | R-6 | 0.9 | 0.906 | 0.79
8% | R-6 | 0.895 | 0.901 | 0.783
9% | R-6 | 0.89 | 0.896 | 0.777
10% | R-6 | 0.885 | 0.891 | 0.771
11% | R-6 | 0.88 | 0.886 | 0.764
12% | R-6 | 0.874 | 0.881 | 0.758
13% | R-6 | 0.869 | 0.876 | 0.751
14% | R-6 | 0.864 | 0.871 | 0.745
15% | R-6 | 0.859 | 0.866 | 0.739
16% | R-6 | 0.854 | 0.861 | 0.732
17% | R-6 | 0.849 | 0.856 | 0.726
18% | R-6 | 0.844 | 0.851 | 0.719
19% | R-6 | 0.839 | 0.846 | 0.713
20% | R-6 | 0.834 | 0.841 | 0.707
21% | R-6 | 0.829 | 0.836 | 0.7
22% | R-6 | 0.824 | 0.831 | 0.694
23% | R-6 | 0.818 | 0.826 | 0.687
24% | R-6 | 0.813 | 0.821 | 0.681
25% | R-6 | 0.808 | 0.816 | 0.675
26% | R-6 | 0.803 | 0.811 | 0.668
27% | R-6 | 0.798 | 0.806 | 0.662
28% | R-6 | 0.793 | 0.801 | 0.655
29% | R-6 | 0.788 | 0.796 | 0.649
30% | R-6 | 0.783 | 0.791 | 0.643
Insulated/un-insulated
Insulated | 2.26
Un-insulated | 2.51
Pipe/Insulation
Pipe | 26.2
Insulation | 0.231
ro
Insulated | 0.359
Un-insulated | 0.443
Note on R29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Delete later
Note on J40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to 3.4 for PY15-PY17
Note on J41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to 3.4 for PY15-PY17
Note on J44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Fixed efficiency tables, per Matt at PPL Reply: Changed to 3.4 for PY15-PY17
Note on J45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to 3.3 for PY15-PY17

## Dropdowns (hidden)
Dropdowns
yBuilding_Type_HVAC | yBuilding Type_Chillers | yBuildingType_GuestRooms | yProject_Type | yEfficiencyKnown | xBuilding_Location | HVAC Equipment Type | Economizer HVAC Equipment Type | Chiller Equipment Type | Geothermal Equipment Type | yGR_EqmtType_Motel | yGR_EqmtType_Hotel | Electric Resistance? | Fuel Switching Equipment Type_Electric | Fuel Switching Equipment Type_NonElectric | PTAC/PTHP Type | yOperating_Schedule | xExpValve | yRefCharge% | yDHPBaseHeatingEquipment Type | yDHPBaseCoolingEquipment Type | yMotorSize | yMotorType | yMotorPoles | y_RACeqmttype | yRAC_options | Capcity Grouping | Capacity Grouping AC | y_Comp_Room_AC | y_CRAC _Mounting_Type | y_Flow | y_ECM_VSD | y_Location of Fan Plug | y_Conv_Fan_Size | Equipment Type | DMSHP Baseline | yThermostat_Heating_Type | Heat Pump | Ground Source Heat Pump | Central AC | Heating Type | yThermostat_Type | Tune Up Components | Tune Up Cooling System Type | Tune Up Heating System Type | Rating Condition | Smart Thermostat Cooling System Type | Smart Thermostat Heating System Type | Rate Codes | Insulated/un-insulated | Pipe/Insulation | ro | Unconditioned Space Type | Building Type Thermostats |  | Baseline |  | Duct total leakage (%)
Data Center - No Economizer | Data Center - No Economizer | Hotel | Early Replacement | Nameplate Efficiency Values known | Allentown | Air-Source Air Conditioners | Air-Source Air Conditioners | Air Cooled Chiller | Air-Source Heat Pumps | PTAC with Electric Resistance Heat | PTAC with Electric Resistance Heat | Yes | Air-Source Heat Pumps | Gas Furnace | Standard | 1 Shift, 5 days per week | TXV | 60% | DHP / Split System ASHP | DHP / Split System ASHP | 1 | Open | 2 poles | Room Air Conditioners | Without Louvered Sides | < 65000 | < 6000 | Air-Cooled | Floor-Mounted | Upflow Ducted | ECM | In Unit | ≥ 8 and < 10 | Single Package | New Space/No Existing Heating or Cooling | Gas | Heat Pump | Ground Source Heat Pump | Gas Furnace | Heat Pump | Manual | Condenser Cleaning | Air-Source Air Conditioners | Electric Resistance | Split System | Central AC | Electric Resistance | Small Business (GS1 & GS3 Rate Codes) | Insulated | Pipe | Insulated | Attic | Education – College/University | Education - College/University | Uninsulated | Restaurant | 2%
Data Center - With Economizer | Data Center - With Economizer | Motel | Replace on Burnout | Nameplate Efficiency Values NOT known | Binghamton | Air-Source Heat Pumps | Air-Source Heat Pumps | Water Cooled Chiller: Positive Displacement or Reciprocating | Groundwater Source Heat Pumps: Water-to-Air | PTAC with Gas Heat | PTAC with Gas Heat | No | Electric Furnace | Oil Furnace | Non-Standard | 2 Shift, 5 days per week | Orifice | 59% | Single Package ASHP | Single Package ASHP | 1.5 | Enclosed | 4 poles | Reverse-Cycle Room Air Conditioners | With Louvered Sides | ≥ 65000 and < 135000 | ≥ 6000 and < 8000 | Air-Cooled | Ceiling-Mounted | Upflow Non-Ducted | VSD | Underfloor | ≥ 10 and < 12 | Split System | Standard Ductless Heat Pump | Electric Furnace |  |  | Electric Resistance | Gas Furnace | Conventional Programmable | Evaporator Cleaning | Air-Source Heat Pumps | Other | Single Package | Heat Pump | Heat Pump | Large Business (LP4 & LP5 Rate Codes) | un-insulated | Insulation | Un-insulated | Basement, Uninsulated | Education - Other | Education - Other | R-6 | Retail | 3%
Education - College/University | Education - College/University |  | New Construction |  | Bradford | Water-Cooled Air Conditioners | Water-Cooled Air Conditioners | Water Cooled Chiller: Centrifugal | Ground Source Heat Pumps: Brine-to-Air | PTHP | PTHP |  | Baseboard Heating | Gas/Propane Steam Boiler |  | 3 Shift, 5 days per week |  | 58% | Electric Resistance | Room Air Conditoner | 2 |  | 6 poles | Casement-Only Room Air Conditioners |  | ≥ 135000 and < 240000 | ≥ 8000 and < 11000 | Air-Cooled with Fluid Economizer |  | Downflow |  | If Unknown | ≥ 12 and < 14 |  |  | None |  |  | None | Electric Resistance | Unknown | Refrigerant Charge Correction (<=20%) | PTAC |  |  | Ground Source Heat Pump | Ground Source Heat Pump |  |  |  |  | Basement, Insulated Walls | Grocery | Grocery |  | Other | 4%
Education - Primary School | Education - Primary School |  |  |  | Erie | Evaporatively-Cooled Air Conditioners | Evaporatively-Cooled Air Conditioners |  | Groundwater Source Heat Pumps: Water-to-Water |  | Central HW Fan Coil with Electric Resistance Heat |  | PTHP | Gas/Propane Hot Water Boiler |  | 24/7 |  | 57% | Electric Furnace | PTAC | 3 |  | 8 poles | Casement-Slider Room Air Conditioners |  | = 240000 | ≥ 11000 and < 14000 | Water-Cooled |  | Horizontal Flow |  |  | ≥ 14 and < 16 |  |  | Heat Pump |  |  |  | None |  | Refrigerant Charge Correction (>20%) | PTHP |  |  |  | Gas Furnace |  |  |  |  | Vented Crawl, Uninsulated | Health - Hospital | Health - Hospital |  |  | 5%
Education - Secondary School | Education - Secondary School |  |  |  | Harrisburg | PTAC |  |  | Ground Source Heat Pumps: Brine-to-Water |  | Central HW Fan Coil with Gas Heat |  |  | Oil Steam Boiler |  |  |  | 56% | New Space/No existing heat/Non-electric Heat | PTHP | 5 |  |  |  |  | ≥ 25000 and < 28000 | ≥ 14000 and < 20000 | Water-Cooled with Fluid Economizer |  |  |  |  | ≥ 16 and < 18 | [8 empty] | Condenser Cleaning, Evaporator Cleaning, Ref Charge Correction (<=20%) | [9 empty] | Vented Crawl, Insulated Frame Floor | Health - Other | Health - Other |  |  | 6%
Grocery | Grocery |  |  |  | Philadelphia | PTHP | [7 empty] | Oil Hot Water Boiler |  |  |  | 55% | PTHP | New Space/No existing cooling | 7.5 | [5 empty] | ≥ 20000 and < 25000 | Glycol-Cooled |  |  |  |  | ≥ 18 and < 20 | [8 empty] | Condenser Cleaning, Evaporator Cleaning, Ref Charge Correction (>20%) | [9 empty] | Vented Crawl, Ins. Frame Floor & Crawl Walls | Industrial Manufacturing | Industrial Manufacturing |  |  | 7%
Health - Hospital | Health - Hospital |  |  |  | Pittsburgh | [12 empty] | 54% |  |  | 10 | [5 empty] | ≥ 28000 | Glycol-Cooled with Fluid Economizer |  |  |  |  | ≥ 20 and < 24 | [18 empty] | Unvented Crawl, Uninsulated | Institutional/Public Service | Institutional/Public Service |  |  | 8%
Health - Other | Health - Other |  |  |  | Scranton | [12 empty] | 53% |  |  | 15 | [6 empty] | Air-Cooled with Free Air Discharge Condenser |  |  |  |  | ≥ 24 | [18 empty] | Unvented Crawl, Insulated Frame Floor | Lodging | Lodging |  |  | 9%
Industrial Manufacturing - 1 Shift | Industrial Manufacturing - 1 Shift |  |  |  | Williamsport | [12 empty] | 52% |  |  | 20 | [6 empty] | Air-Cooled with Free Air Discharge Condenser and Fluid Economizer | [23 empty] | Unvented Crawl, Ins. Frame Floor & Crawl Walls | Multifamily (Common Areas) | Multifamily (Common Areas) |  |  | 10%
Industrial Manufacturing - 2 Shift | Industrial Manufacturing - 2 Shift | [16 empty] | 51% |  |  | Other | [6 empty] | Air-Cooled with Ducted Condenser | [24 empty] | Office | Office |  |  | 11%
Industrial Manufacturing - 3 Shift | Industrial Manufacturing - 3 Shift | [16 empty] | 50% | [9 empty] | Air-Cooled with Fluid Economizer and Ducted Condenser | [24 empty] | Restaurant | Restaurant |  |  | 12%
Institutional/Public Service | Institutional/Public Service | [16 empty] | 49% | [34 empty] | Retail | Retail |  |  | 13%
Large Office | Large Office | [16 empty] | 48% | [34 empty] | Warehouse - Other | Warehouse - Other |  |  | 14%
Lodging - Large Hotel | Lodging - Large Hotel | [16 empty] | 47% | [34 empty] | Warehouse - Refrigerated | Warehouse - Refrigerated |  |  | 15%
Lodging - Small Hotel | Lodging - Small Hotel | [16 empty] | 46% | [38 empty] | 16%
Medium Office | Medium Office | [16 empty] | 45% | [38 empty] | 17%
Multifamily Common Areas | Multifamily Common Areas | [16 empty] | 44% | [38 empty] | 18%
Restaurant - Full Service | Restaurant - Full Service | [16 empty] | 43% | [38 empty] | 19%
Restaurant - Quick Service | Restaurant - Quick Service | [16 empty] | 42% | [38 empty] | 20%
Retail - Standalone | Retail - Standalone | [16 empty] | 41% | [38 empty] | 21%
Retail - Strip Mall | Retail - Strip Mall | [16 empty] | 40% | [38 empty] | 22%
Small Office | Small Office | [16 empty] | 39% | [38 empty] | 23%
Warehouse - Other | Warehouse - Other | [16 empty] | 38% | [38 empty] | 24%
Warehouse - Refrigerated | Warehouse - Refrigerated | [16 empty] | 37% | [38 empty] | 25%
[18 empty] | 36% | [38 empty] | 26%
[18 empty] | 35% | [38 empty] | 27%
[18 empty] | 34% | [38 empty] | 28%
[18 empty] | 33% | [38 empty] | 29%
List References: Guest Room Occ Sensor, Geothermal | [17 empty] | 32% | [38 empty] | 30%
Hotel | yGR_EqmtType_Hotel | [16 empty] | 31% | [38 empty] | 2%
Motel | yGR_EqmtType_Motel | [16 empty] | 30% | [38 empty] | 3%
End of Useful Life | yGeothermal_EOL_Eqpt | [16 empty] | 29% | [38 empty] | 4%
Early Replacement | yGeothermal_Retro_Eqpt | [16 empty] | 28% | [38 empty] | 5%
New Construction | yGeothermal_NC_Eqpt | [16 empty] | 27% | [38 empty] | 6%
[18 empty] | 26% | [38 empty] | 7%
[18 empty] | 25% | [38 empty] | 8%
Incentives | [17 empty] | 24% | [38 empty] | 9%
Custom Lite Incentive | 0.06 | [16 empty] | 23% | [38 empty] | 10%
Prescriptive Incentive | 0.05 | [16 empty] | 22% | [38 empty] | 11%
[18 empty] | 21% | [38 empty] | 12%
[18 empty] | 20% | [38 empty] | 13%
[18 empty] | 19% | [38 empty] | 14%
[18 empty] | 18% | [38 empty] | 15%
[18 empty] | 17% | [38 empty] | 16%
[18 empty] | 16% | [38 empty] | 17%
[18 empty] | 15% | [38 empty] | 18%
[18 empty] | 14% | [38 empty] | 19%
[18 empty] | 13% | [38 empty] | 20%
[18 empty] | 12% | [38 empty] | 21%
[18 empty] | 11% | [38 empty] | 22%
[18 empty] | 10% | [38 empty] | 23%
[18 empty] | 9% | [38 empty] | 24%
[18 empty] | 8% | [38 empty] | 25%
[18 empty] | 7% | [38 empty] | 26%
[18 empty] | 6% | [38 empty] | 27%
[18 empty] | 5% | [38 empty] | 28%
[18 empty] | 4% | [38 empty] | 29%
[18 empty] | 3% | [38 empty] | 30%
2%
1%
0%
-1%
-2%
-3%
-4%
-5%
-6%
-7%
-8%
-9%
-10%
-11%
-12%
-13%
-14%
-15%
-16%
-17%
-18%
-19%
-20%
-21%
-22%
-23%
-24%
-25%
-26%
-27%
-28%
-29%
-30%
-31%
-32%
-33%
-34%
-35%

## Printable Report
PPL Electric Direct Discount Program
Customer Name:
Prepared by:
| Customer Acknowledgement (please initial): _______________ Contractor Acknowledgement (please initial): _______________ |  | Date: _______________ Date: _______________
| Summary Table |  |  | This project's annual electric savings are equivalent to:
| Project Cost: | 0 |  |  | 0 |  | acres of forest saved
| Energy Savings (kWh): | 0
| Annual Cost Savings: | 0
| Available Utility Incentive: | 0 |  |  | 0 |  | miles driven by an average car
| Cost to Customer: | 0
Simple Pay Back (Yrs.)
[5 empty] | 0 |  | tons of waste recycled instead of landfilled
| BY THE NUMBERS | COST OF WAITING
| 0 | 0
[5 empty] | 0 |  | gallons of gasoline consumed
| Available Utility Incentive | Monthly
| 0% | 0 |  |  | 0 |  | pounds of coal burned
| Return on Investment | Annually
Factors from US EPA GHG Equivalencies Calculator
Measure List row | Measure | Measure Details | Quantity | Project Cost ($) | Energy Savings (kWh) | Demand Savings (kW) | Utility Cost Savings ($) | Incentive ($) | Cost to Customer

## HVAC Systems
Last Updated: See Version Log | [21 empty] | HIDE | HIDE | HIDE | HIDE
| HVAC Systems | [20 empty] | HIDE | HIDE | HIDE | HIDE |  |  | HIDE |  | HIDE
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information. For additional support, contact pplbusiness@clearesult.com or call us at 1-866-432-5501.
| Date | 0
| Project Site | 0
| Address | 0
| Zip Code Lookup* | 0
Weather Station Location*
| Building Type* | 0
Measure Description
Replacement of Air Cooled, Water Cooled or Evaporatively Cooled ACs, Split and Packaged Terminal Air Conditioners (PTACs) or Heat Pumps (PTHPs), and Air-Source Heat Pumps with higher efficiency units that exceed requirements of 2021 IECC. "Standard" size PTACs and PTHPs are defined as units with external wall openings with the following dimensions: ≥16 inches high, ≥42 inches wide, and ≥670 square inches of cross-sectional area; any units that do not comply with these dimensions shall be considered "Non-Standard" size units for the purposes of this calculator.
Eligibility
The following methodology should be used for air conditioning (central AC, air-cooled DX, split systems, and packaged terminal AC) and heating systems (air source and packaged terminal heat pump). This protocol excludes water source, ground source, and groundwater source heat pumps measures that are covered in the Water Source and Geothermal Heat Pumps section. All retrofit or new construction projects will use an end of useful life/new construction baseline. All HVAC applications other than comfort cooling and heating, such as process cooling, are defined as non-standard applications and are ineligible for this measure.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.1 HVAC Systems
| Project Type* | Baseline Unit (Early Replacement Only) |  |  |  |  | Proposed Unit | [14 empty] | Baseline Case |  | Energy-Efficient Case |  | Savings Summary
|  | Cooling Efficiency |  |  | Heating Efficiency |  | Equipment ID | Manufacturer | Model Number | Equipment Type* | Standard / Non Standard Size* Split System / Single Package* | Rated Cooling Capacity (BTU/hr) * | Rated Heating Capacity (BTU/hr)* | Does the Unit have Electric Resistance Heating?* | Quantity* | Cooling Efficiency* |  |  | Heating Efficiency*
|  | IEER | EER | SEER2 | COP | HSPF2 | [9 empty] | IEER | EER | SEER2 | COP | HSPF2 |  | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh | Proposed Annual Peak kW | Annual kWh Savings | Summer Peak kW Savings | Winter Peak kW Savings | Average Peak kW Savings | Uncapped Incentive | Incentive | Name Manager
Ex | Replace on Burnout | [5 empty] | A Wing | Daikin | RPS085D | Air-Source Air Conditioners |  | 983182 |  | No | 1 | 14.15 | 9.7 |  |  |  |  | 2125.8923 | 0.6726 | 1092 | 0.34549 | 1033.89 | 0.3271 | 0.0367 | 0.1819 | 103.389 | 103.39
1
2
3
4
5
6
7
8
9
10
[21 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Chiller (hidden)
Last Updated: See Version Log
Chillers
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information
| Date |  |  |  | 0 |  |  | 2021-01-01
| Project Site |  |  |  | 0 |  |  | Store 1
| Address |  |  |  | 0 |  |  | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* |  |  |  | 0 |  |  | 15501
| Weather Station Location* |  |  |  | Error: Zip code not found in Pennsylvania lookups table |  |  | Pittsburgh
Measure Description
This protocol shall apply to high efficiency electric chillers in commercial applications as furhter described below. This measure may apply to early replacement of an existing system, replacement on burnout, or installation of a new unit in a new or existing non-residential building for HVAC applications.
Eligibility
These prescriptive algorithms and stipulated values are valid for standard comfort cooling applications, defined as unitary electric chillers serving a single load at the system or sub-system level. The savings calculated using the prescriptive algorithms need to be supported by a certification that the chiller is appropriately sized for site design load condition. All other chiller applications, including existing multiple chiller configurations (including redundant or ‘stand-by’ chillers), existing chillers serving multiple load groups, chillers in industrial applications, chillers using glycol, and heat recovery chillers are defined as non-standard applications and must follow a site-specific custom protocol. Situations with existing non-VFD chillers upgrading to VFD chillers may use the protocol algorithm. This protocol does not apply to VFD retrofits to an existing chiller. In this scenario, the IPLV of the baseline chiller (factory tested IPLV) would be known, but the IPLV for the old chiller/new VFD would be unknown. The algorithms, assumptions, and default factors in this section may be applied to new construction applications.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.3 Electric Chillers
| Select a Building Type* | 0
| Project Type* | Baseline Equipment (Early Replacement Only) |  |  | Proposed Unit | [11 empty] | Baseline Case |  | Energy-Efficient Case |  | Savings Summary
|  | Cooling Efficiency* |  |  | Chiller ID | Manufactuer | Model Number | Equipment Type* | How will the chiller system perform (i.e., optimized for full-load or for part-load operation)? | Will this unit (or these units) typically operate above 70% full load? | Rated Cooling Capacity (tons) | Quantity | Cooling Efficiency*
|  | IPLV (in EER for Air Cooled; kW/ton for Water Cooled) | Full Load kW/ton (Water Cooled Chillers Only) | Full Load EER (Air Cooled Chillers Only) | [8 empty] | IPLV (in EER for Air Cooled; kW/ton for Water Cooled) | Full Load kW/ton (Water Cooled Chillers Only) | Full Load EER (Air Cooled Chillers Only) |  | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh | Proposed Annual peak kW | Annual kWh Savings | Summer Peak kW Savings | Winter Peak kW Savings | Average Peak kW Savings | Uncapped Incentive | Incentive
Ex | Replace on Burnout |  |  |  | CH-1 | Carrier | 30RAP070 | Air Cooled Chiller | Path A (Full-Load Optimized Applications) | Yes | 70 | 1 | 16.65 |  | 20 |  | 268514.8515 | 147.978 | 246545.4545 | 135.8707 | 21969.4 | 12.1073 | 0.1673 | 613.7% | 2196.94 | 2196.94
1
2
3
4
5
6
7
8
9
10
[16 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Geothermal (hidden)
Last Updated: See Version Log
Groundwater Source and Ground Source Heat Pumps
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information. For additional support, contact PPLBusiness@clearesult.com or call us at 1-866-432-5501
| Date | 0 |  |  | 2021-01-01
| Project Site | 0 |  |  | Store 1
| Address | 0 |  |  | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 |  |  | 15501
| Weather Station Location* |  |  |  | Pittsburgh
| Building Type* | 0 |  |  | Retail
Eligibility
This protocol shall apply to ground source, groundwater source, water source heat pumps, and water source and evaporatively cooled air conditioners in commercial applications . This measure may apply to early replacement of an existing system, replacement on burnout, or installation of a new unit in a new or existing non-residential building for HVAC applications. For "Replace on Burnout" and "New Construction" projects, the baseline assumes an equivalent air-source heat pump as the existing unit, while "Early Replacement" projects have a groundwater or ground source heat pump as the existing baseline unit; please complete the baseline section of this calculator accordingly.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.4 Groundwater Source and Ground Source Heat Pumps
| Project Type* | Baseline Equipment | [20 empty] | Savings Summary
|  | Equipment ID | Manufacturer | Model Number | Existing Equipment Type | Quantity | Rated Cooling Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Split System / Single Package (Air-Source Heat Pumps Only) | Does The Unit have Electric Resistance? | Cooling Efficiency (Not Required but Recommended) |  |  | Heating Efficiency (Not Required but Recommended) |  | Ground Loop Motor Information (Does Not Apply to Air-Source Heat Pumps)
[11 empty] | IEER | EER | SEER2 | COP | HSPF2 | Motor Quantity* | Motor Size (HP)* | Number of Poles (Required if Efficiency is Unknown) | Open / Enclosed (Required if Efficiency is Unknown) | Motor Efficiency (Recommended but Not Required) | Pump Efficiency (Recommended but Not Required) |  | Existing kWh | Existing Summer kW | Existing Winter kW | Proposed kWh | Proposed Summer kW | Proposed Winter kW | kWh Savings | Summer Peak kW Savings | Winter Peak kW Savings | Average Peak kW Savings | Uncapped Incentive | Incentive
| Replace on Burnout | A-1 | MSP | HPX110VSS | Air-Source Heat Pumps | 1 | 60000 | 60000 |  | Yes | [19 empty] | 0.79 |  |  |  | 121.9
1 | Early Replacement | A | B | C | Ground Source Heat Pumps: Brine-to-Water | 1 | 120000 | 110000 | Single Package | Yes | [5 empty] | 1 | 10 | 8 poles | Open | [6 empty] | 0
2 | New Construction |  |  |  |  | 1 | 60000 | 55000 | Split System | Yes | [15 empty] | 0
3 | New Construction |  |  |  |  | 1 | 60000 | 55000 | Single Package | No | [15 empty] | 0
4 | New Construction |  |  |  |  | 1 | 120000 | 110000 | Single Package | No | [15 empty] | 0
5 | New Construction |  |  |  |  | 1 | 180000 | 170000 | Single Package | Yes | [15 empty] | 0
6 | [25 empty] | 0
7 | [25 empty] | 0
8 | [25 empty] | 0
9 | [25 empty] | 0
10 | [25 empty] | 0
[22 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Proposed Equipment
| Proposed Equipment Type* | Cooling Efficiency* | Heating Efficiency* | Ground Loop Motor Information*
|  | EER | COP | Motor Quantity | Motor Size (HP) | Motor Efficiency* | Pump Efficiency*
| Groundwater Source Heat Pumps: Water-to-Air | 25 | 5 | 1 | 1 | 95% | 75%
1 | Ground Source Heat Pumps: Brine-to-Water | 25 | 5 | 1 | 10 | 95% | 75%
2 | Ground Source Heat Pumps: Brine-to-Water | 25 | 5 | 1 | 1 | 95% | 75%
3 | Ground Source Heat Pumps: Brine-to-Water | 25 | 5 | 1 | 1 | 95% | 75%
4 | Ground Source Heat Pumps: Brine-to-Water | 25 | 5 | 1 | 1 | 95% | 75%
5 | Ground Source Heat Pumps: Brine-to-Water | 25 | 5 | 1 | 1 | 95% | 75%
6
7
8
9
10

## Ductless Mini Splits
Last Updated: See Version Log
Ductless Mini-Split Heat Pumps - Commercial < 5.4 Tons
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information.
| Date | 0
| Project Site | 0
| Address | 0
| Zip Code Lookup* | 0
Weather Station Location*
| Building Type* | 0
Measure Description
ENERGY STAR Version 6.1 ductless "mini-split" heat pumps (DHP) utilize high efficiency SERR2/EER2 and HSPF2 energy performance factors of 15.2/11,7 and 7.8, respectively, or greater. This technology typically converts an electric resistance heated space into a space heated/cooled with a single or multi-zonal ductless heat pump system.
Eligibility
This protocol documents the energy savings attributed to ENERGY STAR ductless mini-split heat pumps with energy-efficiency performance of 15/12.5 SEER/EER and 8.5 HSPF or greater with inverter technology. The DHP could be a new device in an existing space, a new device in a new space, or could replace an existing heating/cooling device. The DHP systems could be installed as a single-zone system (one indoor unit, one outdoor unit) or a multi-zone system (multiple indoor units, one outdoor unit). In addition, the old systems should be de-energized, completely uninstalled and removed in order to ensure that the full savings is realized. All HVAC applications other than comfort cooling and heating, such as process cooling, are defined as non-standard applications and are ineligible for this measure.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.5 Ductless Mini-Split Heat Pumps - Commercial <5.4 tons
| Zone ID | Baseline Equipment |  |  | Proposed Equipment | [8 empty] | Baseline Case |  | Energy-Efficient Case |  | Savings Summary
|  | Cooling Equipment Type | Heating Equipment Type | Standard / Non-Standard Size (PTACs & PTHPs Only) | Manufacturer | Model Number | Rated Cooling Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Quantity | Cooling Efficiency | Heating Efficiency | Energy Star Product ID*
[10 empty] | SEER 2 Efficiency Rating | HSPF2 Efficiency Rating |  |  | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh | Proposed Annual peak kW | Annual kWh Savings | Summer Peak kW Savings | Winter Peak kW Savings | Average Peak kW Savings | Uncapped Incentive | Incentive
Ex | Zone 1
1
2
3
4
5
6
7
8
9
10
[13 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Ref Charge Correction (hidden)
Last Updated: See Version Log
HIDE
Refrigerant Charge Correction
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information
| Date | 0 | 2021-01-01
| Project Site | 0 | Store 1
| Address | 0 | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 | 15501
| Weather Station Location* |  | Pittsburgh
| Building Type* | 0 | Retail
Eligibility
This protocol is applicable for small commercial and industrial customers, and applies to documented tune-ups for package or split systems up to 20 tons. All HVAC applications other than comfort cooling and heating, such as process cooling, are defined as non-standard applications and are ineligible for this measure.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.7 Small C&I HVAC Refrigerant Charge Correction
| Baseline (Affected Equipment) | [13 empty] | Refrigerant Adjustment |  |  | Savings Summary
| Equipment ID | Manufacturer | Model Number | Equipment Type* | Single Package / Split System Standard / Non Standard Size | Rated Cooling Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Does the Unit have Electric Resistance Heating? | Quantity | Cooling Efficiency (If Available) |  |  | Heating Efficiency (If Available) |  | % Refrigerant Charge Corrected | Expansion Valve |  | kWh Saved | Summer Peak kW Savings | Winter Peak kW Savings | Average Peak kW | Uncapped Incentive | Incentive
[10 empty] | IEER | EER | SEER2 | COP | HSPF2 | [9 empty] | Name Manager
Ex | 1 | LG | 104802a | Air-Source Air Conditioners |  | 50000 |  | Yes | 1 |  | 17 | 20 |  |  | 19% | TXV |  | 19945.99 | 12.5336 | 0 | 6.27 | 1994.599 | 1994.6
1 |  |  |  | Air-Source Air Conditioners | Single Package | 60000 |  | Yes | 1 |  |  | 13.4 |  |  | -24% | TXV |  |  |  | 0 | 0 |  |  | EquipmentType
2 |  |  |  | Air-Source Air Conditioners | Single Package | 120000 |  | Yes | 1 | 14.8 |  |  |  |  | 25% | TXV |  |  |  | 0 | 0 |  |  | EquipmentType
3 |  |  |  | Air-Source Heat Pumps | Single Package | 60000 | 55000 | No | 1 |  |  | 13.4 |  | 6.7 | 52% | TXV | [7 empty] | EquipmentType
4 |  |  |  | Air-Source Heat Pumps | Single Package | 120000 | 110000 | No | 1 | 14.1 |  |  | 3.4 |  | -16% | TXV | [7 empty] | EquipmentType
5 | [19 empty] | 0 | 0
6 | [19 empty] | 0 | 0
7 | [19 empty] | 0 | 0
8 | [19 empty] | 0 | 0
9 | [19 empty] | 0 | 0
10 | [19 empty] | 0 | 0
[17 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0

## HVAC Tune Up
HVAC Tune Up
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information.
| Date | 0
| Project Site | 0
| Address | 0
| Zip Code Lookup* | 0
Weather Station Location*
| Building Type* | 0
Eligibility
This protocol is applicable for small commercial and industrial customers and applies to documented tune-ups for air cooled package or split air conditioners or air source heat pumps up to 20 tons. All HVAC applications other than comfort cooling and heating, such as process cooling, are defined as non-standard applications and are ineligible for this measure.The HVAC system must not have a standing maintenance contract and must not have had a tune-up in the last three years. In cases where refrigerant charge correction is the only tune-up action performed, savings must be calculated using measure protocol 3.2.7 Small C&I HVAC Refrigerant Charge Correction.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.8 HVAC Tune Up
| Is this unit under an annual preventative maintenance contract? | Has a tune up been performed within the past 3 years? | Equipment ID | Manufacturer | Model Number | Equipment Type* | Electric Resistance Heating?* | Split System/Single Package* Standard/Non-Standard* | Rated Cooling Capacity (BTU/hr) * | Rated Heating Capacity (BTU/hr)* | Quantity* | Cooling Efficiency* |  |  | Heating Efficiency* |  | Tune-Up Components Implemented |  | Savings Summary
[12 empty] | IEER | EER | SEER2 | COP | HSPF2 |  |  | Annual kWh Savings | Summer Peak kW Savings | Winter Peak kW Savings | Average Peak kW | Uncapped Incentive | Incentive | Name Manager
Ex | [16 empty] | Refrigerant Charge Correction (<=20%)
1 | [16 empty] | Refrigerant Charge Correction (<=20%)
2 | [16 empty] | Refrigerant Charge Correction (<=20%)
3 | [16 empty] | Refrigerant Charge Correction (<=20%)
4 | [16 empty] | Refrigerant Charge Correction (<=20%)
5 | [16 empty] | Refrigerant Charge Correction (<=20%)
6 | [16 empty] | Refrigerant Charge Correction (<=20%)
7 | [16 empty] | Refrigerant Charge Correction (<=20%)
8 | [16 empty] | Refrigerant Charge Correction (<=20%)
9 | [16 empty] | Refrigerant Charge Correction (<=20%)
10 | [16 empty] | Refrigerant Charge Correction (<=20%)
11 | [16 empty] | Refrigerant Charge Correction (<=20%)
12 | [16 empty] | Refrigerant Charge Correction (<=20%)
13 | [16 empty] | Refrigerant Charge Correction (<=20%)
14 | [16 empty] | Refrigerant Charge Correction (<=20%)
15 | [16 empty] | Refrigerant Charge Correction (<=20%)
16 | [16 empty] | Refrigerant Charge Correction (<=20%)
17 | [16 empty] | Refrigerant Charge Correction (<=20%)
18 | [16 empty] | Refrigerant Charge Correction (<=20%)
19 | [16 empty] | Refrigerant Charge Correction (<=20%)
20 | [16 empty] | Refrigerant Charge Correction (<=20%)
[18 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0

## Room AC (hidden)
Last Updated: See Version Log
| Room Air Conditioner | [14 empty] | HIDE
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information
| Date | 0 | 2021-01-01
| Project Site | 0 | Store 1
| Address | 0 | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 | 15501
| Weather Station Location* |  | Pittsburgh
| Building Type* | 0 | Retail
Eligibility
This protocol is for ENERGY STAR Version 4.1 room air conditioner units installed in small commercial spaces. All HVAC applications other than comfort cooling and heating, such as process cooling, are defined as non-standard applications and are ineligible for this measure. Only ENERGY STAR units qualify for this protocol.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.9 Room Air Conditioner
| Project Type* | Proposed Unit | [9 empty] | Savings Summary
|  | Equipment ID | Manufacturer | Model Number | Equipment Type* | Louver Existence (Not Required for Casement-Only or Casement-Slider Units) | Cooling Capacity (Btu/h) | New Unit CEER | Energy Star Product ID | Quantity |  | kWh Savings | Summer Peak kW Savings | Winter Peak kW Savings | Average Peak kW | Uncapped Incentive | Incentive
Ex | Early Replacement | Unit 1 | LG | LW8016ER | Room Air Conditioners | With Louvered Sides | 8000 | 22 | 101145826 | 10 |  | 333.38 | 0.5118 | 0 | 0.2559 | 33.338 | 33.34
1
2
3
4
5
6
7
8
9
10
[11 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0
0
0
0
0
0
0
0
0
0
0

## Guest Room Occ Sensor (hidden)
Last Updated: See Version Log
HIDE
Guest Room Occupancy Sensors
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information
| Date | 0 |  | 2021-01-01
| Project Site | 0 |  | Store 1
| Address | 0 |  | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 |  | 15501
| Weather Station Location* |  |  | Pittsburgh
Measure Description
This protocol applies to the installation of control systems in hotel guest rooms to automatically adjust the temperature setback during unoccupied periods. Savings are based on the management of the guest room's set temperatures and controlling the HVAC unit for various occupancy modes. The savings are per guestroom controlled, rather than per sensor, for multi-room suites. Savings are calculated per number of HVAC units controlled and capacity in tons. Enter unique equipment in each line item with their associated tonnage and quantity.
Eligibility
This measure is targeted to hotel customers whose guest rooms are equipped with energy management thermostats replacing manual heating/cooling temperature set-point and fan On/Off/Auto thermostat controls. Acceptable baseline conditions are hotel guest rooms with manual heating/cooling temperature set-point and fan On/Off/Auto thermostat controls. Efficient conditions are hotel/motel guest rooms with energy management controls of the heating/cooling temperature set-points and operation state based on occupancy modes.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.10 Controls: Guest Room Occupancy Sensor
| Building Type* | 0
| Facility Information | [7 empty] | Savings Summary
| Equipment ID | Manufacturer | Model Number | Total Rated Cooling Capacity per unit (tons) | Quantity of HVAC Units Controlled | Equipment Type | Is There Housekeeping Setback? |  | kWh Savings | Summer Peak kW Savings | Winter Peak kW Savings | Average Peak kW | Uncapped Incentive | Incentive $
Ex | PTAC-1 | Amana | PTC153K35 | 1.25 | 5 | PTAC with Electric Resistance Heat | Yes |  | 1435 | 0.355 | 0 | 0.1775 | 143.5 | 143.5
1 | [6 empty] | Yes
2 | [6 empty] | Yes
3 | [6 empty] | Yes
4 | [6 empty] | Yes
5 | [6 empty] | Yes
6 | [6 empty] | Yes
7 | [6 empty] | Yes
8 | [6 empty] | Yes
9 | [6 empty] | Yes
10 | [6 empty] | Yes
[8 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0

## Economizers (hidden)
Last Updated: See Version Log
HIDE
Economizer
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information
| Date | 0 | 2021-01-01
| Project Site | 0 | Store 1
| Address | 0 | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 | 15501
| Weather Station Location* | Error: Zip code not found in Pennsylvania lookups table | Pittsburgh
| Building Type* | 0 | Retail
Measure Description
This protocol describes the assumptions and algorithms used to quantify energy savigns for dual enthalpy economizers on HVAC equipment in commercial applications. Dual enthalpy economizers regulate the amount of outside air introduced into ventilation system based on the relative temperature and humidity of the outside and return air. If the enthalpy (latent and sensible heat) of the outside air is less than that of the return air when space cooling is required, then outside air is allowed in to reduce or eliminate the cooling requirement of the air conditiong equipment. Since the economizers will not be saving energy during peak hours, the demand savings are zero.
Eligibility
This measure is targeted to non-residential establishments whose HVAC equipment is not equipped with a functional economizer. The baseline condition is an HVAC unit with no economizer installed or with a non-functional/disabled economizer. The efficient condition is an HVAC unit with an economizer and dual enthalpy (differential) control. New construction installations are only eligible when not already required by IECC 2021 energy code.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.11 Controls: Economizer
| Project Type | Facility Information | [5 empty] | Equipment Type | Rated Cooling Capacity (BTU/hr) | Does the Unit have Electric Resistance Heating? | Standard / Non-Standard Size (PTACs & PTHPs Only) | Cooling Efficiency (Highly Recommended for Retrofits) |  |  |  | Savings Summary
|  | Equipment ID | Manufacturer | Model Number | HVAC Nameplate Efficiency Values | Operating Hours | Area Served (sq. ft.) |  |  |  |  | IEER | SEER2 | EER (Last Resort Only) |  | kWh Savings | Summer Peak kW Savings | Winter Peak kW Savings | Average Peak kW | Uncapped Incentive | Incentive
| Retrofit | Economizer RTU 1 | York | ZJ090 | Nameplate Efficiency Values known | 3 Shift, 5 days per week | 1099 | Air-Source Air Conditioners | 55000 | No |  |  | 18 |  |  | 1460.94 | 0 | 0 | 0 | 73.047 | 73.05
| Replace on Burnout |  |  |  | Nameplate Efficiency Values known | 1 Shift, 5 days per week | 10000 | Air-Source Air Conditioners | 60000 | No |  |  | 13.4 | 11 |  |  | 0 | 0 | 0
| Replace on Burnout |  |  |  | Nameplate Efficiency Values known | 2 Shift, 5 days per week | 10000 | Air-Source Air Conditioners | 120000 | No |  | 14.8 |  | 11 |  |  | 0 | 0 | 0
| Replace on Burnout |  |  |  | Nameplate Efficiency Values known | 3 Shift, 5 days per week | 10000 | Air-Source Air Conditioners | 180000 | No |  | 14.2 |  | 11 |  |  | 0 | 0 | 0
| Replace on Burnout |  |  |  | Nameplate Efficiency Values known | 24/7 | 10000 | Air-Source Air Conditioners | 500000 | No |  | 13.2 |  | 11 |  |  | 0 | 0 | 0
[17 empty] | 0 | 0 | 0
[17 empty] | 0 | 0 | 0
[17 empty] | 0 | 0 | 0
[17 empty] | 0 | 0 | 0
[17 empty] | 0 | 0 | 0
[17 empty] | 0 | 0 | 0
[15 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0
1
2
3
4
5
6
7
8
9
10

## Computer Room AC (hidden)
Last Updated: See Version Log
[12 empty] | HIDE | HIDE
Computer Room Air Conditioner
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information
| Date | 0 |  | 2021-01-01
| Project Site | 0 |  | Store 1
| Address | 0 |  | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 |  | 15501
| Weather Station Location* | Error: Zip code not found in Pennsylvania lookups table |  | Pittsburgh
| Building Type* | 0 |  | Retail
Eligibility
This protocol builds upon the existing HVAC Systems protocol to include computer room air conditioners, given their specific baseline efficiency requirements. The energy and demand savings for Commercial and Industrial HVAC systems are determined from the same algorithm as the HVAC systems measure. Newly-installed computer room air conditioner (CRAC) systems that exceed the baseline efficiencies (in SCOP) outlined in Table 3-56 of the TRM are eligible for this measure. VFDs and other CRAC measures can be found in other sections of the TRM.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.12 Computer Room Air Conditioner
| Proposed Unit | [9 empty] | Savings Summary | [5 empty] | Financial Summary
| Equipment ID | Manufacturer | Model Number | Equipment Type* | Mounting Type* | Upflow / Downflow | Cooling Capacity (Btu/hr) | New Unit SCOP | Quantity |  | kWh Savings | kW summer | kW winter | kW Savings average | Uncapped Incentive | Incentive
[18 empty] | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh | Proposed Annual Peak kW | Annual kWh Savings | Annual kW Savings (%) | Peak kW Savings | Peak kW Savings | Incremental Measure Cost | Incentive
Ex | CRAC-1 | Senville | Leto | Air Cooled | Floor-Mounted | Upflow | 36000 | 3.1 | 1 |  | 869.37 | 0.43469 | 0.43469 | 0.4347 | 121.1975 | 121.2
1 | Crac 1 | senville | Leto | Air-Cooled | Floor-Mounted | Upflow Ducted | 36000 | 3 | 1 |  | 869.37 | 0.43469 | 0.43469 | 0.4347 | 173.874 | 0.086937 |  | 0 | 4.8673 | 9900 | 5.5 | -9900 |  | -0.63274 | -13% |  | Project does not qualify; check efficiency requirements
2 | Crac 2 | senville | Leto | Glycol-Cooled | Ceiling-Mounted | Upflow Ducted | 47000 | 3 | 1 |  | 5091.25 | 2.5456 | 2.5456 | 2.5456 | 1018.25 |  |  | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% |  | Project does not qualify; check efficiency requirements
3 | Crac 3 | senville | Leto | Glycol-Cooled | Ceiling-Mounted | Upflow Ducted | 412500 | 3 | 1 |  | 55241.25 | 27.6206 | 27.6206 | 27.6206 | 11048.25 |  |  | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% |  | Project does not qualify; check efficiency requirements
4 | Crac 4 | senville | Leto | Glycol-Cooled | Floor-Mounted | Upflow Ducted | 24000 | 3 | 1 |  | 871.14 | 0.43557 | 0.43557 | 0.4356 | 174.228 |  |  | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% |  | Project does not qualify; check efficiency requirements
5 | Crac 5 | senville | Leto | Glycol-Cooled | Floor-Mounted | Upflow Non-Ducted | 47000 | 3 | 1 |  | 4061.83 | 2.0309 | 2.0309 | 2.0309 | 812.366 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0
6 | Crac 6 | senville | Leto | Glycol-Cooled | Ceiling-Mounted | Upflow Non-Ducted | 412500 | 3 | 1 |  | 52989.77 | 26.4949 | 26.4949 | 26.4949 | 10597.954 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0
7 | Crac 7 | senville | Leto | Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 24000 | 3 | 1 |  | 2637.75 | 1.3189 | 1.3189 | 1.3189 | 527.55 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0
8 | Crac 8 | senville | Leto | Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 47000 | 3 | 1 |  | 5470.89 | 2.7354 | 2.7354 | 2.7354 | 1094.178 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0
9 | Crac 9 | senville | Leto | Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Ducted | 412500 | 3 | 1 |  | 59167.24 | 29.5836 | 29.5836 | 29.5836 | 11833.448 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0
10 | Crac 10 | senville | Leto | Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 24000 | 3 | 1 |  | 2525.02 | 1.2625 | 1.2625 | 1.2625 | 505.004 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0
11 | Crac 11 | senville | Leto | Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 47000 | 3 | 1 |  | 5091.25 | 2.5456 | 2.5456 | 2.5456 | 1018.25
12 | Crac 12 | senville | Leto | Glycol-Cooled with Fluid Economizer | Ceiling-Mounted | Upflow Non-Ducted | 412500 | 3 | 1 |  | 56784.88 | 28.3924 | 28.3924 | 28.3924 | 11356.976
[10 empty] | Total | 250801.64 | 125.4008 | 125.4008 | 125.4007 | 50160.328 | 0.086937

## Computer Room AC ECM or VSD (hidden)
Last Updated: See Version Log
| Computer Room Air Conditioner EC Motor or VSD on AC Fan Motors | [9 empty] | HIDE | HIDE
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information
| Date | 0 |  |  | 2021-01-01
| Project Site | 0 |  |  | Store 1
| Address | 0 |  |  | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 |  |  | 15501
| Weather Station Location* | Error: Zip code not found in Pennsylvania lookups table |  |  | Pittsburgh
| Building Type* | 0 |  |  | Retail
Eligibility
This protocol builds upon the existing HVAC Systems protocol to include computer room air conditioners, given their specific baseline efficiency requirements. The energy and demand savings for Commercial and Industrial HVAC systems are determined from the same algorithm as the HVAC systems measure. Newly-installed computer room air conditioner (CRAC) systems that exceed the baseline efficiencies (in SCOP) outlined in Table 3-56 of the TRM are eligible for this measure. VFDs and other CRAC measures can be found in other sections of the TRM.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.13-14 COMPUTER ROOM AIR CONDITIONER/HANDLER ELECTRONICALLY COMMUTATED PLUG FANS or VSD on AC Fan Motors
| Equipment ID | Manufacturer | Model Number | ECM or VSD Measure Installation | Horsepower if Known | Location of Fan Plug - Required for ECM | Hours if Other than 8760 | Quantity |  | kWh Savings | kW summer | kW winter | kW average | Uncapped Incentive | Incentive
Ex | RTU 1 & 2 | Yaskawa | CIMR-VU4A0009FAA | ECM | 5 | Underfloor | 4356 | 2 |  | 5631.8712 | 1.2929 | 1.2929 | 1.2929 | 563.1871 | 563.19
1 | [9 empty] | 0 | 0 | 0 | 0 | 0
2 | [9 empty] | 0 | 0 | 0 | 0 | 0
3 | [9 empty] | 0 | 0 | 0 | 0 | 0
4 | [9 empty] | 0 | 0 | 0 | 0 | 0
5 | [9 empty] | 0 | 0 | 0 | 0 | 0
6 | [9 empty] | 0 | 0 | 0 | 0 | 0
7 | [9 empty] | 0 | 0 | 0 | 0 | 0
8 | [9 empty] | 0 | 0 | 0 | 0 | 0
9 | [9 empty] | 0 | 0 | 0 | 0 | 0
10 | [9 empty] | 0 | 0 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0

## Hi Vol Low Speed Fans (hidden)
[11 empty] | HIDE | HIDE |  | HIDE
Circulation Fan: High Volume Low Speed Fans
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information
| Date | 0 | 2021-01-01
| Project Site | 0 | Store 1
| Address | 0 | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 | 15501
| Weather Station Location* |  | Pittsburgh
| Building Type* | 0 | Retail
Eligibility
This protocol covers energy and demand savings associated with the installation of high-volume low-speed (HVLS) circulating fans to replace conventional circulating fans. HVLS fans generally range from 8 feet to 24 feet in diameter and move more cubic feet of air per Watt than conventional circulating fans. This measure is for use in Commercial and Industrial applications only. For Agricultural applications, please refer to TRM Measure 4.1.5 High Volume Low Speed Fans.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.15 Circulation Fan: High-Volume Low-Speed
| Proposed Unit | [8 empty] | Savings Summary
| Equipment ID | Manufacturer | Model Number | No. of Conventional Fans Removed* | No. of HVLS Circulating Fans Installed* | Rated CFM* | Conventional Fan Size* | Fan Size (Diameter)* |  | Annual Energy Savings (kWh) | kW summer | kWwinter | Peak Demand Savings (kW) Average | Uncapped Incentive | Incentive
| Fan 1 | PMSM | HVLS_FD1A | 1 | 1 | 30000 | ≥ 20 and < 24 | ≥ 20 and < 24 |  | 1298.83 | 0.81616 | 0.0051512 | 4.615 | 287.053 | 287.05
1
2
3
4
5
6
7
8
9
10
[9 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0

## Fuel Switching (hidden)
Last Updated: See Version Log
Fuel Switching
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information
| Date | 0 |  |  | 2021-01-01
| Project Site | 0 |  |  | Store 1
| Address | 0 |  |  | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 |  |  | 15501
| Weather Station Location* |  |  |  | Pittsburgh
| Building Type* | 0 |  |  | Retail
Eligibility
The energy and demand savings for small commercial fuel switching for heating systems is determined from the algorithms listed below. This protocol excludes water source, ground source, and groundwater source heat pumps. The baseline for this measure is an existing commercial facility with an electric primary heating source. The heating source can be electric baseboards, packaged terminal heat pump (PTHP) units, electric furnace, or electric air source heat pump. The retrofit condition for this measure is the installation of a new standard efficiency natural gas, propane, or oil furnace or boiler. This algorithm does not apply to combination space and water heating units. This protocol applies to furnace measures with input rating of less than 225,000 Btu/hr and boiler measures with input rating of less than 300,000 Btu⁄hr.
Source: Pennsylvania 2021 TRM Volume 3 - 3.2.5 FUEL SWITCHING: SMALL COMMERCIAL ELECTRIC HEAT TO NATURAL GAS / PROPANE / OIL HEAT
| Project Type* | Proposed Unit | [11 empty] | Financial Summary
|  | Equipment ID* | Manufacturer | Model Number | Proposed Equipment Type* | Project Cost* | Rated Heating Capacity* (BTU/hr) | Proposed Quantity* | AFUE* (%) | Blower Motor Size* (HP) | Blower Motor Efficiency* (%) | Energy Star Product ID* |  | Annual kWh Savings | Peak kW Savings | Increase in Annual Fuel Consumption (therms) | Uncapped Incentive | Incentive
| Early Replacement | Boilers 8-17 | Mitsubishi | A0224CSX | Gas/Propane Hot Water Boiler | 10000 | 224000 | 1 | 98% |  |  | 9 |  | 9158.26 | 0 | 1488 | 457.913 | 457.91
1 | [14 empty] | 0
2 | [14 empty] | 0
3 | [14 empty] | 0
4 | [14 empty] | 0
5 | [14 empty] | 0
6 | [14 empty] | 0
7 | [14 empty] | 0
8 | [14 empty] | 0
9 | [14 empty] | 0
10 | [14 empty] | 0
[13 empty] | Total | 0 | 0 | 0 | 0 | 0
Baseline Equipment
| Model # / Equipment Notes* |  | Remaining Useful Life* (in Years) | Equipment Type* | Standard/Non Standard Size* | Rated Heating Capacity* (BTU/hr) | Existing Quantity* | Heating Efficiency
[8 empty] | COP* | HSPF*
Ex | RTU-8-17 |  | 5 | Air-Source Heat Pumps | Standard | 240000 | 1 | 5
1
2
3
4
5
6
7
8
9
10

## Demand Controlled Ventilation (hidden)
[6 empty] | HIDE | HIDE |  | HIDE
Demand Controlled Ventilation
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information
Eligibility
This protocol is applicable for commercial and institutional market segments only. The base case for this measure is conditioned space with no DCV capability. For heating savings, this measure does not apply to any system with terminal reheat (constant volume or variable air volume). This protocol is intended for DCV retrofits on HVAC systems without economizers installed. Units with economizers may be eligible for the Advanced Rooftop Controls measure (3.2.17).
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.16 Demand Controlled Ventillation
| Demand Controlled Ventilation (DCV) |  |  |  | Savings Summary
| Unit | Heating Type | Conditioned space area (sq ft) |  | Annual kWh Savings | Peak kW summer | Peak kW winter | kW Average | Uncapped Incentive | Incentive $
1 |  |  |  |  | #N/A | #N/A | #N/A | #N/A
2 |  |  |  |  | #N/A | #N/A | #N/A | #N/A
3 |  |  |  |  | #N/A | #N/A | #N/A | #N/A
4 |  |  |  |  | #N/A | #N/A | #N/A | #N/A
5 |  |  |  |  | #N/A | #N/A | #N/A | #N/A
6 |  |  |  |  | #N/A | #N/A | #N/A | #N/A
7 |  |  |  |  | #N/A | #N/A | #N/A | #N/A
8 |  |  |  |  | #N/A | #N/A | #N/A | #N/A
9 |  |  |  |  | #N/A | #N/A | #N/A | #N/A
10 |  |  |  |  | #N/A | #N/A | #N/A | #N/A
|  |  |  | Totals | #N/A | #N/A | #N/A | #N/A | 0 | 0

## Advanced Rooftop Controls (hidden)
[8 empty] | HIDE | HIDE |  | HIDE
Advanced Rooftop Controls
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information
Eligibility
This protocol is only applicable for commercial and institutional market segments with buildings served by single-zone packaged HVAC units that include functional integrated economizers. The measure is eligible as retrofit or new construction vintages, if demand control ventilation or drives on air handlers are not specifically required by code. To be eligible for a retrofit, the baseline HVAC system must have a functioning economizer, but it must lack DCV and must operate as a constant-volume, constant-ventilation unit. VFD installations that do not involve integrated DCV and economizer controls are not eligible for this protocol but may be eligible for the Variable Frequency Drive (VFD) Improvements protocol (3.3.2). HVAC units without economizers may be eligible for the standalone Demand Controlled Ventilation (3.2.16).
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.17 Advanced Rooftop Controls
Advanced Rooftop Controls | [6 empty] | Savings Summary
Unit | Cooling Equipment Type | Heating Equipment Type | Rated Cooling Capacity (tons) | Rated Heating Capacity (tons) | DCV Type |  | Annual kWh Savings | Peak kW Summer | Peak kW Winter | kW Average | Uncapped Incentive | Incentive $
1 | Air Conditioner | Electric Resistance | 1 | 1 | Without Motor Drive Improvements |  | 0
2 | Air Conditioner | Natural Gas | 1 | 1 | Without Motor Drive Improvements |  | 0
3 | Heat Pump | Heat Pump | 1 | 1 | Without Motor Drive Improvements |  | 0
4 | Air Conditioner | Electric Resistance | 1 | 1 | Two-Speed Controls |  | 0
5 | Air Conditioner | Natural Gas | 1 | 1 | Two-Speed Controls |  | 0
6 | Heat Pump | Heat Pump | 1 | 1 | Two-Speed Controls |  | 0
7 | Air Conditioner | Electric Resistance | 1 | 1 | Three-Speed Controls or VFD |  | 0
8 | Air Conditioner | Natural Gas | 1 | 1 | Three-Speed Controls or VFD |  | 0
9 | Heat Pump | Heat Pump | 1 | 1 | Three-Speed Controls or VFD |  | 0
10 | [6 empty] | 0
[6 empty] | Totals | 0 | 0 | 0 | 0 | 0 | 0

## Smart Thermostats
[14 empty] | Hide |  | HIDE | HIDE |  | HIDE
Smart Thermostats
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information.
Date | 0
Project Site | 0
Address | 0
Zip Code Lookup* | 0
Weather Station Location*
Building Type* | 0
Eligibility
This measure documents the energy savings resulting from the installation of ENERGY STAR®-certified connected thermostats in non-residential facilities with central cooling or heating or line voltage heating provided that professional installers use aftermarket transformers to step down the line voltage to 24V. Eligible HVAC systems must be single-zone and <65 kBtu/h for cooling systems and <225 kBtu/h for heating systems.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.18 C&I ENERGY STAR Certified Connected Thermostats
Project Type* | Thermostat Location | Manufacturer | Model Number | Quantity | Pre-Existing Thermostat Type | HVAC Cooling Equipment Type* | HVAC Heating Equipment Type* | Rated Cooling Capacity (kBTU/hr) | Heating Capacity (kBTU/hr) |  | Motor HP (If Known, Gas Furnace Only) | Motor Efficiency (If Known, Gas Furnace Only) |  |  | Savings Summary
[9 empty] | Heat Pump | Electric Resistance Heating
[15 empty] | Annual kWh Savings | kW summer | kW winter | kW average | Uncapped Incentive | Incentive
New Construction | Main Office | ABC | 123 | 2 | Conventional Programmable | Air-Source Heat Pumps | Heat Pump | 60 | 60 |  | 0.5 | 50%
[13 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Thermostat Adjustments (hidden)
Last Updated: See Version Log
| Adjustment of Programmable Thermostats | [13 empty] | HIDE
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information
| Date | 0 | 2021-01-01
| Project Site | 0 | Store 1
| Address | 0 | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 | 15501
| Weather Station Location* |  | Pittsburgh
| Building Type* | 0 | Retail
Eligibility
This measure is targeted to non-residential establishments with single zone HVAC units. The baseline for this measure is an existing programmable thermostat installed on a single zone HVAC unit.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.19 Adjustment of Programmable Thermostats
| Equipment Specifications | [13 empty] | Setback Schedule
| Zone ID | Manufacturer | Model Number | Cooling Equipment Type* | Heating Equipment Type* | Standard / Non Standard Size* Split System / Single Package* | Rated Cooling Capacity (BTU/hr) * | Rated Heating Capacity (BTU/hr)* | Quantity* | Cooling Efficiency* |  |  | Heating Efficiency* |  | Occupancy Schedule |  |  | Cooling - Baseline |  | Heating - Baseline |  | Cooling - Proposed |  | Heating - Proposed
[10 empty] | IEER | EER | SEER2 | COP | HSPF2 | Occupancy Starting Hour | Occupancy Ending Hour | Number of Holidays | Setpoint Temperature (°F) | Setback Temperature (°F) | Setpoint Temperature (°F) | Setback Temperature (°F) | Setpoint Temperature (°F) | Setback Temperature (°F) | Setpoint Temperature (°F) | Setback Temperature (°F)
Ex | Room 112 | Daikin | RPS085D | Air-Source Air Conditioners | Electric Resistance |  | 983182 |  | 1 | 14.15 | 9.7 |  |  |  | 8 | 16 | 10 | 72 | 72 | 65 | 65 | 72 | 78 | 65 | 60
1 | Test |  |  | Air-Source Air Conditioners | Heat Pump | Standard | 120000 |  | 1 | 14.15 |  |  | 4
2
3
4
5
6
7
8
9
10

## Duct Sealing and Insulation (hidden)
[20 empty] | HIDE | HIDE |  | HIDE
Duct Sealing and Insulation
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information
Eligibility
This measure documents the energy savings resulting from the installation of duct insulation, sealing ducts passing through unconditioned spaces, or both sealing and insulation. The baseline condition for this measure is a duct system in a non-residential facility, with sub-optimal sealing, insulation, or both. An eligible system must have the following to be eligible for this measure: •HVAC supply ducts passing through an unconditioned space •Existing Construction (System Retrofit Only)
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.20 Duct Sealing and Insulation
| Date |  | 2021-01-01
| Project Site |  | Store 1
| Address |  | 500 Example Rd, Pittsburgh, PA
| Zip Code Lookup* | 0 | 15501
| Weather Station Location* |  | Pittsburgh
| Building Type* | 0 | Retail
| HVAC Equipment Information | [10 empty] | Insulation Information | [6 empty] | Savings Summary
| Cooling Equipment Type | Heating Equipment Type | Rated Cooling Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Electric Furnace Rating (kW) | Are HVAC Equipment Efficiency Values Known? | Cooling Efficiency |  |  | Heating Efficiency |  | Unconditioned Space Type | Percentage of equipment in space | Baseline |  | Energy Efficient (EE) Condition |  |  | Annual kWh Savings | kW summer | kW winter | kW average | Uncapped Totals | Incentive
|  |  | Rated Cooling Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Are HVAC Equipment Efficiency Values Known? | IEER | EER2 | SEER2 | COP | HSPF2 |  |  | Insulation Type | Duct Leakage | Insulation Type | Duct Leakage | [6 empty] | Incentive
1 | None | Electric Furnace | 0 | 0 | 1 | Yes | 0 | 0 | 13.4 | 0 | 6.7 | Unvented Crawl, Ins. Frame Floor & Crawl Walls | 80% | Uninsulated | 23% | R-6 | 7% |  | 0 | #N/A | #N/A | #N/A
2 | Heat Pump | Heat Pump | 12000 | 12000 | 0 | Yes | 0 | 0 | 13 | 0 | 6.7 | Unvented Crawl, Ins. Frame Floor & Crawl Walls | 0% | Uninsulated | 20% | R-6 | 3% |  | 0 | #N/A | #N/A | #N/A
3 | Heat Pump | Heat Pump | 72000 | 72000 | 0 | Yes | 14.8 | 0 | 0 | 3.4 | 0 | Unvented Crawl, Ins. Frame Floor & Crawl Walls | 50% | Uninsulated | 22% | R-6 | 10% |  | 0 | #N/A | #N/A | #N/A
4 | Air Conditioner | Gas | 12000 | 0 | 0 | Yes | 0 | 0 | 13 | 0 | 0 | Vented Crawl, Insulated Frame Floor | 0% | Uninsulated | 13% | R-6 | 8% |  | 0 | #N/A | #N/A | #N/A
5 | Heat Pump | Heat Pump | 12000 | 12000 | 0 | Yes | 0 | 0 | 13 | 0 | 6.7 | Unvented Crawl, Ins. Frame Floor & Crawl Walls | 50% | Uninsulated | 18% | R-6 | 2% |  | 0 | #N/A | #N/A | #N/A
6 | Heat Pump | Heat Pump | 72000 | 72000 | 0 | Yes | 14.8 | 0 | 0 | 3.4 | 0 | Unvented Crawl, Ins. Frame Floor & Crawl Walls | 80% | Uninsulated | 28% | R-6 | 8% |  | 0 | #N/A | #N/A | #N/A
7 | None | Electric Furnace | 0 | 0 | 1 | No | [5 empty] | Vented Crawl, Uninsulated | 50% | Uninsulated | 20% | Uninsulated | 9% |  | 0 | #N/A | #N/A | #N/A
8 | [18 empty] | 0 | #N/A | #N/A | #N/A
9 | [18 empty] | 0 | #N/A | #N/A | #N/A
10 | [18 empty] | 0 | #N/A | #N/A | #N/A
[18 empty] | Total | 0 | #N/A | #N/A | #N/A | 0 | 0

## Chilled Water Pipe Insulation (hidden)
Last Updated: See Version Log
Duct Sealing and Insulation
Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information
Eligibility
This measure documents the energy savings resulting from the installation of CHW pipe insulation in non-residential facilities. The baseline condition for this measure is an uninsulated indoor CHW pipe. An eligible CHW system must have the following to be eligible for this measure: •Electric Chiller •Existing Construction (System Retrofit Only) •CHW pipe requires a minimum of 1-inch of insulation that is in compliance with the specifications above •Deemed savings are not provided for Data Centers through this protocol. Savings for Data Center projects should be calculated using custom measure protocols.
Source: Pennsylvania 2026 TRM Volume 3 - 3.2.21 Chilled Water Pipe Insulation
Savings Summary
| Space Description | Pipe Length, ft | Annual kWh Savings | kW summer | kW winter | kW average | Uncapped Incentive | Incentive
| Warehouse | 60 | #N/A | #N/A | #N/A | #N/A
|  |  | #N/A | #N/A | #N/A | #N/A | 0 | 0

## Calculations (hidden)
-0.21
-0.22
| HVAC Calculations | [12 empty] | BTU/hr*(1/1000)*(1/eff_base)*EFLH_cool*Quantity | BTU/hr*(1/1000)*(1/eff_base)*EFLH_heat*Quantity |  | kWh_total_base*ETDF_summer | kWh_total_base*ETDF_winter | BTU/hr*(1/1000)*(1/eff_ee)*EFLH_cool*Quantity | BTU/hr*(1/1000)*(1/eff_ee)*EFLH_heat*Quantity |  | kWh_total_ee*ETDF
| EFLH_Cool_Default | EFLH_heat_Default | ETDF_summer | ETDF_winter | IEER | EER | SEER2 | COP | HSPF2 | Cooling Baseline Efficiency | Cooling Proposed Efficiency | Heating Baseline Efficiency | Heating Proposed Efficiency | Existing Cooling kWh | Existing Heating kWh | Existing Total kWh | Existing Total kW (Summer) | Existing Total kW (Winter) | Proposed Cooling kWh | Proposed Heating kWh | Proposed Total kWh | Proposed Total kW (Summer) | Proposed Total kW (Winter) | Annual Energy Savings (kWh) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW) | Average Peak Demand Savings (kW) |  |  | -0.25
[6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | [9 empty] | -0.26
[6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | [9 empty] | -0.27
[6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | [9 empty] | -0.28
[6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | [9 empty] | -0.29
[6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | [9 empty] | -0.3
[6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | [9 empty] | -0.31
[6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | [9 empty] | -0.32
[6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | [9 empty] | -0.33
[6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | [9 empty] | -0.34
[6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 0 | [9 empty] | -0.35
HVAC - NC Baseline Savings
| NC_Cooling kWh Baseline Efficiency | NC_Heating kWh baseline Efficiency | NC_kW Baseline Efficiency | NC_Baseline Cooling kWh Consumption | NC_Baseline Heating kWh Consumption | NC_Baseline Total kWh Consumption | NC_Baseline kW Consumption | NC_kWh Savings | NC_kW Savings
| 10.809 | 3.018 | 10.809 | 556.9433 | 1048.8068 | 1605.7501 | 0.27755 | -378.2327 | 0.077546
| 10.809 | 3.018 | 10.809 | 556.9433 | 1048.8068 | 1605.7501 | 0.27755 | -378.2327 | 0.077546
| 10.809 | 3.018 | 10.809 | 556.9433 | 1048.8068 | 1605.7501 | 0.27755 | -378.2327 | 0.077546
| 10.809 | 3.018 | 10.809 | 556.9433 | 1048.8068 | 1605.7501 | 0.27755 | -378.2327 | 0.077546
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
Lifetime Savings
| Life of Equipment | Early Replacement Savings (kWh) | Early Replacement Savings (kW) | Remaining Useful Life | New Construction Savings (kWh) | New Construction Savings (kW) | Number of Years | Lifetime Savings (kWh) | Lifetime Savings (kW)
| 15 |  |  | 0 | -378.2327 | 0.077546 | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | -378.2327 | 0.077546 | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | -378.2327 | 0.077546 | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | -378.2327 | 0.077546 | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
Chillers Calculations
| Default Cooling EFLH | ETDF_summer | ETDF_winter | IPLV | Full Load kW/ton | Full Load EER | Baseline Efficiency | Proposed Efficiency | Existing Total kWh | Existing Total kW (Summer) | Existing Total kW (Winter) | Proposed Total kWh | Proposed Total kW (Summer) | Proposed Total kW (Winter) | Annual Energy Savings (kWh) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW) | Average Peak Demand Savings (kW)
0
0
0
0
0
0
0
0
0
0
HVAC - NC Baseline Savings
| NC_Cooling kWh Baseline Efficiency | NC_Heating kWh baseline Efficiency | NC_Baseline kWh Consumption | NC_Baseline kW Consumption | NC_kWh Savings | NC_kW Savings
Lifetime Savings
| Life of Equipment | Early Replacement Savings (kWh) | Early Replacement Savings (kW) | Remaining Useful Life | New Construction Savings (kWh) | New Construction Savings (kW) | Number of Years | Lifetime Savings (kWh) | Lifetime Savings (kW)
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
Geothermal Calculations
| EFLH_Cooling_Default | EFLH_heat_Default | ETDF_summer | ETDF_winter | Default Motor Load Factor | Baseline Motor Efficiency_Default | Baseline Pump Efficiency_Default | Baseline Equipment Type | Electric Resistance Heating? | Baseline IEER | Baseline EER | Baseline SEER2 | Baseline COP | Baseline HSPF2 | Proposed EER | Proposed COP | Cooling kWh Baseline | Heating kWh Baseline | Pump kWh Baseline | Total kWh (Baseline) | Cooling kWh Proposed | Heating kWh Proposed | Pump kWh Proposed | Total kWh (Proposed) | Baseline Total kW (Summer) | Baseline Total kW (Winter) | Proposed Total kW (Summer) | Proposed Total kW (Winter) | Cooling Savings (kWh) | Heating Savings (kWh) | Pump Energy Savings (kWh) | Summer Pump Energy Savings (kWh) | Winter Pump Energy Savings (kWh) | Total Energy Savings (kWh) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW) | Average Peak Demand Savings (kW)
|  |  | #N/A | #N/A | 0.75 | 90.2% | 75% | Ground Source Heat Pumps: Brine-to-Water | Yes | 0 | 12.1 | 0 | 2.5 | 0 | 25 | 5 | [7 empty] | 0 |  |  | #N/A | #N/A | [5 empty] | 0
|  |  | #N/A | #N/A | 0.75 | NA |  | Air-Source Heat Pumps | Yes | 0 | 0 | 14.3 | 0 | 7.5 | 25 | 5 |  |  | 0 |  |  |  |  | 0 |  |  | #N/A | #N/A | [5 empty] | 0
|  |  | #N/A | #N/A | 0.75 | NA |  | Air-Source Heat Pumps | No | 0 | 0 | 13.4 | 0 | 6.7 | 25 | 5 |  |  | 0 |  |  |  |  | 0 |  |  | #N/A | #N/A | [5 empty] | 0
|  |  | #N/A | #N/A | 0.75 | NA |  | Air-Source Heat Pumps | No | 13.9 | 0 | 0 | 3.4 | 0 | 25 | 5 |  |  | 0 |  |  |  |  | 0 |  |  | #N/A | #N/A | [5 empty] | 0
|  |  | #N/A | #N/A | 0.75 | NA |  | Air-Source Heat Pumps | Yes | 13.5 | 0 | 0 | 3.3 | 0 | 25 | 5 |  |  | 0 |  |  |  |  | 0 |  |  | #N/A | #N/A | [5 empty] | 0
|  |  | #N/A | #N/A | 0.75 |  |  | 0 | 0 | [14 empty] | 0 |  |  | #N/A | #N/A | [5 empty] | 0
|  |  | #N/A | #N/A | 0.75 |  |  | 0 | 0 | [14 empty] | 0 |  |  | #N/A | #N/A | [5 empty] | 0
|  |  | #N/A | #N/A | 0.75 |  |  | 0 | 0 | [14 empty] | 0 |  |  | #N/A | #N/A | [5 empty] | 0
|  |  | #N/A | #N/A | 0.75 |  |  | 0 | 0 | [14 empty] | 0 |  |  | #N/A | #N/A | [5 empty] | 0
|  |  | #N/A | #N/A | 0.75 |  |  | 0 | 0 | [14 empty] | 0 |  |  | #N/A | #N/A | [5 empty] | 0
Geothermal - NC Baseline Savings
| NC_Cooling kWh Baseline Efficiency | NC_Heating kWh Baseline Efficiency | NC_kW Baseline Efficiency | NC_Motor Efficiency | NC_Pump Efficiency | NC_Baseline Cooling kWh Consumption | NC_Baseline Heating kWh Consumption | NC_Baseline Motor kWh Consumption | NC_Total kWh Consumption | NC_Baseline Cooling kW | NC_Baseline Motor kW | NC_Baseline Total kW | NC_kWh Savings | NC_kW Savings
| 12.1 | 2.5 | 12.1 |  | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #N/A | 0 | #N/A | #VALUE! | #N/A
| 14.3 | #REF! | 0 |  | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #N/A | 0 |  | #VALUE! | #VALUE!
| 13.4 | #REF! | 0 |  | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #N/A | 0 |  | #VALUE! | #VALUE!
| 13.9 | 3.4 | 0 |  | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #N/A | 0 |  | #VALUE! | #VALUE!
| 13.5 | 3.3 | 0 |  | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #N/A | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #N/A | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #N/A | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #N/A | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #N/A | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #N/A | 0 |  | #VALUE! | #VALUE!
Lifetime Savings
| Life of Equipment | Early Replacement Savings (kWh) | Early Replacement Savings (kW) | Remaining Useful Life | New Construction Savings (kWh) | New Construction Savings (kW) | Number of Years | Lifetime Savings (kWh) | Lifetime Savings (kW)
| 15 |  |  | #REF! | #VALUE! | #N/A | #REF! | #VALUE! | #VALUE!
| 15 |  |  | #REF! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE!
| 15 |  |  | #REF! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE!
| 15 |  |  | #REF! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE!
| 15 |  |  | #REF! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE!
| 15 |  |  | #REF! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE!
| 15 |  |  | #REF! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE!
| 15 |  |  | #REF! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE!
| 15 |  |  | #REF! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE!
| 15 |  |  | #REF! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE!
| Ductless Mini Split Calculations | [7 empty] | Converts COP to HSPF2 scale per TRM guidance
| Default Cooling EFLH | Default Heating EFLH | ETDF_summer | ETDF_winter | Baseline EER | Baseline SEER2 | Baseline COP | Baseline HSPF2 | Baseline Heating Efficiency | Baseline Cooling Efficiency | Proposed Heating Efficiency | Proposed Cooling Efficiency | Cooling kWh Baseline | Heating kWh Baseline | Total kWh Baseline | Total kW Baseline (Summer) | Total kW Baseline (Winter) | Cooling kWh Proposed | Heating kWh Proposed | Total kWh Proposed | Total kW Proposed (Summer) | Total kW Proposed (Winter) | Annual Energy Savings (kWh) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW) | Average Peak Demand Savings (kW)
| #N/A | #N/A | #N/A | #N/A | NA |  | NA |  |  |  | 0 | 0
| #N/A | #N/A | #N/A | #N/A | NA |  | NA |  |  |  | 0 | 0
| #N/A | #N/A | #N/A | #N/A | NA |  | NA |  |  |  | 0 | 0
| #N/A | #N/A | #N/A | #N/A | NA |  | NA |  |  |  | 0 | 0
| #N/A | #N/A | #N/A | #N/A | NA |  | NA |  |  |  | 0 | 0
| #N/A | #N/A | #N/A | #N/A | NA |  | NA |  |  |  | 0 | 0
| #N/A | #N/A | #N/A | #N/A | NA |  | NA |  |  |  | 0 | 0
| #N/A | #N/A | #N/A | #N/A | NA |  | NA |  |  |  | 0 | 0
| #N/A | #N/A | #N/A | #N/A | NA |  | NA |  |  |  | 0 | 0
| #N/A | #N/A | #N/A | #N/A | NA |  | NA |  |  |  | 0 | 0
Ref Charge Correction Calculations
| Cooling EFLH | Heating EFLH | Cooling Capacity | Heating Capacity | ETDF_summer | ETDF_winter | Baseline EER | Baseline SEER2 | Baseline IEER | Baseline COP | Baseline HSPF2 | RCF | Baseline Cooling Efficiency | Baseline Heating Efficiency | Cooling kWh | Heating kWh | Total kWh | Total kW (Summer) | Total kW (Winter) | Total kW (Average)
|  |  | 60000 | 0 | #N/A | #N/A |  | 13.4 |  | 0 |  | 97% | 13.4 | 0 |  | 0 |  |  | 0 | 0
|  |  | 120000 | 0 | #N/A | #N/A |  |  | 14.8 | 0 |  | 97% | 14.8 | 0 |  | 0 |  |  | 0 | 0
|  |  | 60000 | 55000 | #N/A | #N/A |  | 13.4 |  | 0 | 6.7 | 78% | 13.4 | 6.7 |  | 0
|  |  | 120000 | 110000 | #N/A | #N/A |  |  | 14.1 | FALSE |  | 98% | 14.1 | 0 |  | 0
|  |  | 0 | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 | 0
|  |  | 0 | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 | 0
|  |  | 0 | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 | 0
|  |  | 0 | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 | 0
|  |  | 0 | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 | 0
|  |  | 0 | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 | 0
HVAC Tune Up
| EFLH cool | EFLH heat | HVAC Equipment Type | Rated Cooling Capacity (BTU/hr) * | Rated Heating Capacity (BTU/hr)* | ETDF_summer | ETDF_winter | IEER | EER | SEER2 | COP | HSPF2 | Cooling Efficiency | Heating Efficiency | Tune-Up Components Implemented | ESF | Heating kWh Savings | Cooling kWh Savings | Total kWh savings | Total kW (Summer) | Total kW (Winter) | Total kW (Average)
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | 0 | 0 | 0 | [8 empty] | 0 | Refrigerant Charge Correction (<=20%) | 0.0068 | 0
|  |  | #N/A | #N/A
Room Air Conditioning Calculations
| EFLHc | CAPYc | Type | Louver Existence | CEER base | CEER ee | QTY | CF | Total kWh | Total kW (Summer) | Total kW (Winter) | Total kW (Average)
| #N/A | 0 | 0 | 0 |  | 0 | 0 | #N/A
| #N/A | 0 | 0 | 0 |  | 0 | 0 | #N/A
| #N/A | 0 | 0 | 0 |  | 0 | 0 | #N/A
| #N/A | 0 | 0 | 0 |  | 0 | 0 | #N/A
| #N/A | 0 | 0 | 0 |  | 0 | 0 | #N/A
| #N/A | 0 | 0 | 0 |  | 0 | 0 | #N/A
| #N/A | 0 | 0 | 0 |  | 0 | 0 | #N/A
| #N/A | 0 | 0 | 0 |  | 0 | 0 | #N/A
| #N/A | 0 | 0 | 0 |  | 0 | 0 | #N/A
| #N/A | 0 | 0 | 0 |  | 0 | 0 | #N/A
Guest Room Occ Sensor Calculations
Calculations
| Quantity | Cooling Energy Savings Factor (ESF_cool) | Heating Energy Savings Factor (ESF_heat) | ETDF_summer | ETDF_winter | Cooling kWh Savings | Heating kWh Savings | Total kWh Savings | Summer kW Savings | Winter kW Savings | Average kW Savings
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
Economizer Calculations
| Facility Defaults | Baseline Efficiency |  |  | Calculations
| Free Cooling Hours (FCHr) | EER | IEER | SEER2 | Cooling Efficiency | kWh Savings | Summer kW Savings | Winter kW Savings
|  | 11 | 0 | 13.4 | 13.4 |  | 0 | 0
|  | 11 | 14.8 | 0 | 14.8 |  | 0 | 0
|  | 11 | 14.2 | 0 | 14.2 |  | 0 | 0
|  | 11 | 13.2 | 0 | 13.2 |  | 0 | 0
|  | 11 | 0 | 0 | 11 |  | 0 | 0
|  | 11 | 0 | 0 | 11 |  | 0 | 0
|  | 11 | 0 | 0 | 11 |  | 0 | 0
|  | 11 | 0 | 0 | 11 |  | 0 | 0
|  | 11 | 0 | 0 | 11 |  | 0 | 0
|  | 11 | 0 | 0 | 11 |  | 0 | 0
Fuel Switching Calculations
| Facility Defaults |  | Baseline Efficiency |  |  | Efficiencies Used | Calculations |  | NC Baseline Savings Calculations
| EFLH_heat_Default | CF_Default | COP | HSPF | AFUE | Heating kWh Baseline Efficiency | Annual kWh Savings | Fuel Consumption Increase | NC_Heating kWh Baseline Efficiency | NC_Baseline kWh Consumption
|  |  | 1 | NA |  | #REF! |  | #VALUE! | 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | 3.412
Lifetime Savings
| Life of Equipment | Early Replacement Savings (kWh) | Remaining Useful Life | New Construction Savings (kWh) | Number of Years | Lifetime Savings (kWh)
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
Computer Room Air Conditioning Calculations
| Line Item | EFLHc | CAPYc | Type | Flow | SCOP base | SCOP ee | QTY | CF | kWh | kW(summer) | kW(winter) | kW(average) | Incentive
| 1 | 2000 | 36000 | Air-Cooled | Upflow Ducted | 2.67 | 3 | 1 | 1 | 869.3705 | 0.43469 | 0.43469 | 0.43469
| 2 | 2000 | 47000 | Glycol-Cooled | Upflow Ducted | 1.93 | 3 | 1 | 1 | 5091.2456 | 2.5456 | 2.5456 | 2.5456
| 3 | 2000 | 412500 | Glycol-Cooled | Upflow Ducted | 1.78 | 3 | 1 | 1 | 55241.2503 | 27.6206 | 27.6206 | 27.6206
| 4 | 2000 | 24000 | Glycol-Cooled | Upflow Ducted | 2.53 | 3 | 1 | 1 | 871.1407 | 0.43557 | 0.43557 | 0.43557
| 5 | 2000 | 47000 | Glycol-Cooled | Upflow Non-Ducted | 2.08 | 3 | 1 | 1 | 4061.833 | 2.0309 | 2.0309 | 2.0309
| 6 | 2000 | 412500 | Glycol-Cooled | Upflow Non-Ducted | 1.81 | 3 | 1 | 1 | 52989.7729 | 26.4949 | 26.4949 | 26.4949
| 7 | 2000 | 24000 | Glycol-Cooled with Fluid Economizer | Upflow Ducted | 1.92 | 3 | 1 | 1 | 2637.7491 | 1.3189 | 1.3189 | 1.3189
| 8 | 2000 | 47000 | Glycol-Cooled with Fluid Economizer | Upflow Ducted | 1.88 | 3 | 1 | 1 | 5470.8871 | 2.7354 | 2.7354 | 2.7354
| 9 | 2000 | 412500 | Glycol-Cooled with Fluid Economizer | Upflow Ducted | 1.73 | 3 | 1 | 1 | 59167.237 | 29.5836 | 29.5836 | 29.5836
| 10 | 2000 | 24000 | Glycol-Cooled with Fluid Economizer | Upflow Non-Ducted | 1.95 | 3 | 1 | 1 | 2525.0248 | 1.2625 | 1.2625 | 1.2625
| 10 | 2000 | 47000 | Glycol-Cooled with Fluid Economizer | Upflow Non-Ducted | 1.93 | 3 | 1 | 1 | 5091.2456 | 2.5456 | 2.5456 | 2.5456
| 10 | 2000 | 412500 | Glycol-Cooled with Fluid Economizer | Upflow Non-Ducted | 1.76 | 3 | 1 | 1 | 56784.8769 | 28.3924 | 28.3924 | 28.3924
Computer Room Air Conditioning ECM and VSD Calculations
| Line Item | ηbase fan | ηbase belt | ηbase motor | ηec fan | ηec drive | ηec motor | USDF | CLF | Horesepower | ηcooling | HOU | UF | Fan Power | CF | LF | Quantity | kWh ECM | Summer kW ECM | Winter kW ECM | Average kW ECM | kWh VSD | Summer kW VSD | Winter kW VSD | Average kW VSD | Incentive
| 1 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 79.82% | 0 | 0.95 | 8760 | 83% | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 79.82% | 0 | 0.95 | 8760 | 83% | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 79.82% | 0 | 0.95 | 8760 | 83% | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 79.82% | 0 | 0.95 | 8760 | 83% | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 79.82% | 0 | 0.95 | 8760 | 83% | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 79.82% | 0 | 0.95 | 8760 | 83% | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 79.82% | 0 | 0.95 | 8760 | 83% | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 79.82% | 0 | 0.95 | 8760 | 83% | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 79.82% | 0 | 0.95 | 8760 | 83% | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 79.82% | 0 | 0.95 | 8760 | 83% | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| High Volume Low Speed Fans | Baseline Quantity | Fans Installed | Eff base | Eff ee | CFM | Hours of Use | ETDF Summer | ETDF Winter | Annual Savings (kWh) | kW summer | kW winter | Peak Reduction (kW) average | Incentive
|  | 0 | 0 | 22.7 | #N/A | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | 22.7 | #N/A | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | 22.7 | #N/A | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | 22.7 | #N/A | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | 22.7 | #N/A | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | 22.7 | #N/A | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | 22.7 | #N/A | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | 22.7 | #N/A | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | 22.7 | #N/A | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | 22.7 | #N/A | 0 | #N/A | #N/A | #N/A
| Insulation Calculations | *Moved to bottom*
HVAC Baseline Efficiencies
| Facility Defaults |  |  |  | Cooling Efficiency |  |  | Heating Efficiency
| EFLH_cool_Default | CF_Default | CDD | HDD | IEER | EER2 | SEER | COP | HSPF
1
2
3
4
5
6
7
8
9
10
|  |  |  | Insulation Baseline Efficiencies |  | Insulation Efficiencies Used
| HVAC Efficiencies Used |  |  | Ceiling Insulation | Wall Insulation | Ceiling Insulation | Ceiling Insulation | Wall Insulation | Wall Insulation
| Cooling kWh Baseline Efficiency | Heating kWh Baseline Efficiency | kW Baseline Efficiency | R-Value of Existing Ceiling Insulation | R-Value of Existing Wall Insulation | R-Value of Existing Ceiling Insulation | R-Value of Proposed Ceiling Insulation | R-Value of Existing Wall Insulation | R-Value of Proposed Wall Insulation
| 0 | 0 | 0 |  |  |  | #REF! |  | #REF!
| 0 | 0 | 0 |  |  |  | #REF! |  | #REF!
| 14.8 | 3.4 | 0 |  |  |  | #REF! |  | #REF!
| 0 | 0 | 0 |  |  |  | #REF! |  | #REF!
| 0 | 0 | 0 |  |  |  | #REF! |  | #REF!
| 14.8 | 3.4 | 0 |  |  |  | #REF! |  | #REF!
[7 empty] | #REF! |  | #REF!
[7 empty] | #REF! |  | #REF!
[7 empty] | #REF! |  | #REF!
[7 empty] | #REF! |  | #REF!
Calculations
| Existing Cooling kWh | Existing Heating kWh | Existing kWh | Existing kW | Proposed Cooling kWh | Proposed Heating kWh | Proposed kWh | Proposed kW
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations
| NC_Cooling kWh Baseline Efficiency | NC_Heating kWh Baseline Efficiency | NC_kW Baseline Efficiency | NC_Ceiling R-Value | NC_Wall R-Value | NC_Baseline Cooling kWh Consumption | NC_Baseline Heating kWh Consumption | NC_Baseline Total kWh Consumption | NC_Baseline kW Consumption | NC_kWh Savings | NC_kW Savings
| 0 | 0 | 0 |  |  | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 0 | 0 | 0 |  |  | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 14.8 | 3.4 | 0 |  |  | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 0 | 0 | 0 |  |  | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 0 | 0 | 0 |  |  | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 14.8 | 3.4 | 0 |  |  | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Lifetime Savings
| Life of Equipment | Early Replacement Savings (kWh) | Early Replacement Savings (kW) | Remaining Useful Life | New Construction Savings (kWh) | New Construction Savings (kW) | Number of Years | Lifetime Savings (kWh) | Lifetime Savings (kW)
| 15 | 0 | #N/A | #REF! | #VALUE! | #VALUE! | #REF! | #REF! | #REF!
| 15 | 0 | #N/A | #REF! | #VALUE! | #VALUE! | #REF! | #REF! | #REF!
| 15 | 0 | #N/A | #REF! | #VALUE! | #VALUE! | #REF! | #REF! | #REF!
| 15 | 0 | #N/A | #REF! | #VALUE! | #VALUE! | #REF! | #REF! | #REF!
| 15 | 0 | #N/A | #REF! | #VALUE! | #VALUE! | #REF! | #REF! | #REF!
| 15 | 0 | #N/A | #REF! | #VALUE! | #VALUE! | #REF! | #REF! | #REF!
| 15 | 0 | #N/A | #REF! | #VALUE! | #VALUE! | #REF! | #REF! | #REF!
| 15 | 0 | #N/A | #REF! | #VALUE! | #VALUE! | #REF! | #REF! | #REF!
| 15 | 0 | #N/A | #REF! | #VALUE! | #VALUE! | #REF! | #REF! | #REF!
| 15 | 0 | #N/A | #REF! | #VALUE! | #VALUE! | #REF! | #REF! | #REF!
Smart Thermostat Calculations
| Project Type | Building Type | Weather Location | Quantity | Baseline Thermostat Type | HVAC Equipment Type | Heating Type | Rated Cooling Capacity (kBTU/hr) * | Capacity Heat pump | Capacity elect furn | Gas Blower Motor HP | Gas Blower Motor Efficiency | EFLH Cool | EFLH Heat | ETDFsummer | ETDFwinter | SEER2 | EER2 | Cooling Efficiency | HSPF2 | Eff duct | DFelecresistance | PDSF | ESFcool | ESFheat | kWh cool savings | kWh heat, HP Savings | kWh heat Elec resistance Savings | kWh heat, fuel furnace | kWh savings | Summer Peak Demand Savings | Winter Peak Demand Savings | Average Peak Demand Savings
|  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 50% |  |  | #N/A | #N/A |  |  |  |  | 0.83 | 0.85 | 0.25 |  |  | 0 | 0 | 0 | 0 |  |  |  | #DIV/0!
|  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 50% |  |  | #N/A | #N/A |  |  |  |  | 0.83 | 0.85 | 0.25 |  |  | 0 | 0 | 0 | 0 |  |  |  | #DIV/0!
|  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 50% |  |  | #N/A | #N/A |  |  |  |  | 0.83 | 0.85 | 0.25 |  |  | 0 | 0 | 0 | 0 |  |  |  | #DIV/0!
|  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 50% |  |  | #N/A | #N/A |  |  |  |  | 0.83 | 0.85 | 0.25 |  |  | 0 | 0 | 0 | 0 |  |  |  | #DIV/0!
|  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 50% |  |  | #N/A | #N/A |  |  |  |  | 0.83 | 0.85 | 0.25 |  |  | 0 | 0 | 0 | 0 |  |  |  | #DIV/0!
|  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 50% |  |  | #N/A | #N/A |  |  |  |  | 0.83 | 0.85 | 0.25 |  |  | 0 | 0 | 0 | 0 |  |  |  | #DIV/0!
|  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 50% |  |  | #N/A | #N/A |  |  |  |  | 0.83 | 0.85 | 0.25 |  |  | 0 | 0 | 0 | 0 |  |  |  | #DIV/0!
|  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 50% |  |  | #N/A | #N/A |  |  |  |  | 0.83 | 0.85 | 0.25 |  |  | 0 | 0 | 0 | 0 |  |  |  | #DIV/0!
|  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 50% |  |  | #N/A | #N/A |  |  |  |  | 0.83 | 0.85 | 0.25 |  |  | 0 | 0 | 0 | 0 |  |  |  | #DIV/0!
|  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 50% |  |  | #N/A | #N/A |  |  |  |  | 0.83 | 0.85 | 0.25 |  |  | 0 | 0 | 0 | 0 |  |  |  | #DIV/0!
Demand Controlled Ventilation
| Heating Type | Conditioned space | SFcooling | SFheatHP | SFelectricFan | SFheatER | ETDFsummer | ETDFwinter | kWh savings | kWsummer | kWwinter | kWaverage | $ Incentive
| 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Advanced Rooftop Controls
| CCAP | HCAP | NECES | NEHES | NHFES | Heatelectric | Heatnon-electric | ETDFsummer | ETDFwinter | kWhcool | kWhheat | Annual kWh | kWsummer | kWwinter | kWaverage
| 1 | 1 | 0 | 0 | 0 | 1 | 0 | #N/A | #N/A | 0 | 0 | 0
| 1 | 1 | 0 | 0 | 0 | 0 | 1 | #N/A | #N/A | 0 | 0 | 0
| 1 | 1 | 0 | 0 | 0 | 1 | 0 | #N/A | #N/A | 0 | 0 | 0
| 1 | 1 | 0 | 0 | 0 | 1 | 0 | #N/A | #N/A | 0 | 0 | 0
| 1 | 1 | 0 | 0 | 0 | 0 | 1 | #N/A | #N/A | 0 | 0 | 0
| 1 | 1 | 0 | 0 | 0 | 1 | 0 | #N/A | #N/A | 0 | 0 | 0
| 1 | 1 | 0 | 0 | 0 | 1 | 0 | #N/A | #N/A | 0 | 0 | 0
| 1 | 1 | 0 | 0 | 0 | 0 | 1 | #N/A | #N/A | 0 | 0 | 0
| 1 | 1 | 0 | 0 | 0 | 1 | 0 | #N/A | #N/A | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | 0 | 0
Insulation Calculations
| kBTU/houtcool | kBTU/houtheat | kWin | EFLHcool | EFLHheat | IEER | EER2 | SEER2 | Cooling Efficiency | COP | HSPF2 | Heating Efficiency (HSPF2 Basis) | TRFcool | TRFheat | ETDFsummer | ETDFwinter | Eff Dist cool base | Eff Dist cool ee | Eff Dist heat base | Eff Dist heat ee
| 0 | 0 | 1 |  |  | 0 | 0 | 13.4 | 13.4 | 0 | 6.7 | 6.7 | 6% | 12% | #N/A | #N/A | 0.806 | 0.934 | 0.583 | 0.79
| 12000 | 12000 | 0 |  |  | 0 | 0 | 13 | 13 | 0 | 6.7 | 6.7 | 30% | 60% | #N/A | #N/A | 0.81 | 0.941 | 0.596 | 0.815
| 72000 | 72000 | 0 |  |  | 14.8 | 0 | 0 | 14.8 | 3.4 | 0 | 11.6008 | 15% | 30% | #N/A | #N/A | 0.807 | 0.928 | 0.588 | 0.771
| 12000 | 0 | 0 |  |  | 0 | 0 | 13 | 13 | 0 | 0 | 0 | 30% | 30% | #N/A | #N/A | 0.818 | 0.932 | 0.626 | 0.783
| 12000 | 12000 | 0 |  |  | 0 | 0 | 13 | 13 | 0 | 6.7 | 6.7 | 15% | 30% | #N/A | #N/A | 0.812 | 0.943 | 0.605 | 0.822
| 72000 | 72000 | 0 |  |  | 14.8 | 0 | 0 | 14.8 | 3.4 | 0 | 11.6008 | 6% | 12% | #N/A | #N/A | 0.8 | 0.932 | 0.562 | 0.783
| 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28% | 30% | #N/A | #N/A | 0.81 | 0.823 | 0.596 | 0.643
| 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | #N/A | #N/A
| 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | #N/A | #N/A
| 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | #N/A | #N/A
Duct Sealing and Insulation
| kWhcool | kWhheat | kWh | kWsummer | kWwinter | kWaverage | Incentive
|  |  | 0 | #N/A | #N/A | #N/A
|  |  | 0 | #N/A | #N/A | #N/A
|  |  | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A
|  |  | 0 | #N/A | #N/A | #N/A
|  |  | 0 | #N/A | #N/A | #N/A
|  |  | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A
| CIRs | ETDFsummer | ETDFwinter | EFLHchiller | hconv | hrad | k | L | Q/ft | Rbare | Rcond | Rconv | Rins | Rrad | ro | ri | Tx | Tinf | kWh/ft | nchiller
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #N/A | 60 | 462 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.333 | 44 | 70 | #REF! | 0.8
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #N/A | #REF! | 463 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.333 | 44 | 70 | #REF! | 1.8
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #N/A | #REF! | 464 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.333 | 44 | 70 | #REF! | 2.8
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #N/A | #REF! | 465 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.333 | 44 | 70 | #REF! | 3.8
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #N/A | #REF! | 466 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.333 | 44 | 70 | #REF! | 4.8
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #N/A | #REF! | 467 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.333 | 44 | 70 | #REF! | 5.8
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #N/A | #REF! | 468 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.333 | 44 | 70 | #REF! | 6.8
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #N/A | #REF! | 469 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.333 | 44 | 70 | #REF! | 7.8
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #N/A | #REF! | 470 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.333 | 44 | 70 | #REF! | 8.8
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #N/A | #REF! | 471 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.333 | 44 | 70 | #REF! | 9.8
Chilled Water Pipe Insulation
| Pipe Length, ft | Energy Loss per LF, kWh/ft |  | ETDFsummer | ETDFwinter | EFLHchiller | kWh | kWsummer | kWwinter | kWaverage | Incentive
| 60 | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Note on W3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need to create ETDF lookup table to support this calculation.
Note on B17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: May be possible to delete this.
Note on B30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: May be possible to delete.
Note on B58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: May possible to delete.
Note on B71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: May be possible to delete.
Note on B100: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: May be possible to delete.
Note on B113: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: May be possible to delete.
Note on B229: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: May be possible to delete.

## Data Export (hidden)
|  | Quantity__c | Description_Product_Style__c | Total_Incentive_New__c |  | Annual_Electric_Energy_Savings_kwh__c | Child___Average_Demand_Savings_kW__c | Calculator_Version__c | Efficient_Seasonal_Energy_Ratio__c | Efficient_Heat_Seasonal_Prfrmnce_Factor__c | Factor_Text_2__c | Efficient_Energy_Efficiency_Ratio__c | Efficient_IEER__c | Efficient_COP__c | Cooling_BTUH__c | Heating_BTUH__c | Cooling_Capacity_tons__c | Baseline_IPLV__c | Efficient_IPLV__c | Baseline_Design_Efficiency_kW_ton__c | Efficient_Design_Efficiency_kW_ton__c | Certificate_of_Occupancy__c | Building_Type__c | Area_sqft__c | Operating_Schedule__c | Existing_Heating_System_Type__c | Existing_Cooling_System_Type__c | Existing_Energy_Efficiency_Ratio__c | Existing_IEER__c | Baseline_COP__c | Existing_Heat_Seasonal_Prfrmnce_Factor__c | Baseline_SEER__c | HVAC_System__c | Efficient_CEER__c | Baseline_CEER__c | Factor_Text_Yes_No__c | Factor_1__c | ENERGY_STAR_Unique_ID__c | Make__c | Model__c | Project_Type__c | Installation_Location__c | Existing_Thermostat_Type__c | Product_Id__c | Item_Description__c |  |  | Summer_Coincident_Peak_Demand_Savings_kW__c | Child___WC_Peak_Demand_Savings_kW__c | Date_Installed__c | Child___ETDF_Summer__c | Child___ETDF_Winter__c | Incentive_Unit__c | Energy_Savings_Factor__c | Cooling_ESF__c | Heating_ESF__c | Efficient_Energy_Factor__c
| Line Item | Measure Quantity | Measure Code Measure Description | Incentive | Project End Date | Total Energy Savings (kWh) | Total Energy Savings (kW) | Estimator Version Number | Efficient SEER | Efficient HSPF | Rating Condition | Efficient EER | Efficient IEER | Efficient COP | Cooling Capacity (btu/hr) | Heating Capacity (btu/hr) | Cooling Capacity Tons | Baseline IPLV | Efficient IPLV | Baseline Design Eff. kW/Ton Base | Efficient Design Eff. kW/Ton EE | CofO - Housekeeping Setback | Building Type | Area | Operating Schedule | Existing Heating System | Existing Cooling System | Baseline EER | Baseline IEER | Baseline COP | Baseline HSPF | Baseline SEER | HVAC System Type | Efficient CEER | Baseline CEER | Fuel Switching (Y/N) | Fuel Switching Savings therms | Energy Star Product ID | Manufacturer | Model Number | Project Type | Installation Location | Existing Thermostat Type | Product Id | Item Description | Nameplate Capacity | DSMT Measure Name | Summer kW | Winter kW | Install Date | ETDF Summer | ETDF Winter | Per Unit Incentive | ESF | ESFcool | ESFheat | Effee
HVAC Systems
Chiller |  |  |  | 0
0
0
0
0
0
0
0
0
0
Geothermal | 1 | 1 | CustHVAC |  |  |  |  | 5 |  |  | Ground Source Heat Pumps: Brine-to-Water | 25 |  | 5 | 120000 | 110000 | 10 | [5 empty] | 0 |  |  | Ground Source Heat Pumps: Brine-to-Water | Ground Source Heat Pumps: Brine-to-Water | [11 empty] | B | C | [6 empty] | Ground Source Heat Pumps: Brine-to-Water |  |  | 0
| 1 | 1 | CustHVAC |  |  |  |  | 5 |  |  | Ground Source Heat Pumps: Brine-to-Water | 25 |  | 5 | 60000 | 55000 | 5 | [5 empty] | 0 |  |  | New Construction | New Construction | [11 empty] | 0 | 0 | [6 empty] | Ground Source Heat Pumps: Brine-to-Water |  |  | 0
| 1 | 1 | CustHVAC |  |  |  |  | 5 |  |  | Ground Source Heat Pumps: Brine-to-Water | 25 |  | 5 | 60000 | 55000 | 5 | [5 empty] | 0 |  |  | New Construction | New Construction | [11 empty] | 0 | 0 | [6 empty] | Ground Source Heat Pumps: Brine-to-Water |  |  | 0
| 1 | 1 | CustHVAC |  |  |  |  | 5 |  |  | Ground Source Heat Pumps: Brine-to-Water | 25 |  | 5 | 120000 | 110000 | 10 | [5 empty] | 0 |  |  | New Construction | New Construction | [11 empty] | 0 | 0 | [6 empty] | Ground Source Heat Pumps: Brine-to-Water |  |  | 0
| 1 | 1 | CustHVAC |  |  |  |  | 5 |  |  | Ground Source Heat Pumps: Brine-to-Water | 25 |  | 5 | 180000 | 170000 | 15 | [5 empty] | 0 |  |  | New Construction | New Construction | [11 empty] | 0 | 0 | [6 empty] | Ground Source Heat Pumps: Brine-to-Water |  |  | 0
Ductless Mini-Splits
Fuel Switching
Refrigerant Charge Correction | 1 | 1 | CustHVACOpt | 0 |  |  |  | 5 |  |  | Air-Source Air Conditioners |  |  |  | 60000 | 0 | 5 | [5 empty] | 0 |  |  | Air-Source Air Conditioners | Air-Source Air Conditioners | 0 | 0 | 0 | 0 | 13.4 | Air-Source Air Conditioners | [5 empty] | 0 | 0 | [6 empty] | Refrigeration Correction |  |  | 0 |  |  | 0
| 1 | 1 | CustHVACOpt | 0 |  |  |  | 5 |  |  | Air-Source Air Conditioners |  |  |  | 120000 | 0 | 10 | [5 empty] | 0 |  |  | Air-Source Air Conditioners | Air-Source Air Conditioners | 0 | 14.8 | 0 | 0 | 0 | Air-Source Air Conditioners | [5 empty] | 0 | 0 | [6 empty] | Refrigeration Correction |  |  | 0 |  |  | 0
| 1 | 1 | CustHVACOpt | 0 |  |  |  | 5 |  |  | Air-Source Heat Pumps |  |  |  | 60000 | 55000 | 5 | [5 empty] | 0 |  |  | Air-Source Heat Pumps | Air-Source Heat Pumps | 0 | 0 | 0 | 6.7 | 13.4 | Air-Source Heat Pumps | [5 empty] | 0 | 0 | [6 empty] | Refrigeration Correction |  |  | 0 |  |  | 0
| 1 | 1 | CustHVACOpt | 0 |  |  |  | 5 |  |  | Air-Source Heat Pumps |  |  |  | 120000 | 110000 | 10 | [5 empty] | 0 |  |  | Air-Source Heat Pumps | Air-Source Heat Pumps | 0 | 14.1 | 3.4 | 0 | 0 | Air-Source Heat Pumps | [5 empty] | 0 | 0 | [6 empty] | Refrigeration Correction |  |  | 0 |  |  | 0
0
0
0
0
0
0
Room AC
Guest Room Occ
Economizers | 1 | 1 | EconSEER |  |  |  | 0 | 5 |  |  | Air-Source Air Conditioners |  |  |  | 60000 |  | 5 | [5 empty] | 0 | 10000 | 1 Shift, 5 days per week | Air-Source Air Conditioners | [12 empty] | 0 | 0 | [5 empty] | Nameplate Efficiency Values known | Economizer |  |  | 0
| 1 | 1 | EconIEER |  |  |  | 0 | 5 |  |  | Air-Source Air Conditioners |  |  |  | 120000 |  | 10 | [5 empty] | 0 | 10000 | 2 Shift, 5 days per week | Air-Source Air Conditioners | [12 empty] | 0 | 0 | [5 empty] | Nameplate Efficiency Values known | Economizer |  |  | 0
| 1 | 1 | EconIEER |  |  |  | 0 | 5 |  |  | Air-Source Air Conditioners |  |  |  | 180000 |  | 15 | [5 empty] | 0 | 10000 | 3 Shift, 5 days per week | Air-Source Air Conditioners | [12 empty] | 0 | 0 | [5 empty] | Nameplate Efficiency Values known | Economizer |  |  | 0
| 1 | 1 | EconIEER |  |  |  | 0 | 5 |  |  | Air-Source Air Conditioners |  |  |  | 500000 |  | 41.6667 | [5 empty] | 0 | 10000 | 24/7 | Air-Source Air Conditioners | [12 empty] | 0 | 0 | [5 empty] | Nameplate Efficiency Values known | Economizer |  |  | 0
Computer Room AC | 1 | 1 | CustHVAC | 0.086937 |  | 869.37 | 0.4347 | 5 |  |  | Air-Cooled |  |  | 3 | 36000 | [7 empty] | 0 | [15 empty] | senville | Leto | [6 empty] | Computer Room AC |  |  | 0 |  |  | 0.09
| 1 | 1 | CustHVACOpt |  |  | 5091.25 | 2.5456 | 5 |  |  | Glycol-Cooled |  |  | 3 | 47000 | [7 empty] | 0 | [15 empty] | senville | Leto | [6 empty] | Computer Room AC |  |  | 0
| 1 | 1 | EAC |  |  | 55241.25 | 27.6206 | 5 |  |  | Glycol-Cooled |  |  | 3 | 412500 | [7 empty] | 0 | [15 empty] | senville | Leto | [6 empty] | Computer Room AC |  |  | 0
| 1 | 1 | EAC IEER |  |  | 871.14 | 0.4356 | 5 |  |  | Glycol-Cooled |  |  | 3 | 24000 | [7 empty] | 0 | [15 empty] | senville | Leto | [6 empty] | Computer Room AC |  |  | 0
| 1 | 1 | EconIEER |  |  | 4061.83 | 2.0309 | 5 |  |  | Glycol-Cooled |  |  | 3 | 47000 | [7 empty] | 0 | [15 empty] | senville | Leto | [6 empty] | Computer Room AC |  |  | 0
| 1 | 1 | EconSEER |  |  | 52989.77 | 26.4949 | 5 |  |  | Glycol-Cooled |  |  | 3 | 412500 | [7 empty] | 0 | [15 empty] | senville | Leto | [6 empty] | Computer Room AC |  |  | 0
| 1 | 1 | ESRAC |  |  | 2637.75 | 1.3189 | 5 |  |  | Glycol-Cooled with Fluid Economizer |  |  | 3 | 24000 | [7 empty] | 0 | [15 empty] | senville | Leto | [6 empty] | Computer Room AC |  |  | 0
| 1 | 1 | GROOC Sensor |  |  | 5470.89 | 2.7354 | 5 |  |  | Glycol-Cooled with Fluid Economizer |  |  | 3 | 47000 | [7 empty] | 0 | [15 empty] | senville | Leto | [6 empty] | Computer Room AC |  |  | 0
| 1 | 1 | WCChill |  |  | 59167.24 | 29.5836 | 5 |  |  | Glycol-Cooled with Fluid Economizer |  |  | 3 | 412500 | [7 empty] | 0 | [15 empty] | senville | Leto | [6 empty] | Computer Room AC |  |  | 0
| 1 | 1 | WCEChill |  |  | 2525.02 | 1.2625 | 5 |  |  | Glycol-Cooled with Fluid Economizer |  |  | 3 | 24000 | [7 empty] | 0 | [15 empty] | senville | Leto | [6 empty] | Computer Room AC |  |  | 0
Computer Room AC ECM or VSD |  |  |  | 0
0
0
0
0
0
0
0
0
0
High Vol Low Speed Fans
Smart Thermostat
HVAC Tune Up
Formulas:
Date_Installed__c = IF([Quantity__c]="","", 'Inputs & Summary'!$C6)

## Lookups (hidden)
Lookups | [30 empty] | TRM 2026 Table 3-47
Cooling EFLHs | [10 empty] | Chiller EFLHs | [9 empty] | Free Cooling Hours by Operating Schedule | [9 empty] | Refrigerant Charge Correction Factor |  |  | Guest Room Controls | [5 empty] | Motor Efficiencies |  |  |  |  | Ground Pump Efficiencies |  | Degree Days | [8 empty] | MEASURE_CODE | MEASURE_DESC
Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport |  | Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Operating Schedule | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | % of nameplate charge added (removed) | TXV | Orifice | Building Type | Building Type Lookup Value | HVAC System Type | Housekeeping Setback | Cooling ESF Lookup | Heating ESF Lookup | Poles | Type | Motor HP | Helper column | Efficiency | HP | Minimum Pump Efficiency at Design Point (ηpump) | Space and/or Building Type | Allentown | Binghamton, NY | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | CAC<5.4Tons | HVAC Systems | PPL MEASURE_DESC | DSMT Description/Product Style | Data Model | PPL Commercial Downstream Measure List
Education - College/University | 870 | 436 | 513 | 664 | 729 | 895 | 701 | 741 | 678 |  | Education - College/University | 904 | 412 | 512 | 681 | 773 | 939 | 708 | 728 | 706 | 1 Shift, 5 days per week | 384 | 421 | 430 | 398 | 363 | 374 | 384 | 401 | 391 | 0.6 | 0.68 | 0.13 | Motel | Lodging - Small Hotel | PTAC with Electric Resistance Heat | Yes | 85 | 474 | 2 poles | Enclosed | 1 | 2 polesEnclosed1 | 0.77 | 1 | 0.65 | CDD | 787 | 747 | 620 | 955 | 1235 | 726 | 611 | 709 | CAC EER | HVAC Systems | Air-Cooled Electric Chillers | ACChill | Electric Chillers
Education - Other | 363 | 161 | 193 | 257 | 344 | 421 | 322 | 302 | 272 |  | Education - Other | 374 | 180 | 224 | 297 | 382 | 475 | 333 | 339 | 360 | 2 Shift, 5 days per week | 754 | 855 | 856 | 790 | 717 | 728 | 754 | 807 | 775 | 0.59 | 0.7 | 0.16 | Motel | Lodging - Small Hotel | PTAC with Electric Resistance Heat | No | 287 | 1590 | 2 poles | Enclosed | 1.5 | 2 polesEnclosed1.5 | 0.84 | 1.5 | 0.65 | HDD | 5318 | 5318 | 6353 | 4997 | 4709 | 5429 | 6176 | 5651 | CAC IEER | HVAC Systems | Commercial ASHP > 5.4 Tons EER | ASHP EER | HVAC Systems | Air Source Heat Pumps
Grocery | 889 | 537 | 753 | 884 | 503 | 654 | 753 | 603 | 504 |  | Health - Hospital | 1686 | 926 | 1147 | 1529 | 1512 | 1898 | 1398 | 1576 | 1377 | 3 Shift, 5 days per week | 1205 | 1274 | 1166 | 1260 | 1161 | 1170 | 1205 | 1258 | 1233 | 0.58 | 0.71 | 0.19 | Motel | Lodging - Small Hotel | PTAC with Gas Heat | Yes | 85 | 0 | 2 poles | Enclosed | 2 | 2 polesEnclosed2 | 0.855 | 2 | 0.65 | [9 empty] | ASHP<5.4Tons | HVAC Systems | Commercial ASHP > 5.4 Tons IEER | ASHP IEER | HVAC Systems | Air Source Heat Pumps
Health - Hospital | 1401 | 967 | 1358 | 1443 | 990 | 1292 | 930 | 1421 | 1155 |  | Health - Other | 624 | 344 | 425 | 567 | 577 | 759 | 557 | 581 | 527 | 24/7 | 1687 | 1761 | 1604 | 1744 | 1629 | 1646 | 1687 | 1746 | 1714 | 0.57 | 0.72 | 0.22 | Motel | Lodging - Small Hotel | PTAC with Gas Heat | No | 287 | 0 | 2 poles | Enclosed | 3 | 2 polesEnclosed3 | 0.865 | 3 | 0.67 | Ceiling and Wall Insulation Values | [8 empty] | ASHP EER | HVAC Systems | Commercial ASHP <= 5.4 Tons | ASHP<5.4Tons | HVAC Systems | Air Source Heat Pumps
Health - Other | 649 | 393 | 487 | 669 | 599 | 834 | 603 | 649 | 543 |  | Industrial Manufacturing | 963 | 445 | 549 | 733 | 777 | 952 | 745 | 798 | 700 | [10 empty] | 0.56 | 0.73 | 0.25 | Motel | Lodging - Small Hotel | PTHP | Yes | 85 | 175 | 2 poles | Enclosed | 5 | 2 polesEnclosed5 | 0.885 | 5 | 0.7 | Building Type | Wall Ri-Value (New Construction) | Wall Ri-Value (Existing) | Ceiling Ri-Value (New Construction) | Ceiling Ri-Value (Existing) | PA TRM assumed type |  |  |  | ASHP IEER | HVAC Systems | Commercial CAC > 5.4 Tons EER | CAC EER | HVAC Systems | Packaged Split A/C
Industrial Manufacturing | 775 | 357 | 430 | 571 | 684 | 832 | 625 | 619 | 545 |  | Lodging | 1900 | 1166 | 1373 | 1831 | 1677 | 2018 | 1690 | 1879 | 1613 | [10 empty] | 0.55 | 0.74 | 0.28 | Motel | Lodging - Small Hotel | PTHP | No | 287 | 736 | 2 poles | Enclosed | 7.5 | 2 polesEnclosed7.5 | 0.895 | 7.5 | 0.73 | Assembly | 14 | 2.5 | 24.4 | 13.4 | Warehouse |  |  |  | WEAC | HVAC Systems | Commercial CAC > 5.4 Tons IEER | CAC IEER | HVAC Systems | Packaged/Split AC
Institutional/Public Service | 1024 | 511 | 632 | 844 | 910 | 1326 | 833 | 874 | 781 |  | Office | 607 | 331 | 410 | 546 | 578 | 715 | 523 | 570 | 516 | [10 empty] | 0.54 | 0.76 | 0.31 | Hotel | Lodging - Large Hotel | PTAC with Electric Resistance Heat | Yes | 259 | 63 | 2 poles | Enclosed | 10 | 2 polesEnclosed10 | 0.902 | 10 | 0.75 | Education - Community College | 13 | 2 | 20 | 9 | Education |  |  |  | WEAC IEER | HVAC Systems | Commercial CAC <= 5.4 Tons | CAC<5.4Tons | HVAC Systems | Packaged/Split AC
Lodging | 1885 | 1193 | 1507 | 1935 | 1691 | 2113 | 1744 | 1874 | 1578 |  | Retail | 1019 | 513 | 635 | 847 | 928 | 1094 | 825 | 916 | 846 | [10 empty] | 0.53 | 0.77 | 0.33 | Hotel | Lodging - Large Hotel | PTAC with Electric Resistance Heat | No | 876 | 207 | 2 poles | Enclosed | 15 | 2 polesEnclosed15 | 0.91 | 15 | 0.77 | Education - Primary School | 13 | 2 | 20 | 9 | Education |  |  |  | EAC | HVAC Systems | Custom CHP | CHP | Custom Combined Heat and Power | Custom
Multifamily (Common Areas) | 1897 | 647 | 802 | 1069 | 1645 | 2009 | 1388 | 1377 | 1199 | [21 empty] | 0.52 | 0.78 | 0.36 | Hotel | Lodging - Large Hotel | PTAC with Gas Heat | Yes | 259 | 0 | 2 poles | Enclosed | 20 | 2 polesEnclosed20 | 0.91 | 20 | 0.77 | Education - Relocatable Classroom | 13 | 2 | 20 | 9 | Education |  |  |  | EAC IEER | HVAC Systems | Commercial DHP <5.4 Tons | CommDHP | Ductless mini-split heat pumps < 5.4 tons | Ductless Mini-split Heat Pump
Office | 623 | 211 | 449 | 573 | 627 | 859 | 851 | 695 | 531 |  |  | Table 3-41: Conversion Factors to Derive Air-Source Equivalent Metrics of a Ground Source Heat Pump | [18 empty] | 0.51 | 0.79 | 0.39 | Hotel | Lodging - Large Hotel | PTAC with Gas Heat | No | 876 | 0 | 2 poles | Open | 1 | 2 polesOpen1 | 0.77 |  |  | Education - Secondary School | 13 | 2 | 20 | 9 | Education |  |  |  | ACChill | Electric Chillers | Custom HVAC | CustHVAC | Custom HVAC | Custom
Restaurant | 748 | 425 | 520 | 713 | 655 | 965 | 746 | 726 | 677 |  |  | GSHP Type | GSER | GSOP | [16 empty] | 0.5 | 0.8 | 0.41 | Hotel | Lodging - Large Hotel | PTHP | Yes | 259 | 24 | 2 poles | Open | 1.5 | 2 polesOpen1.5 | 0.84 |  |  | Education - University | 13 | 2 | 20 | 9 | Education |  |  |  | WCChill | Electric Chillers | Custom HVAC Optimization | CustHVACOpt | Custom HVAC Optimization | Custom
Retail | 1000 | 530 | 645 | 862 | 824 | 1111 | 963 | 838 | 739 |  |  | Groundwater Source Heat Pumps: Water-to-Air | 1.04 | 0.81 | [16 empty] | 0.49 | 0.81 | 0.44 | Hotel | Lodging - Large Hotel | PTHP | No | 876 | 237 | 2 poles | Open | 2 | 2 polesOpen2 | 0.855 |  |  | Grocery | 13 | 2 | 20 | 9 | Grocery |  |  |  | WCEChill | Electric Chillers | Evaporated Cooled AC EER | EAC | HVAC Systems | Packaged/Split AC
Warehouse - Other | 237 | 96 | 120 | 158 | 261 | 422 | 227 | 181 | 203 |  |  | Ground Source Heat Pumps: Brine-to-Air | 1.03 | 0.87 | [16 empty] | 0.48 | 0.82 | 0.46 | Hotel | Lodging - Large Hotel | Central HW Fan Coil with Electric Resistance Heat | Yes | 182 | 63 | 2 poles | Open | 3 | 2 polesOpen3 | 0.855 |  |  | Health/Medical - Hospital | 13 | 2 | 20 | 9 | Health |  |  |  | CommDHP | Ductless mini-split heat pumps < 5.4 tons | Evaporated Cooled AC IEER | EAC IEER | HVAC Systems | Packaged/Split AC
Warehouse - Refrigerated | 4257 | 3018 | 4184 | 4281 | 3511 | 3904 | 3677 | 4301 | 3574 |  |  | Groundwater Source Heat Pumps: Water-to-Water | 0.93 | 0.84 | [16 empty] | 0.47 | 0.83 | 0.48 | Hotel | Lodging - Large Hotel | Central HW Fan Coil with Electric Resistance Heat | No | 615 | 207 | 2 poles | Open | 5 | 2 polesOpen5 | 0.865 |  |  | Health/Medical - Nursing Home | 13 | 2 | 20 | 9 | Health |  |  |  | GROOC Sensor | Guest Room Occupancy Sensor controls | Economizer> 5.4Tons IEER | EconIEER | Economizer controls | Economizer Controls
[12 empty] | Ground Source Heat Pumps: Brine-to-Water | 0.96 | 0.89 | [16 empty] | 0.46 | 0.84 | 0.51 | Hotel | Lodging - Large Hotel | Central HW Fan Coil with Gas Heat | Yes | 182 | 0 | 2 poles | Open | 7.5 | 2 polesOpen7.5 | 0.885 |  |  | Lodging - Hotel | 13 | 2 | 20 | 9 | Lodging |  |  |  | EconSEER | Economizer controls | Economizer units <=5.4 Tons | EconSEER | Economizer controls | Economizer Controls
Heating EFLHs | [30 empty] | 0.45 | 0.85 | 0.53 | Hotel | Lodging - Large Hotel | Central HW Fan Coil with Gas Heat | No | 615 | 0 | 2 poles | Open | 10 | 2 polesOpen10 | 0.895 |  |  | Manufacturing – Bio Tech/High Tech | 14 | 2.5 | 24.4 | 13.4 | Warehouse |  |  |  | EconIEER | Economizer controls | ENERGY STAR Room A/C | ESRAC | ENERGY STAR Room A/C | ENERGY STAR Room A/C
Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | [21 empty] | 0.44 | 0.86 | 0.55 | [6 empty] | 2 poles | Open | 15 | 2 polesOpen15 | 0.902 |  |  | Manufacturing – 1 Shift/Light Industrial | 14 | 2.5 | 24.4 | 13.4 | Warehouse |  |  |  | IncCorrect | Incentive Correction | Guest Room Occupancy Sensors | GROOC Sensor | Guest Room Occupancy Sensor controls | Guest Room Occupancy Sensor Controls
Education - College/University | 654 | 984 | 938 | 763 | 442 | 418 | 592 | 733 | 629 | [21 empty] | 0.43 | 0.86 | 0.57 | [6 empty] | 2 poles | Open | 20 | 2 polesOpen20 | 0.91 |  |  | Multi-Family (Common Areas) | 13 | 2 | 20 | 9 | Lodging |  |  |  | IncAdjust | Incentive Adjustment | Water Centrifugal Chiller | WCChill | Electric Chillers | Water Cooled Chillers
Education - Other | 579 | 910 | 886 | 593 | 593 | 581 | 804 | 823 | 629 | [21 empty] | 0.42 | 0.87 | 0.6 | [6 empty] | 4 poles | Enclosed | 1 | 4 polesEnclosed1 | 0.855 |  |  | Office - Large | 14 | 1.6 | 20 | 9 | Large Office |  |  |  | CustHVAC | Custom HVAC | Water Cooled Electric Chiller | WCEChill | Electric Chillers | Water Cooled Chillers
Grocery | 667 | 1068 | 929 | 475 | 1015 | 1095 | 513 | 1546 | 1362 | [21 empty] | 0.41 | 0.88 | 0.62 | [6 empty] | 4 poles | Enclosed | 1.5 | 4 polesEnclosed1.5 | 0.865 |  |  | Office - Small | 14 | 3 | 24.4 | 13.4 | Small Office |  |  |  | CHP | Custom Combined Heat and Power | Water cooled EER | WEAC | HVAC Systems | Packaged/Split AC
Health - Hospital | 134 | 81 | 62 | 85 | 289 | 311 | 380 | 94 | 148 | [21 empty] | 0.4 | 0.89 | 0.64 | [6 empty] | 4 poles | Enclosed | 2 | 4 polesEnclosed2 | 0.865 |  |  | Restaurant - Fast-Food | 14 | 3.2 | 20 | 9 | Restaurant |  |  |  | HVLSFANSHVAC |  | Water cooled IEER | WEAC IEER | HVAC Systems | Packaged/Split AC
Health - Other | 859 | 1432 | 1418 | 1161 | 683 | 725 | 931 | 1062 | 920 | [21 empty] | 0.39 | 0.89 | 0.65 | [6 empty] | 4 poles | Enclosed | 3 | 4 polesEnclosed3 | 0.895 |  |  | Restaurant - Sit-Down | 14 | 3.2 | 20 | 9 | Restaurant |  |  |  | CustHVACOpt | Custom HVAC Optimization | High Volume Low Speed fans | HVLSFANS | High Volume Low Speed fans | High Volume Low Speed Fans
Industrial Manufacturing | 369 | 500 | 494 | 421 | 299 | 305 | 364 | 392 | 332 | [21 empty] | 0.38 | 0.9 | 0.67 | [6 empty] | 4 poles | Enclosed | 5 | 4 polesEnclosed5 | 0.895 |  |  | Retail - Multistory Large | 14 | 3 | 20 | 9 | Large Retail |  |  |  | ESRAC | ENERGY STAR Room A/C | Smart Thermostat | Smart Thermostat - Description | Smart Thermostat - Data Model | ENERGY STAR Smart Thermostat
Institutional/Public Service | 1072 | 1489 | 1496 | 1279 | 878 | 1009 | 1058 | 1247 | 1023 |  | Chiller CFs | [19 empty] | 0.37 | 0.91 | 0.69 | [6 empty] | 4 poles | Enclosed | 7.5 | 4 polesEnclosed7.5 | 0.917 |  |  | Retail - Single-Story Large | 14 | 3 | 20 | 9 | Large Retail | [5 empty] | HVAC Tune Up | HVAC Tune Up - Description | HVAC Tune Up - Data Model | HVAC Tune Up
Lodging | 2158 | 3219 | 3346 | 2739 | 1727 | 1815 | 2194 | 2306 | 2307 |  | Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | [10 empty] | 0.36 | 0.91 | 0.71 | [6 empty] | 4 poles | Enclosed | 10 | 4 polesEnclosed10 | 0.917 |  |  | Retail - Small | 14 | 3 | 20 | 9 | Small Retail
Multifamily (Common Areas) | 252 | 320 | 308 | 287 | 210 | 233 | 240 | 250 | 267 |  | Education - College/University | 0.42 | 0.28 | 0.23 | 0.31 | 0.43 | 0.46 | 0.41 | 0.34 | 0.4 | [10 empty] | 0.35 | 0.92 | 0.73 | [6 empty] | 4 poles | Enclosed | 15 | 4 polesEnclosed15 | 0.924 |  |  | Storage - Conditioned | 14 | 2.5 | 24.4 | 13.4 | Warehouse
Office | 292 | 159 | 458 | 376 | 264 | 253 | 313 | 293 | 326 |  | Education - Other | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17 | [10 empty] | 0.34 | 0.92 | 0.74 | [6 empty] | 4 poles | Enclosed | 20 | 4 polesEnclosed20 | 0.93 |  |  | Warehouse - Refrigerated | 14 | 2.5 | 24.4 | 13.4 | Warehouse
Restaurant | 1047 | 1865 | 1835 | 1501 | 832 | 894 | 1219 | 1336 | 1191 |  | Health - Hospital | 0.5 | 0.45 | 0.42 | 0.48 | 0.5 | 0.54 | 0.48 | 0.48 | 0.5 | [10 empty] | 0.33 | 0.93 | 0.76 | [6 empty] | 4 poles | Open | 1 | 4 polesOpen1 | 0.855
Retail | 736 | 1085 | 1062 | 872 | 518 | 569 | 711 | 761 | 648 |  | Health - Other | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26 | [10 empty] | 0.32 | 0.94 | 0.77 | [6 empty] | 4 poles | Open | 1.5 | 4 polesOpen1.5 | 0.865
Warehouse - Other | 771 | 1108 | 1094 | 991 | 674 | 810 | 890 | 897 | 768 |  | Industrial Manufacturing | 0.53 | 0.41 | 0.33 | 0.43 | 0.53 | 0.58 | 0.54 | 0.48 | 0.5 | [10 empty] | 0.31 | 0.94 | 0.79 | [6 empty] | 4 poles | Open | 2 | 4 polesOpen2 | 0.865
Warehouse - Refrigerated | 330 | 613 | 581 | 475 | 246 | 200 | 372 | 391 | 315 |  | Lodging | 0.62 | 0.59 | 0.54 | 0.61 | 0.68 | 0.69 | 0.71 | 0.6 | 0.68 | [10 empty] | 0.3 | 0.95 | 0.8 | [6 empty] | 4 poles | Open | 3 | 4 polesOpen3 | 0.895
[11 empty] | Office | 0.29 | 0.24 | 0.21 | 0.27 | 0.35 | 0.23 | 0.32 | 0.29 | 0.32 | [10 empty] | 0.29 | 0.95 | 0.82 | [6 empty] | 4 poles | Open | 5 | 4 polesOpen5 | 0.895
Space and/or Building Type |  | Energy to Demand Factors (ETDFs) | [8 empty] | Retail | 0.46 | 0.34 | 0.28 | 0.38 | 0.54 | 0.55 | 0.48 | 0.43 | 0.48 | [10 empty] | 0.28 | 0.95 | 0.83 | [6 empty] | 4 poles | Open | 7.5 | 4 polesOpen7.5 | 0.91
Sub-Category | Main Category | ASHP/PTHP |  | AC/PTAC/Electric Chillers | [26 empty] | 0.27 | 0.96 | 0.84 | [6 empty] | 4 poles | Open | 10 | 4 polesOpen10 | 0.917
|  | ETDF_summer | ETDF_winter | ETDF_summer | ETDF_winter | [25 empty] | 0.26 | 0.96 | 0.85 | [6 empty] | 4 poles | Open | 15 | 4 polesOpen15 | 0.93
Data Center - No Economizer | Data Center | 0.00062838 | 0.00037862 | 0.00062838 | 3.966e-06 | [25 empty] | 0.25 | 0.97 | 0.87 | [6 empty] | 4 poles | Open | 20 | 4 polesOpen20 | 0.93
Data Center - With Economizer | Data Center | 0.00062838 | 0.00037862 | 0.00062838 | 3.966e-06 | [25 empty] | 0.24 | 0.97 | 0.88 | [6 empty] | 6 poles | Enclosed | 1 | 6 polesEnclosed1 | 0.825
Education - College/University | Education - College/University | 0.0005511 | 0.00039922 | 0.0005511 | 7.615e-06 | [25 empty] | 0.23 | 0.97 | 0.89 | [6 empty] | 6 poles | Enclosed | 1.5 | 6 polesEnclosed1.5 | 0.875
Education - Primary School | Education - Other | 0.00054016 | 0.00038547 | 0.00054016 | 9.855e-06 | [25 empty] | 0.22 | 0.98 | 0.9 | [6 empty] | 6 poles | Enclosed | 2 | 6 polesEnclosed2 | 0.885
Education - Secondary School | Education - Other | 0.0005511 | 0.00039922 | 0.0005511 | 7.615e-06 | [25 empty] | 0.21 | 0.98 | 0.91 | [6 empty] | 6 poles | Enclosed | 3 | 6 polesEnclosed3 | 0.895
Grocery | Grocery | 0.00046255 | 0.00035074 | 0.00046255 | 1.4563e-05 | [25 empty] | 0.2 | 0.98 | 0.92 | [6 empty] | 6 poles | Enclosed | 5 | 6 polesEnclosed5 | 0.895
Health - Hospital | Health - Hospital | 0.00030227 | 0.00029534 | 0.00030227 | 1.1491e-05 | [25 empty] | 0.19 | 0.98 | 0.92 | [6 empty] | 6 poles | Enclosed | 7.5 | 6 polesEnclosed7.5 | 0.91
Health - Other | Health - Other | 0.00039045 | 0.0003181 | 0.00039045 | 1.7713e-05 | [25 empty] | 0.18 | 0.99 | 0.93 | [6 empty] | 6 poles | Enclosed | 10 | 6 polesEnclosed10 | 0.91
Industrial Manufacturing - 1 Shift | Industrial Manufacturing | 0.00062838 | 0.00037862 | 0.00062838 | 3.966e-06 | [25 empty] | 0.17 | 0.99 | 0.94 | [6 empty] | 6 poles | Enclosed | 15 | 6 polesEnclosed15 | 0.917
Industrial Manufacturing - 2 Shift | Industrial Manufacturing | 0.00062838 | 0.00037862 | 0.00062838 | 3.966e-06 | [25 empty] | 0.16 | 0.99 | 0.95 | [6 empty] | 6 poles | Enclosed | 20 | 6 polesEnclosed20 | 0.917
Industrial Manufacturing - 3 Shift | Industrial Manufacturing | 0.00062838 | 0.00037862 | 0.00062838 | 3.966e-06 | [25 empty] | 0.15 | 0.99 | 0.95 | [6 empty] | 6 poles | Open | 1 | 6 polesOpen1 | 0.825
Institutional/Public Service | Institutional/Public Service | 0.00031638 | 0.00030642 | 0.00031638 | 3.5531e-05 | [25 empty] | 0.14 | 0.99 | 0.96 | [6 empty] | 6 poles | Open | 1.5 | 6 polesOpen1.5 | 0.865
Large Office | Office | 0.00031638 | 0.00030642 | 0.00031638 | 3.5531e-05 | [25 empty] | 0.13 | 1 | 0.97 | [6 empty] | 6 poles | Open | 2 | 6 polesOpen2 | 0.875
Lodging - Large Hotel | Lodging | 0.00029489 | 0.00037578 | 0.00029489 | 4.7198e-05 | [25 empty] | 0.12 | 1 | 0.97 | [6 empty] | 6 poles | Open | 3 | 6 polesOpen3 | 0.885
Lodging - Small Hotel | Lodging | 0.0002474 | 0.00041121 | 0.0002474 | 4.3987e-05 | [25 empty] | 0.11 | 1 | 0.98 | [6 empty] | 6 poles | Open | 5 | 6 polesOpen5 | 0.895
Medium Office | Office | 0.0004272 | 0.00035944 | 0.0004272 | 2.0284e-05 | [25 empty] | 0.1 | 1 | 0.98 | [6 empty] | 6 poles | Open | 7.5 | 6 polesOpen7.5 | 0.902
Multifamily Common Areas | Multifamily (Common Areas) | 0.0002474 | 0.00041121 | 0.0002474 | 4.3987e-05 | [25 empty] | 0.09 | 1 | 0.98 | [6 empty] | 6 poles | Open | 10 | 6 polesOpen10 | 0.917
Restaurant - Full Service | Restaurant | 0.00048491 | 0.00030256 | 0.00048491 | 2.3505e-05 | [25 empty] | 0.08 | 1 | 0.99 | [6 empty] | 6 poles | Open | 15 | 6 polesOpen15 | 0.917
Restaurant - Quick Service | Restaurant | 0.00035901 | 0.0003348 | 0.00035901 | 4.9439e-05 | [25 empty] | 0.07 | 1 | 0.99 | [6 empty] | 6 poles | Open | 20 | 6 polesOpen20 | 0.924
Retail - Standalone | Retail | 0.0004876 | 0.00032604 | 0.0004876 | 7.464e-06 | [25 empty] | 0.06 | 1 | 0.99 | [6 empty] | 8 poles | Enclosed | 1 | 8 polesEnclosed1 | 0.755
Retail - Strip Mall | Retail | 0.00046255 | 0.00035074 | 0.00046255 | 1.4563e-05 | [25 empty] | 0.05 | 1 | 1 | [6 empty] | 8 poles | Enclosed | 1.5 | 8 polesEnclosed1.5 | 0.785
Small Office | Office | 0.00058566 | 0.00040403 | 0.00058566 | 4.985e-06 | [25 empty] | 0.04 | 1 | 1 | [6 empty] | 8 poles | Enclosed | 2 | 8 polesEnclosed2 | 0.84
Warehouse - Other | Warehouse - Other | 0.00062838 | 0.00037862 | 0.00062838 | 3.966e-06 | [25 empty] | 0.03 | 1 | 1 | [6 empty] | 8 poles | Enclosed | 3 | 8 polesEnclosed3 | 0.855
Warehouse - Refrigerated | Warehouse - Refrigerated | 0.00062838 | 0.00037862 | 0.00062838 | 3.966e-06 | [25 empty] | 0.02 | 1 | 1 | [6 empty] | 8 poles | Enclosed | 5 | 8 polesEnclosed5 | 0.865
[31 empty] | 0.01 | 1 | 1 | [6 empty] | 8 poles | Enclosed | 7.5 | 8 polesEnclosed7.5 | 0.865
[31 empty] | 0 | 1 | 1 | [6 empty] | 8 poles | Enclosed | 10 | 8 polesEnclosed10 | 0.895
Room Air Conditioner CFs | [30 empty] | -0.01 | 1 | 1 | [6 empty] | 8 poles | Enclosed | 15 | 8 polesEnclosed15 | 0.895
Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | [21 empty] | -0.02 | 1 | 1 | [6 empty] | 8 poles | Enclosed | 20 | 8 polesEnclosed20 | 0.902
Education - College/University | 0.48 | 0.4 | 0.37 | 0.38 | 0.48 | 0.51 | 0.48 | 0.45 | 0.49 | [21 empty] | -0.03 | 1 | 1 | [6 empty] | 8 poles | Open | 1 | 8 polesOpen1 | 0.755
Education - Other | 0.12 | 0.09 | 0.07 | 0.09 | 0.18 | 0.19 | 0.18 | 0.13 | 0.15 | [21 empty] | -0.04 | 1 | 1 | [6 empty] | 8 poles | Open | 1.5 | 8 polesOpen1.5 | 0.77
Grocery | 0.33 | 0.26 | 0.26 | 0.27 | 0.24 | 0.26 | 0.27 | 0.21 | 0.24 | [21 empty] | -0.05 | 1 | 0.99 | [6 empty] | 8 poles | Open | 2 | 8 polesOpen2 | 0.865
Health - Hospital | 0.43 | 0.36 | 0.34 | 0.37 | 0.39 | 0.44 | 0.39 | 0.37 | 0.42 | [21 empty] | -0.06 | 1 | 0.99 | [6 empty] | 8 poles | Open | 3 | 8 polesOpen3 | 0.875
Health - Other | 0.26 | 0.25 | 0.23 | 0.27 | 0.3 | 0.34 | 0.32 | 0.28 | 0.29 | [21 empty] | -0.07 | 0.99 | 0.99 | [6 empty] | 8 poles | Open | 5 | 8 polesOpen5 | 0.885
Industrial Manufacturing | 0.51 | 0.37 | 0.33 | 0.39 | 0.55 | 0.6 | 0.53 | 0.45 | 0.48 | [21 empty] | -0.08 | 0.99 | 0.99 | [6 empty] | 8 poles | Open | 7.5 | 8 polesOpen7.5 | 0.895
Institutional/Public Service | 0.53 | 0.38 | 0.34 | 0.45 | 0.6 | 0.72 | 0.56 | 0.48 | 0.52 | [21 empty] | -0.09 | 0.99 | 0.98 | [6 empty] | 8 poles | Open | 10 | 8 polesOpen10 | 0.902
Lodging | 0.72 | 0.73 | 0.71 | 0.77 | 0.78 | 0.83 | 0.83 | 0.73 | 0.78 | [21 empty] | -0.1 | 0.99 | 0.98 | [6 empty] | 8 poles | Open | 15 | 8 polesOpen15 | 0.902
Multifamily (Common Areas) | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | [21 empty] | -0.11 | 0.99 | 0.97 | [6 empty] | 8 poles | Open | 20 | 8 polesOpen20 | 0.91
Office | 0.32 | 0.16 | 0.26 | 0.31 | 0.41 | 0.27 | 0.35 | 0.36 | 0.37 | [21 empty] | -0.12 | 0.99 | 0.97
Restaurant | 0.38 | 0.36 | 0.33 | 0.37 | 0.42 | 0.5 | 0.49 | 0.39 | 0.45 |  | Eff For AC | [19 empty] | -0.13 | 0.99 | 0.96
Retail | 0.52 | 0.45 | 0.42 | 0.46 | 0.53 | 0.57 | 0.56 | 0.47 | 0.49 |  | [Cooling Capacity] | [Cooling Efficiency Default] | [Cooling Efficiency EER Lookup] | [17 empty] | -0.14 | 0.98 | 0.96
Warehouse - Other | 0.18 | 0.11 | 0.1 | 0.13 | 0.24 | 0.3 | 0.23 | 0.15 | 0.2 |  | < 65000 | 13 | 11.3 | [17 empty] | -0.15 | 0.98 | 0.95
Warehouse - Refrigerated | 0.5 | 0.47 | 0.45 | 0.48 | 0.52 | 0.53 | 0.51 | 0.48 | 0.51 |  | >= 65000 and < 135000 | 11.4 | 11.2 | [17 empty] | -0.16 | 0.98 | 0.95
[11 empty] | >= 135000 and < 240000 | 11.2 | 11 | [17 empty] | -0.17 | 0.98 | 0.94
[11 empty] | = 240000 | 10.1 | 10 | [17 empty] | -0.18 | 0.98 | 0.93
[31 empty] | -0.19 | 0.98 | 0.93
[12 empty] | EFF for HP | [18 empty] | -0.2 | 0.97 | 0.92
[12 empty] | [Cooling Capacity] | [Cooling Efficiency Default] | [Cooling Efficiency EER Lookup] | [16 empty] | -0.21 | 0.97 | 0.91
[12 empty] | < 65000 | 13 | 11.3 | [16 empty] | -0.22 | 0.97 | 0.9
[12 empty] | >= 65000 and < 135000 | 11.2 | 11 | [16 empty] | -0.23 | 0.97 | 0.9
[12 empty] | >= 135000 and < 240000 | 10.7 | 10.6 | [16 empty] | -0.24 | 0.97 | 0.89
[12 empty] | = 240000 | 9.6 | 9.5 | [16 empty] | -0.25 | 0.96 | 0.88
[31 empty] | -0.26 | 0.96 | 0.87
COMPUTER ROOM AC SCOP | [11 empty] | Eff for HP | [18 empty] | -0.27 | 0.96 | 0.86
System Type | Flow Direction | Concatenate | Capacity | SCOP | [7 empty] | [Heating Capacity] | [Heating Efficiency Default] | [17 empty] | -0.28 | 0.96 | 0.85
Computer Room Air Conditioner Air Cooled | Upflow | Computer Room Air Conditioner Air Cooled Upflow <65,000 BTU/hr | <65,000 BTU/hr | 2.09 | [7 empty] | < 65000 | 7.7 | [17 empty] | -0.29 | 0.95 | 0.84
Computer Room Air Conditioner Air Cooled | Upflow | Computer Room Air Conditioner Air Cooled Upflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 1.99 | [7 empty] | >= 65000 and < 135000 | 3.3 | [17 empty] | -0.3 | 0.95 | 0.83
Computer Room Air Conditioner Air Cooled | Upflow | Computer Room Air Conditioner Air Cooled Upflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 1.79 | [7 empty] | >= 135000 and < 240000 | 3.2 | [17 empty] | -0.31 | 0.95 | 0.82
Computer Room Air Conditioner Air Cooled | Downflow | Computer Room Air Conditioner Air Cooled Downflow <65,000 BTU/hr | <65,000 BTU/hr | 2.2 | [7 empty] | = 240000 | 3.2 | [17 empty] | -0.32 | 0.95 | 0.81
Computer Room Air Conditioner Air Cooled | Downflow | Computer Room Air Conditioner Air Cooled Downflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.1 | [26 empty] | -0.33 | 0.95 | 0.8
Computer Room Air Conditioner Air Cooled | Downflow | Computer Room Air Conditioner Air Cooled Downflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 1.9 | [26 empty] | -0.34 | 0.94 | 0.78
Computer Room Air Conditioner Water Cooled | Upflow | Computer Room Air Conditioner Water Cooled Upflow <65,000 BTU/hr | <65,000 BTU/hr | 2.49 | [26 empty] | -0.35 | 0.94 | 0.77
Computer Room Air Conditioner Water Cooled | Upflow | Computer Room Air Conditioner Water Cooled Upflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.39
Computer Room Air Conditioner Water Cooled | Upflow | Computer Room Air Conditioner Water Cooled Upflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.29
Computer Room Air Conditioner Water Cooled | Downflow | Computer Room Air Conditioner Water Cooled Downflow <65,000 BTU/hr | <65,000 BTU/hr | 2.6
Computer Room Air Conditioner Water Cooled | Downflow | Computer Room Air Conditioner Water Cooled Downflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.5
Computer Room Air Conditioner Water Cooled | Downflow | Computer Room Air Conditioner Water Cooled Downflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.4
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Upflow <65,000 BTU/hr | <65,000 BTU/hr | 2.44
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Upflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.34
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Upflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.24
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Downflow <65,000 BTU/hr | <65,000 BTU/hr | 2.55
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Downflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.45
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Downflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.35
Computer Room Air Conditioner Glycol Cooled | Upflow | Computer Room Air Conditioner Glycol Cooled Upflow <65,000 BTU/hr | <65,000 BTU/hr | 2.39
Computer Room Air Conditioner Glycol Cooled | Upflow | Computer Room Air Conditioner Glycol Cooled Upflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.04
Computer Room Air Conditioner Glycol Cooled | Upflow | Computer Room Air Conditioner Glycol Cooled Upflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 1.99
Computer Room Air Conditioner Glycol Cooled | Downflow | Computer Room Air Conditioner Glycol Cooled Downflow <65,000 BTU/hr | <65,000 BTU/hr | 2.5
Computer Room Air Conditioner Glycol Cooled | Downflow | Computer Room Air Conditioner Glycol Cooled Downflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.15
Computer Room Air Conditioner Glycol Cooled | Downflow | Computer Room Air Conditioner Glycol Cooled Downflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.1
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Upflow <65,000 BTU/hr | <65,000 BTU/hr | 2.34
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Upflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 1.99
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Upflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 1.94
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Downflow <65,000 BTU/hr | <65,000 BTU/hr | 2.45
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Downflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.1
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Downflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.05
High Volume Low Speed Fan Hours of Use
Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Education - College/University | 1525 | 1420 | 1451 | 1427 | 1171 | 1313 | 1293 | 1474 | 1307
Education - Other | 942 | 1071 | 1079 | 850 | 937 | 1002 | 1127 | 1125 | 901
Grocery | 1556 | 1605 | 1683 | 1359 | 1518 | 1749 | 1266 | 2149 | 1866
Health - Hospital | 1535 | 1048 | 1420 | 1527 | 1279 | 1602 | 1310 | 1515 | 1303
Health - Other | 1508 | 1825 | 1905 | 1829 | 1283 | 1559 | 1534 | 1711 | 1462
Industrial Manufacturing | 1145 | 857 | 924 | 992 | 983 | 1137 | 989 | 1011 | 877
Institutional/Public Service | 2096 | 2000 | 2128 | 2123 | 1789 | 2335 | 1891 | 2121 | 1804
Lodging | 4043 | 4412 | 4853 | 4673 | 3418 | 3928 | 3938 | 4180 | 3885
Multifamily (Common Areas) | 2149 | 967 | 1110 | 1355 | 1855 | 2242 | 1628 | 1628 | 1466
Office | 915 | 370 | 907 | 948 | 891 | 1112 | 1164 | 988 | 858
Restaurant | 1795 | 2290 | 2355 | 2215 | 1487 | 1859 | 1965 | 2061 | 1869
Retail | 1736 | 1615 | 1707 | 1734 | 1342 | 1680 | 1674 | 1599 | 1387
Warehouse - Other | 1007 | 1204 | 1214 | 1150 | 935 | 1232 | 1117 | 1078 | 971
Warehouse - Refrigerated | 4587 | 3631 | 4765 | 4756 | 1757 | 4104 | 4049 | 4691 | 3889
Duct Insulation
3-80: Thermal Regain Factor
Unconditioned Space Type | TRF_cool |  |  | TRF_heat
| 0 | 0.5 | 0.8 | 0 | 0.5 | 0.8
Attic | 0.1 | 0.05 | 0.02 | 0.1 | 0.05 | 0.02
Basement, Uninsulated | 0.5 | 0.25 | 0.1 | 0.5 | 0.25 | 0.1
Basement, Insulated Walls | 0.6 | 0.3 | 0.12 | 0.6 | 0.3 | 0.12
Vented Crawl, Uninsulated | 0.55 | 0.28 | 0.11 | 0.6 | 0.3 | 0.12
Vented Crawl, Insulated Frame Floor | 0.3 | 0.15 | 0.06 | 0.3 | 0.15 | 0.06
Vented Crawl, Ins. Frame Floor & Crawl Walls | 0.6 | 0.3 | 0.12 | 0.63 | 0.32 | 0.13
Unvented Crawl, Uninsulated | 0.6 | 0.3 | 0.12 | 0.6 | 0.3 | 0.12
Unvented Crawl, Insulated Frame Floor | 0.3 | 0.15 | 0.06 | 0.3 | 0.15 | 0.06
Unvented Crawl, Ins. Frame Floor & Crawl Walls | 0.3 | 0.15 | 0.06 | 0.6 | 0.3 | 0.12
3-82: Energy Loss Due to Bare Unisnulated CH Water Pipe
Space/Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Education - College/University | 41.44 | 18.87 | 23.44 | 31.2 | 35.39 | 43.04 | 32.44 | 33.37 | 32.33
Education - Other | 17.13 | 8.25 | 10.25 | 13.63 | 17.49 | 21.74 | 15.25 | 15.54 | 16.5
Health - Hospital | 77.26 | 42.41 | 52.54 | 70.05 | 69.26 | 86.97 | 64.06 | 72.22 | 63.09
Health - Other | 28.6 | 15.74 | 19.49 | 25.98 | 26.44 | 34.77 | 25.52 | 26.62 | 24.13
Industrial Manufacturing | 44.11 | 20.37 | 25.15 | 33.56 | 35.6 | 43.6 | 34.11 | 36.55 | 32.07
Lodging | 87.04 | 53.43 | 62.92 | 83.87 | 76.84 | 92.45 | 77.42 | 86.1 | 73.9
Office | 27.79 | 15.15 | 18.79 | 25.03 | 26.5 | 32.75 | 23.95 | 26.11 | 23.66
Retail | 46.67 | 23.49 | 29.1 | 38.78 | 42.51 | 50.14 | 37.79 | 41.97 | 38.75
Table 3-71: Saving factor by heating/cooling type, Building type, and Zone
Building Type | Reference City | SFCooling | SFHeat Pump | SFElectric Fan | SFHeat ER
Data Center - No Economizer | Binghamton | 148 | 131 | 9 | 393
Data Center - With Economizer | Binghamton | 148 | 131 | 9 | 393
Education - College/University | Binghamton | 329 | 1251 | 83 | 3752
Education - Primary School | Binghamton | 318 | 645 | 43 | 1935
Education - Secondary School | Binghamton | 310 | 629 | 42 | 1888
Grocery | Binghamton | 341 | 178 | 12 | 535
Health - Hospital | Binghamton | 312 | 440 | 29 | 1319
Health - Other | Binghamton | 312 | 440 | 29 | 1319
Industrial Manufacturing - 1 Shift | Binghamton | 148 | 131 | 9 | 393
Industrial Manufacturing - 2 Shift | Binghamton | 148 | 131 | 9 | 393
Industrial Manufacturing - 3 Shift | Binghamton | 148 | 131 | 9 | 393
Institutional/Public Service | Binghamton | 653 | 1482 | 98 | 4446
Large Office | Binghamton | 257 | 208 | 14 | 624
Lodging - Large Hotel | Binghamton | 391 | 203 | 13 | 609
Lodging - Small Hotel | Binghamton | 391 | 203 | 13 | 609
Medium Office | Binghamton | 218 | 155 | 10 | 464
Multifamily Common Areas | Binghamton | 459 | 1742 | 115 | 5225
Restaurant - Full Service | Binghamton | 413 | 1056 | 70 | 3168
Restaurant - Quick Service | Binghamton | 413 | 1056 | 70 | 3168
Retail - Standalone | Binghamton | 364 | 363 | 24 | 1089
Retail - Strip mall | Binghamton | 255 | 241 | 16 | 724
Small Office | Binghamton | 273 | 231 | 20 | 692
Warehouse - Other | Binghamton | 148 | 131 | 9 | 393
Warehouse - Refrigerated | Binghamton | 148 | 131 | 9 | 393
Data Center - No Economizer | Scranton | 162 | 124 | 8 | 372
Data Center - With Economizer | Scranton | 162 | 124 | 8 | 372
Education - College/University | Scranton | 369 | 1105 | 73 | 3316
Education - Primary School | Scranton | 340 | 569 | 38 | 1708
Education - Secondary School | Scranton | 333 | 555 | 37 | 1666
Grocery | Scranton | 349 | 160 | 11 | 479
Health - Hospital | Scranton | 331 | 392 | 26 | 1177
Health - Other | Scranton | 331 | 392 | 26 | 1177
Industrial Manufacturing - 1 Shift | Scranton | 162 | 124 | 8 | 372
Industrial Manufacturing - 2 Shift | Scranton | 162 | 124 | 8 | 372
Industrial Manufacturing - 3 Shift | Scranton | 162 | 124 | 8 | 372
Institutional/Public Service | Scranton | 712 | 1323 | 88 | 3970
Large Office | Scranton | 263 | 183 | 12 | 550
Lodging - Large Hotel | Scranton | 400 | 180 | 12 | 541
Lodging - Small Hotel | Scranton | 400 | 180 | 12 | 541
Medium Office | Scranton | 222 | 137 | 9 | 410
Multifamily Common Areas | Scranton | 514 | 1569 | 104 | 4706
Restaurant - Full Service | Scranton | 457 | 945 | 63 | 2835
Restaurant - Quick Service | Scranton | 457 | 945 | 63 | 2835
Retail - Standalone | Scranton | 377 | 326 | 22 | 978
Retail - Strip mall | Scranton | 262 | 216 | 14 | 648
Small Office | Scranton | 280 | 203 | 13 | 610
Warehouse - Other | Scranton | 162 | 124 | 8 | 372
Warehouse - Refrigerated | Scranton | 162 | 124 | 8 | 372
Data Center - No Economizer | Allentown | 174 | 119 | 8 | 358
Data Center - With Economizer | Allentown | 174 | 119 | 8 | 358
Education - College/University | Allentown | 402 | 1002 | 66 | 3006
Education - Primary School | Allentown | 358 | 516 | 34 | 1548
Education - Secondary School | Allentown | 351 | 503 | 33 | 1508
Grocery | Allentown | 354 | 146 | 10 | 439
Health - Hospital | Allentown | 348 | 359 | 24 | 1076
Health - Other | Allentown | 348 | 359 | 24 | 1076
Industrial Manufacturing - 1 Shift | Allentown | 174 | 119 | 8 | 358
Industrial Manufacturing - 2 Shift | Allentown | 174 | 119 | 8 | 358
Industrial Manufacturing - 3 Shift | Allentown | 174 | 119 | 8 | 358
Institutional/Public Service | Allentown | 760 | 1210 | 80 | 3631
Large Office | Allentown | 268 | 166 | 11 | 498
Lodging - Large Hotel | Allentown | 406 | 165 | 11 | 494
Lodging - Small Hotel | Allentown | 406 | 165 | 11 | 494
Medium Office | Allentown | 226 | 124 | 8 | 371
Multifamily Common Areas | Allentown | 560 | 1446 | 96 | 4338
Restaurant - Full Service | Allentown | 494 | 866 | 57 | 2598
Restaurant - Quick Service | Allentown | 494 | 866 | 57 | 2598
Retail - Standalone | Allentown | 387 | 300 | 20 | 899
Retail - Strip mall | Allentown | 269 | 198 | 13 | 595
Small Office | Allentown | 285 | 184 | 12 | 552
Warehouse - Other | Allentown | 174 | 119 | 8 | 358
Warehouse - Refrigerated | Allentown | 174 | 119 | 8 | 358
Data Center - No Economizer | Philadelphia | 202 | 112 | 7 | 336
Data Center - With Economizer | Philadelphia | 202 | 112 | 7 | 336
Education - College/University | Philadelphia | 485 | 849 | 56 | 2548
Education - Primary School | Philadelphia | 404 | 437 | 29 | 1310
Education - Secondary School | Philadelphia | 395 | 425 | 28 | 1274
Grocery | Philadelphia | 369 | 126 | 8 | 379
Health - Hospital | Philadelphia | 388 | 309 | 20 | 926
Health - Other | Philadelphia | 388 | 309 | 20 | 926
Industrial Manufacturing - 1 Shift | Philadelphia | 202 | 112 | 7 | 336
Industrial Manufacturing - 2 Shift | Philadelphia | 202 | 112 | 7 | 336
Industrial Manufacturing - 3 Shift | Philadelphia | 202 | 112 | 7 | 336
Institutional/Public Service | Philadelphia | 880 | 1043 | 69 | 3131
Large Office | Philadelphia | 279 | 140 | 9 | 420
Lodging - Large Hotel | Philadelphia | 423 | 141 | 9 | 423
Lodging - Small Hotel | Philadelphia | 423 | 141 | 9 | 423
Medium Office | Philadelphia | 234 | 105 | 7 | 314
Multifamily Common Areas | Philadelphia | 672 | 1264 | 84 | 3793
Restaurant - Full Service | Philadelphia | 584 | 750 | 50 | 2249
Restaurant - Quick Service | Philadelphia | 584 | 750 | 50 | 2249
Retail - Standalone | Philadelphia | 413 | 260 | 17 | 782
Retail - Strip mall | Philadelphia | 285 | 172 | 11 | 515
Small Office | Philadelphia | 299 | 156 | 10 | 466
Warehouse - Other | Philadelphia | 202 | 112 | 7 | 336
Warehouse - Refrigerated | Philadelphia | 202 | 112 | 7 | 336
Data Center - No Economizer | Harrisburg | 197 | 123 | 8 | 370
Data Center - With Economizer | Harrisburg | 197 | 123 | 8 | 370
Education - College/University | Harrisburg | 472 | 1086 | 72 | 3256
Education - Primary School | Harrisburg | 397 | 559 | 37 | 1678
Education - Secondary School | Harrisburg | 388 | 545 | 36 | 1636
Grocery | Harrisburg | 367 | 157 | 10 | 471
Health - Hospital | Harrisburg | 382 | 386 | 26 | 1157
Health - Other | Harrisburg | 382 | 386 | 26 | 1157
Industrial Manufacturing - 1 Shift | Harrisburg | 197 | 123 | 8 | 370
Industrial Manufacturing - 2 Shift | Harrisburg | 197 | 123 | 8 | 370
Industrial Manufacturing - 3 Shift | Harrisburg | 197 | 123 | 8 | 370
Institutional/Public Service | Harrisburg | 862 | 1302 | 86 | 3905
Large Office | Harrisburg | 278 | 180 | 12 | 540
Lodging - Large Hotel | Harrisburg | 420 | 177 | 12 | 532
Lodging - Small Hotel | Harrisburg | 420 | 177 | 12 | 532
Medium Office | Harrisburg | 233 | 134 | 9 | 402
Multifamily Common Areas | Harrisburg | 655 | 1545 | 102 | 4636
Restaurant - Full Service | Harrisburg | 570 | 930 | 62 | 2789
Restaurant - Quick Service | Harrisburg | 570 | 930 | 62 | 2789
Retail - Standalone | Harrisburg | 409 | 321 | 21 | 963
Retail - Strip mall | Harrisburg | 282 | 213 | 14 | 638
Small Office | Harrisburg | 297 | 200 | 13 | 599
Warehouse - Other | Harrisburg | 197 | 123 | 8 | 370
Warehouse - Refrigerated | Harrisburg | 197 | 123 | 8 | 370
Data Center - No Economizer | Williamsport | 173 | 120 | 8 | 361
Data Center - With Economizer | Williamsport | 173 | 120 | 8 | 361
Education - College/University | Williamsport | 400 | 1023 | 68 | 3069
Education - Primary School | Williamsport | 357 | 527 | 35 | 1580
Education - Secondary School | Williamsport | 349 | 513 | 34 | 1540
Grocery | Williamsport | 354 | 149 | 10 | 447
Health - Hospital | Williamsport | 346 | 366 | 24 | 1096
Health - Other | Williamsport | 346 | 366 | 24 | 1096
Industrial Manufacturing - 1 Shift | Williamsport | 173 | 120 | 8 | 361
Industrial Manufacturing - 2 Shift | Williamsport | 173 | 120 | 8 | 361
Industrial Manufacturing - 3 Shift | Williamsport | 173 | 120 | 8 | 361
Institutional/Public Service | Williamsport | 756 | 1233 | 82 | 3700
Large Office | Williamsport | 267 | 170 | 11 | 508
Lodging - Large Hotel | Williamsport | 406 | 168 | 11 | 503
Lodging - Small Hotel | Williamsport | 406 | 168 | 11 | 503
Medium Office | Williamsport | 225 | 126 | 8 | 379
Multifamily Common Areas | Williamsport | 556 | 1471 | 97 | 4413
Restaurant - Full Service | Williamsport | 491 | 882 | 58 | 2647
Restaurant - Quick Service | Williamsport | 491 | 882 | 58 | 2647
Retail - Standalone | Williamsport | 387 | 305 | 20 | 915
Retail - Strip mall | Williamsport | 268 | 202 | 13 | 606
Small Office | Williamsport | 285 | 188 | 12 | 564
Warehouse - Other | Williamsport | 173 | 120 | 8 | 361
Warehouse - Refrigerated | Williamsport | 173 | 120 | 8 | 361
Data Center - No Economizer | Bradford | 135 | 141 | 9 | 424
Data Center - With Economizer | Bradford | 135 | 141 | 9 | 424
Education - College/University | Bradford | 288 | 1467 | 97 | 4401
Education - Primary School | Bradford | 295 | 757 | 50 | 2272
Education - Secondary School | Bradford | 289 | 740 | 49 | 2220
Grocery | Bradford | 334 | 207 | 14 | 620
Health - Hospital | Bradford | 292 | 510 | 34 | 1530
Health - Other | Bradford | 292 | 510 | 34 | 1530
Industrial Manufacturing - 1 Shift | Bradford | 135 | 141 | 9 | 424
Industrial Manufacturing - 2 Shift | Bradford | 135 | 141 | 9 | 424
Industrial Manufacturing - 3 Shift | Bradford | 135 | 141 | 9 | 424
Institutional/Public Service | Bradford | 594 | 1719 | 114 | 5156
Large Office | Bradford | 251 | 244 | 16 | 733
Lodging - Large Hotel | Bradford | 383 | 236 | 16 | 709
Lodging - Small Hotel | Bradford | 383 | 236 | 16 | 709
Medium Office | Bradford | 214 | 182 | 12 | 545
Multifamily Common Areas | Bradford | 404 | 1999 | 132 | 5997
Restaurant - Full Service | Bradford | 369 | 1221 | 81 | 3663
Restaurant - Quick Service | Bradford | 369 | 1221 | 81 | 3663
Retail - Standalone | Bradford | 352 | 419 | 28 | 1255
Retail - Strip mall | Bradford | 247 | 279 | 18 | 836
Small Office | Bradford | 266 | 271 | 18 | 815
Warehouse - Other | Bradford | 135 | 141 | 9 | 424
Warehouse - Refrigerated | Bradford | 135 | 141 | 9 | 424
Data Center - No Economizer | Pittsburgh | 170 | 122 | 8 | 365
Data Center - With Economizer | Pittsburgh | 170 | 122 | 8 | 365
Education - College/University | Pittsburgh | 393 | 1053 | 70 | 3158
Education - Primary School | Pittsburgh | 353 | 542 | 36 | 1627
Education - Secondary School | Pittsburgh | 345 | 529 | 35 | 1586
Grocery | Pittsburgh | 353 | 153 | 10 | 458
Health - Hospital | Pittsburgh | 343 | 375 | 25 | 1125
Health - Other | Pittsburgh | 343 | 375 | 25 | 1125
Industrial Manufacturing - 1 Shift | Pittsburgh | 170 | 122 | 8 | 365
Industrial Manufacturing - 2 Shift | Pittsburgh | 170 | 122 | 8 | 365
Industrial Manufacturing - 3 Shift | Pittsburgh | 170 | 122 | 8 | 365
Institutional/Public Service | Pittsburgh | 747 | 1266 | 84 | 3798
Large Office | Pittsburgh | 266 | 175 | 12 | 523
Lodging - Large Hotel | Pittsburgh | 404 | 172 | 11 | 517
Lodging - Small Hotel | Pittsburgh | 404 | 172 | 11 | 517
Medium Office | Pittsburgh | 225 | 130 | 9 | 390
Multifamily Common Areas | Pittsburgh | 547 | 1506 | 100 | 4519
Restaurant - Full Service | Pittsburgh | 483 | 905 | 60 | 2715
Restaurant - Quick Service | Pittsburgh | 483 | 905 | 60 | 2715
Retail - Standalone | Pittsburgh | 384 | 313 | 21 | 938
Retail - Strip mall | Pittsburgh | 267 | 207 | 14 | 621
Small Office | Pittsburgh | 284 | 194 | 13 | 581
Warehouse - Other | Pittsburgh | 170 | 122 | 8 | 365
Warehouse - Refrigerated | Pittsburgh | 170 | 122 | 8 | 365
Data Center - No Economizer | Erie | 160 | 126 | 8 | 379
Data Center - With Economizer | Erie | 160 | 126 | 8 | 379
Education - College/University | Erie | 363 | 1149 | 76 | 3447
Education - Primary School | Erie | 337 | 592 | 39 | 1777
Education - Secondary School | Erie | 329 | 578 | 38 | 1733
Grocery | Erie | 347 | 165 | 11 | 496
Health - Hospital | Erie | 329 | 406 | 27 | 1219
Health - Other | Erie | 329 | 406 | 27 | 1219
Industrial Manufacturing - 1 Shift | Erie | 160 | 126 | 8 | 379
Industrial Manufacturing - 2 Shift | Erie | 160 | 126 | 8 | 379
Industrial Manufacturing - 3 Shift | Erie | 160 | 126 | 8 | 379
Institutional/Public Service | Erie | 704 | 1371 | 91 | 4113
Large Office | Erie | 262 | 191 | 13 | 572
Lodging - Large Hotel | Erie | 398 | 187 | 12 | 562
Lodging - Small Hotel | Erie | 398 | 187 | 12 | 562
Medium Office | Erie | 222 | 142 | 9 | 426
Multifamily Common Areas | Erie | 506 | 1621 | 107 | 4862
Restaurant - Full Service | Erie | 451 | 978 | 65 | 2935
Restaurant - Quick Service | Erie | 451 | 978 | 65 | 2935
Retail - Standalone | Erie | 375 | 337 | 22 | 1011
Retail - Strip mall | Erie | 261 | 224 | 15 | 671
Small Office | Erie | 279 | 212 | 14 | 635
Warehouse - Other | Erie | 160 | 126 | 8 | 379
Warehouse - Refrigerated | Erie | 160 | 126 | 8 | 379
Table 3-73: Per-ton Savings by Measure, Building type, and Zone
Building Type | Reference City | Sub-Measure Type Code | Sub-Measure Type Description | Cooling Savings (kWh/ton) | Electric Heating Savings (kWh/ton) | Heating Fan Savings (kWh/ton)
|  |  |  | (NECES) | (NEHES) | (NHFES)
Data Center - No Economizer | Binghamton | DCV | Without Motor Drive Improvements | -4 | 305 | 20
Data Center - With Economizer | Binghamton | DCV | Without Motor Drive Improvements | -4 | 305 | 20
Education - College/University | Binghamton | DCV | Without Motor Drive Improvements | -34 | 898 | 59
Education - Primary School | Binghamton | DCV | Without Motor Drive Improvements | -34 | 898 | 59
Education - Secondary School | Binghamton | DCV | Without Motor Drive Improvements | -34 | 898 | 59
Grocery | Binghamton | DCV | Without Motor Drive Improvements | 4 | 901 | 60
Health - Hospital | Binghamton | DCV | Without Motor Drive Improvements | 1 | 114 | 8
Health - Other | Binghamton | DCV | Without Motor Drive Improvements | 1 | 114 | 8
Industrial Manufacturing - 1 Shift | Binghamton | DCV | Without Motor Drive Improvements | -13 | 59 | 4
Industrial Manufacturing - 2 Shift | Binghamton | DCV | Without Motor Drive Improvements | -13 | 59 | 4
Industrial Manufacturing - 3 Shift | Binghamton | DCV | Without Motor Drive Improvements | -13 | 59 | 4
Institutional/Public Service | Binghamton | DCV | Without Motor Drive Improvements | -1 | 105 | 7
Large Office | Binghamton | DCV | Without Motor Drive Improvements | 3 | 338 | 22
Lodging - Large Hotel | Binghamton | DCV | Without Motor Drive Improvements | 1 | 114 | 8
Lodging - Small Hotel | Binghamton | DCV | Without Motor Drive Improvements | 1 | 114 | 8
Medium Office | Binghamton | DCV | Without Motor Drive Improvements | 3 | 338 | 22
Multifamily Common Areas | Binghamton | DCV | Without Motor Drive Improvements | 16 | 875 | 58
Restaurant - Full Service | Binghamton | DCV | Without Motor Drive Improvements | 2 | 341 | 23
Restaurant - Quick Service | Binghamton | DCV | Without Motor Drive Improvements | 2 | 341 | 23
Retail - Standalone | Binghamton | DCV | Without Motor Drive Improvements | 9 | 301 | 20
Retail - Strip mall | Binghamton | DCV | Without Motor Drive Improvements | 8 | 281 | 19
Small Office | Binghamton | DCV | Without Motor Drive Improvements | 3 | 338 | 22
Warehouse - Other | Binghamton | DCV | Without Motor Drive Improvements | -4 | 305 | 20
Warehouse - Refrigerated | Binghamton | DCV | Without Motor Drive Improvements | -4 | 305 | 20
Data Center - No Economizer | Scranton | DCV | Without Motor Drive Improvements | -1 | 268 | 18
Data Center - With Economizer | Scranton | DCV | Without Motor Drive Improvements | -1 | 268 | 18
Education - College/University | Scranton | DCV | Without Motor Drive Improvements | 7 | 731 | 48
Education - Primary School | Scranton | DCV | Without Motor Drive Improvements | 7 | 731 | 48
Education - Secondary School | Scranton | DCV | Without Motor Drive Improvements | 7 | 731 | 48
Grocery | Scranton | DCV | Without Motor Drive Improvements | 23 | 776 | 51
Health - Hospital | Scranton | DCV | Without Motor Drive Improvements | 5 | 99 | 7
Health - Other | Scranton | DCV | Without Motor Drive Improvements | 5 | 99 | 7
Industrial Manufacturing - 1 Shift | Scranton | DCV | Without Motor Drive Improvements | -3 | 49 | 3
Industrial Manufacturing - 2 Shift | Scranton | DCV | Without Motor Drive Improvements | -3 | 49 | 3
Industrial Manufacturing - 3 Shift | Scranton | DCV | Without Motor Drive Improvements | -3 | 49 | 3
Institutional/Public Service | Scranton | DCV | Without Motor Drive Improvements | 3 | 93 | 6
Large Office | Scranton | DCV | Without Motor Drive Improvements | 10 | 281 | 19
Lodging - Large Hotel | Scranton | DCV | Without Motor Drive Improvements | 5 | 99 | 7
Lodging - Small Hotel | Scranton | DCV | Without Motor Drive Improvements | 5 | 99 | 7
Medium Office | Scranton | DCV | Without Motor Drive Improvements | 10 | 281 | 19
Multifamily Common Areas | Scranton | DCV | Without Motor Drive Improvements | 34 | 821 | 54
Restaurant - Full Service | Scranton | DCV | Without Motor Drive Improvements | 8 | 296 | 20
Restaurant - Quick Service | Scranton | DCV | Without Motor Drive Improvements | 8 | 296 | 20
Retail - Standalone | Scranton | DCV | Without Motor Drive Improvements | 21 | 263 | 17
Retail - Strip mall | Scranton | DCV | Without Motor Drive Improvements | 20 | 247 | 16
Small Office | Scranton | DCV | Without Motor Drive Improvements | 10 | 281 | 19
Warehouse - Other | Scranton | DCV | Without Motor Drive Improvements | -1 | 268 | 18
Warehouse - Refrigerated | Scranton | DCV | Without Motor Drive Improvements | -1 | 268 | 18
Data Center - No Economizer | Allentown | DCV | Without Motor Drive Improvements | 2 | 242 | 16
Data Center - With Economizer | Allentown | DCV | Without Motor Drive Improvements | 2 | 242 | 16
Education - College/University | Allentown | DCV | Without Motor Drive Improvements | 41 | 612 | 41
Education - Primary School | Allentown | DCV | Without Motor Drive Improvements | 41 | 612 | 41
Education - Secondary School | Allentown | DCV | Without Motor Drive Improvements | 41 | 612 | 41
Grocery | Allentown | DCV | Without Motor Drive Improvements | 38 | 688 | 46
Health - Hospital | Allentown | DCV | Without Motor Drive Improvements | 8 | 89 | 6
Health - Other | Allentown | DCV | Without Motor Drive Improvements | 8 | 89 | 6
Industrial Manufacturing - 1 Shift | Allentown | DCV | Without Motor Drive Improvements | 6 | 42 | 3
Industrial Manufacturing - 2 Shift | Allentown | DCV | Without Motor Drive Improvements | 6 | 42 | 3
Industrial Manufacturing - 3 Shift | Allentown | DCV | Without Motor Drive Improvements | 6 | 42 | 3
Institutional/Public Service | Allentown | DCV | Without Motor Drive Improvements | 6 | 84 | 6
Large Office | Allentown | DCV | Without Motor Drive Improvements | 15 | 241 | 16
Lodging - Large Hotel | Allentown | DCV | Without Motor Drive Improvements | 8 | 89 | 6
Lodging - Small Hotel | Allentown | DCV | Without Motor Drive Improvements | 8 | 89 | 6
Medium Office | Allentown | DCV | Without Motor Drive Improvements | 15 | 241 | 16
Multifamily Common Areas | Allentown | DCV | Without Motor Drive Improvements | 49 | 783 | 52
Restaurant - Full Service | Allentown | DCV | Without Motor Drive Improvements | 13 | 264 | 17
Restaurant - Quick Service | Allentown | DCV | Without Motor Drive Improvements | 13 | 264 | 17
Retail - Standalone | Allentown | DCV | Without Motor Drive Improvements | 32 | 236 | 16
Retail - Strip mall | Allentown | DCV | Without Motor Drive Improvements | 29 | 222 | 15
Small Office | Allentown | DCV | Without Motor Drive Improvements | 15 | 241 | 16
Warehouse - Other | Allentown | DCV | Without Motor Drive Improvements | 2 | 242 | 16
Warehouse - Refrigerated | Allentown | DCV | Without Motor Drive Improvements | 2 | 242 | 16
Data Center - No Economizer | Philadelphia | DCV | Without Motor Drive Improvements | 8 | 204 | 14
Data Center - With Economizer | Philadelphia | DCV | Without Motor Drive Improvements | 8 | 204 | 14
Education - College/University | Philadelphia | DCV | Without Motor Drive Improvements | 126 | 437 | 29
Education - Primary School | Philadelphia | DCV | Without Motor Drive Improvements | 126 | 437 | 29
Education - Secondary School | Philadelphia | DCV | Without Motor Drive Improvements | 126 | 437 | 29
Grocery | Philadelphia | DCV | Without Motor Drive Improvements | 76 | 556 | 37
Health - Hospital | Philadelphia | DCV | Without Motor Drive Improvements | 15 | 74 | 5
Health - Other | Philadelphia | DCV | Without Motor Drive Improvements | 15 | 74 | 5
Industrial Manufacturing - 1 Shift | Philadelphia | DCV | Without Motor Drive Improvements | 26 | 31 | 2
Industrial Manufacturing - 2 Shift | Philadelphia | DCV | Without Motor Drive Improvements | 26 | 31 | 2
Industrial Manufacturing - 3 Shift | Philadelphia | DCV | Without Motor Drive Improvements | 26 | 31 | 2
Institutional/Public Service | Philadelphia | DCV | Without Motor Drive Improvements | 13 | 71 | 5
Large Office | Philadelphia | DCV | Without Motor Drive Improvements | 27 | 181 | 12
Lodging - Large Hotel | Philadelphia | DCV | Without Motor Drive Improvements | 15 | 74 | 5
Lodging - Small Hotel | Philadelphia | DCV | Without Motor Drive Improvements | 15 | 74 | 5
Medium Office | Philadelphia | DCV | Without Motor Drive Improvements | 27 | 181 | 12
Multifamily Common Areas | Philadelphia | DCV | Without Motor Drive Improvements | 85 | 727 | 48
Restaurant - Full Service | Philadelphia | DCV | Without Motor Drive Improvements | 25 | 217 | 14
Restaurant - Quick Service | Philadelphia | DCV | Without Motor Drive Improvements | 25 | 217 | 14
Retail - Standalone | Philadelphia | DCV | Without Motor Drive Improvements | 57 | 196 | 13
Retail - Strip mall | Philadelphia | DCV | Without Motor Drive Improvements | 53 | 186 | 12
Small Office | Philadelphia | DCV | Without Motor Drive Improvements | 27 | 181 | 12
Warehouse - Other | Philadelphia | DCV | Without Motor Drive Improvements | 8 | 204 | 14
Warehouse - Refrigerated | Philadelphia | DCV | Without Motor Drive Improvements | 8 | 204 | 14
Data Center - No Economizer | Harrisburg | DCV | Without Motor Drive Improvements | 7 | 263 | 17
Data Center - With Economizer | Harrisburg | DCV | Without Motor Drive Improvements | 7 | 263 | 17
Education - College/University | Harrisburg | DCV | Without Motor Drive Improvements | 113 | 708 | 47
Education - Primary School | Harrisburg | DCV | Without Motor Drive Improvements | 113 | 708 | 47
Education - Secondary School | Harrisburg | DCV | Without Motor Drive Improvements | 113 | 708 | 47
Grocery | Harrisburg | DCV | Without Motor Drive Improvements | 70 | 759 | 50
Health - Hospital | Harrisburg | DCV | Without Motor Drive Improvements | 14 | 97 | 6
Health - Other | Harrisburg | DCV | Without Motor Drive Improvements | 14 | 97 | 6
Industrial Manufacturing - 1 Shift | Harrisburg | DCV | Without Motor Drive Improvements | 23 | 48 | 3
Industrial Manufacturing - 2 Shift | Harrisburg | DCV | Without Motor Drive Improvements | 23 | 48 | 3
Industrial Manufacturing - 3 Shift | Harrisburg | DCV | Without Motor Drive Improvements | 23 | 48 | 3
Institutional/Public Service | Harrisburg | DCV | Without Motor Drive Improvements | 12 | 91 | 6
Large Office | Harrisburg | DCV | Without Motor Drive Improvements | 25 | 273 | 18
Lodging - Large Hotel | Harrisburg | DCV | Without Motor Drive Improvements | 14 | 97 | 6
Lodging - Small Hotel | Harrisburg | DCV | Without Motor Drive Improvements | 14 | 97 | 6
Medium Office | Harrisburg | DCV | Without Motor Drive Improvements | 25 | 273 | 18
Multifamily Common Areas | Harrisburg | DCV | Without Motor Drive Improvements | 80 | 814 | 54
Restaurant - Full Service | Harrisburg | DCV | Without Motor Drive Improvements | 23 | 290 | 19
Restaurant - Quick Service | Harrisburg | DCV | Without Motor Drive Improvements | 23 | 290 | 19
Retail - Standalone | Harrisburg | DCV | Without Motor Drive Improvements | 53 | 258 | 17
Retail - Strip mall | Harrisburg | DCV | Without Motor Drive Improvements | 49 | 242 | 16
Small Office | Harrisburg | DCV | Without Motor Drive Improvements | 25 | 273 | 18
Warehouse - Other | Harrisburg | DCV | Without Motor Drive Improvements | 7 | 263 | 17
Warehouse - Refrigerated | Harrisburg | DCV | Without Motor Drive Improvements | 7 | 263 | 17
Data Center - No Economizer | Williamsport | DCV | Without Motor Drive Improvements | 2 | 248 | 16
Data Center - With Economizer | Williamsport | DCV | Without Motor Drive Improvements | 2 | 248 | 16
Education - College/University | Williamsport | DCV | Without Motor Drive Improvements | 38 | 636 | 42
Education - Primary School | Williamsport | DCV | Without Motor Drive Improvements | 38 | 636 | 42
Education - Secondary School | Williamsport | DCV | Without Motor Drive Improvements | 38 | 636 | 42
Grocery | Williamsport | DCV | Without Motor Drive Improvements | 37 | 706 | 47
Health - Hospital | Williamsport | DCV | Without Motor Drive Improvements | 7 | 91 | 6
Health - Other | Williamsport | DCV | Without Motor Drive Improvements | 7 | 91 | 6
Industrial Manufacturing - 1 Shift | Williamsport | DCV | Without Motor Drive Improvements | 5 | 43 | 3
Industrial Manufacturing - 2 Shift | Williamsport | DCV | Without Motor Drive Improvements | 5 | 43 | 3
Industrial Manufacturing - 3 Shift | Williamsport | DCV | Without Motor Drive Improvements | 5 | 43 | 3
Institutional/Public Service | Williamsport | DCV | Without Motor Drive Improvements | 5 | 86 | 6
Large Office | Williamsport | DCV | Without Motor Drive Improvements | 14 | 249 | 16
Lodging - Large Hotel | Williamsport | DCV | Without Motor Drive Improvements | 7 | 91 | 6
Lodging - Small Hotel | Williamsport | DCV | Without Motor Drive Improvements | 7 | 91 | 6
Medium Office | Williamsport | DCV | Without Motor Drive Improvements | 14 | 249 | 16
Multifamily Common Areas | Williamsport | DCV | Without Motor Drive Improvements | 47 | 791 | 52
Restaurant - Full Service | Williamsport | DCV | Without Motor Drive Improvements | 13 | 270 | 18
Restaurant - Quick Service | Williamsport | DCV | Without Motor Drive Improvements | 13 | 270 | 18
Retail - Standalone | Williamsport | DCV | Without Motor Drive Improvements | 31 | 242 | 16
Retail - Strip mall | Williamsport | DCV | Without Motor Drive Improvements | 29 | 227 | 15
Small Office | Williamsport | DCV | Without Motor Drive Improvements | 14 | 249 | 16
Warehouse - Other | Williamsport | DCV | Without Motor Drive Improvements | 2 | 248 | 16
Warehouse - Refrigerated | Williamsport | DCV | Without Motor Drive Improvements | 2 | 248 | 16
Data Center - No Economizer | Bradford | DCV | Without Motor Drive Improvements | -7 | 359 | 24
Data Center - With Economizer | Bradford | DCV | Without Motor Drive Improvements | -7 | 359 | 24
Education - College/University | Bradford | DCV | Without Motor Drive Improvements | -76 | 1147 | 76
Education - Primary School | Bradford | DCV | Without Motor Drive Improvements | -76 | 1147 | 76
Education - Secondary School | Bradford | DCV | Without Motor Drive Improvements | -76 | 1147 | 76
Grocery | Bradford | DCV | Without Motor Drive Improvements | -14 | 1087 | 72
Health - Hospital | Bradford | DCV | Without Motor Drive Improvements | -2 | 135 | 9
Health - Other | Bradford | DCV | Without Motor Drive Improvements | -2 | 135 | 9
Industrial Manufacturing - 1 Shift | Bradford | DCV | Without Motor Drive Improvements | -23 | 75 | 5
Industrial Manufacturing - 2 Shift | Bradford | DCV | Without Motor Drive Improvements | -23 | 75 | 5
Industrial Manufacturing - 3 Shift | Bradford | DCV | Without Motor Drive Improvements | -23 | 75 | 5
Institutional/Public Service | Bradford | DCV | Without Motor Drive Improvements | -5 | 124 | 8
Large Office | Bradford | DCV | Without Motor Drive Improvements | -3 | 423 | 28
Lodging - Large Hotel | Bradford | DCV | Without Motor Drive Improvements | -2 | 135 | 9
Lodging - Small Hotel | Bradford | DCV | Without Motor Drive Improvements | -2 | 135 | 9
Medium Office | Bradford | DCV | Without Motor Drive Improvements | -3 | 423 | 28
Multifamily Common Areas | Bradford | DCV | Without Motor Drive Improvements | -2 | 955 | 63
Restaurant - Full Service | Bradford | DCV | Without Motor Drive Improvements | -3 | 408 | 27
Restaurant - Quick Service | Bradford | DCV | Without Motor Drive Improvements | -3 | 408 | 27
Retail - Standalone | Bradford | DCV | Without Motor Drive Improvements | -4 | 358 | 24
Retail - Strip mall | Bradford | DCV | Without Motor Drive Improvements | -3 | 333 | 22
Small Office | Bradford | DCV | Without Motor Drive Improvements | -3 | 423 | 28
Warehouse - Other | Bradford | DCV | Without Motor Drive Improvements | -7 | 359 | 24
Warehouse - Refrigerated | Bradford | DCV | Without Motor Drive Improvements | -7 | 359 | 24
Data Center - No Economizer | Pittsburgh | DCV | Without Motor Drive Improvements | 1 | 255 | 17
Data Center - With Economizer | Pittsburgh | DCV | Without Motor Drive Improvements | 1 | 255 | 17
Education - College/University | Pittsburgh | DCV | Without Motor Drive Improvements | 32 | 671 | 44
Education - Primary School | Pittsburgh | DCV | Without Motor Drive Improvements | 32 | 671 | 44
Education - Secondary School | Pittsburgh | DCV | Without Motor Drive Improvements | 32 | 671 | 44
Grocery | Pittsburgh | DCV | Without Motor Drive Improvements | 34 | 731 | 48
Health - Hospital | Pittsburgh | DCV | Without Motor Drive Improvements | 7 | 94 | 6
Health - Other | Pittsburgh | DCV | Without Motor Drive Improvements | 7 | 94 | 6
Industrial Manufacturing - 1 Shift | Pittsburgh | DCV | Without Motor Drive Improvements | 3 | 45 | 3
Industrial Manufacturing - 2 Shift | Pittsburgh | DCV | Without Motor Drive Improvements | 3 | 45 | 3
Industrial Manufacturing - 3 Shift | Pittsburgh | DCV | Without Motor Drive Improvements | 3 | 45 | 3
Institutional/Public Service | Pittsburgh | DCV | Without Motor Drive Improvements | 5 | 89 | 6
Large Office | Pittsburgh | DCV | Without Motor Drive Improvements | 13 | 261 | 17
Lodging - Large Hotel | Pittsburgh | DCV | Without Motor Drive Improvements | 7 | 94 | 6
Lodging - Small Hotel | Pittsburgh | DCV | Without Motor Drive Improvements | 7 | 94 | 6
Medium Office | Pittsburgh | DCV | Without Motor Drive Improvements | 13 | 261 | 17
Multifamily Common Areas | Pittsburgh | DCV | Without Motor Drive Improvements | 44 | 802 | 53
Restaurant - Full Service | Pittsburgh | DCV | Without Motor Drive Improvements | 12 | 279 | 19
Restaurant - Quick Service | Pittsburgh | DCV | Without Motor Drive Improvements | 12 | 279 | 19
Retail - Standalone | Pittsburgh | DCV | Without Motor Drive Improvements | 29 | 249 | 17
Retail - Strip mall | Pittsburgh | DCV | Without Motor Drive Improvements | 27 | 234 | 16
Small Office | Pittsburgh | DCV | Without Motor Drive Improvements | 13 | 261 | 17
Warehouse - Other | Pittsburgh | DCV | Without Motor Drive Improvements | 1 | 255 | 17
Warehouse - Refrigerated | Pittsburgh | DCV | Without Motor Drive Improvements | 1 | 255 | 17
Data Center - No Economizer | Erie | DCV | Without Motor Drive Improvements | -1 | 279 | 18
Data Center - With Economizer | Erie | DCV | Without Motor Drive Improvements | -1 | 279 | 18
Education - College/University | Erie | DCV | Without Motor Drive Improvements | 1 | 781 | 52
Education - Primary School | Erie | DCV | Without Motor Drive Improvements | 1 | 781 | 52
Education - Secondary School | Erie | DCV | Without Motor Drive Improvements | 1 | 781 | 52
Grocery | Erie | DCV | Without Motor Drive Improvements | 20 | 814 | 54
Health - Hospital | Erie | DCV | Without Motor Drive Improvements | 4 | 103 | 7
Health - Other | Erie | DCV | Without Motor Drive Improvements | 4 | 103 | 7
Industrial Manufacturing - 1 Shift | Erie | DCV | Without Motor Drive Improvements | -4 | 52 | 3
Industrial Manufacturing - 2 Shift | Erie | DCV | Without Motor Drive Improvements | -4 | 52 | 3
Industrial Manufacturing - 3 Shift | Erie | DCV | Without Motor Drive Improvements | -4 | 52 | 3
Institutional/Public Service | Erie | DCV | Without Motor Drive Improvements | 2 | 97 | 6
Large Office | Erie | DCV | Without Motor Drive Improvements | 9 | 298 | 20
Lodging - Large Hotel | Erie | DCV | Without Motor Drive Improvements | 4 | 103 | 7
Lodging - Small Hotel | Erie | DCV | Without Motor Drive Improvements | 4 | 103 | 7
Medium Office | Erie | DCV | Without Motor Drive Improvements | 9 | 298 | 20
Multifamily Common Areas | Erie | DCV | Without Motor Drive Improvements | 31 | 838 | 55
Restaurant - Full Service | Erie | DCV | Without Motor Drive Improvements | 7 | 309 | 20
Restaurant - Quick Service | Erie | DCV | Without Motor Drive Improvements | 7 | 309 | 20
Retail - Standalone | Erie | DCV | Without Motor Drive Improvements | 20 | 275 | 18
Retail - Strip mall | Erie | DCV | Without Motor Drive Improvements | 18 | 257 | 17
Small Office | Erie | DCV | Without Motor Drive Improvements | 9 | 298 | 20
Warehouse - Other | Erie | DCV | Without Motor Drive Improvements | -1 | 279 | 18
Warehouse - Refrigerated | Erie | DCV | Without Motor Drive Improvements | -1 | 279 | 18
Data Center - No Economizer | Binghamton | DCV_VFD2 | Two-Speed Controls | 345 | 170 | 11
Data Center - With Economizer | Binghamton | DCV_VFD2 | Two-Speed Controls | 345 | 170 | 11
Education - College/University | Binghamton | DCV_VFD2 | Two-Speed Controls | 322 | 850 | 56
Education - Primary School | Binghamton | DCV_VFD2 | Two-Speed Controls | 322 | 850 | 56
Education - Secondary School | Binghamton | DCV_VFD2 | Two-Speed Controls | 322 | 850 | 56
Grocery | Binghamton | DCV_VFD2 | Two-Speed Controls | 436 | 840 | 56
Health - Hospital | Binghamton | DCV_VFD2 | Two-Speed Controls | 561 | 51 | 3
Health - Other | Binghamton | DCV_VFD2 | Two-Speed Controls | 561 | 51 | 3
Industrial Manufacturing - 1 Shift | Binghamton | DCV_VFD2 | Two-Speed Controls | 749 | 45 | 3
Industrial Manufacturing - 2 Shift | Binghamton | DCV_VFD2 | Two-Speed Controls | 749 | 45 | 3
Industrial Manufacturing - 3 Shift | Binghamton | DCV_VFD2 | Two-Speed Controls | 749 | 45 | 3
Institutional/Public Service | Binghamton | DCV_VFD2 | Two-Speed Controls | 752 | 128 | 8
Large Office | Binghamton | DCV_VFD2 | Two-Speed Controls | 1076 | 143 | 9
Lodging - Large Hotel | Binghamton | DCV_VFD2 | Two-Speed Controls | 561 | 51 | 3
Lodging - Small Hotel | Binghamton | DCV_VFD2 | Two-Speed Controls | 561 | 51 | 3
Medium Office | Binghamton | DCV_VFD2 | Two-Speed Controls | 1076 | 143 | 9
Multifamily Common Areas | Binghamton | DCV_VFD2 | Two-Speed Controls | 105 | 894 | 59
Restaurant - Full Service | Binghamton | DCV_VFD2 | Two-Speed Controls | 530 | 253 | 17
Restaurant - Quick Service | Binghamton | DCV_VFD2 | Two-Speed Controls | 530 | 253 | 17
Retail - Standalone | Binghamton | DCV_VFD2 | Two-Speed Controls | 669 | 176 | 12
Retail - Strip mall | Binghamton | DCV_VFD2 | Two-Speed Controls | 719 | 219 | 15
Small Office | Binghamton | DCV_VFD2 | Two-Speed Controls | 1076 | 143 | 9
Warehouse - Other | Binghamton | DCV_VFD2 | Two-Speed Controls | 345 | 170 | 11
Warehouse - Refrigerated | Binghamton | DCV_VFD2 | Two-Speed Controls | 345 | 170 | 11
Data Center - No Economizer | Scranton | DCV_VFD2 | Two-Speed Controls | 346 | 134 | 9
Data Center - With Economizer | Scranton | DCV_VFD2 | Two-Speed Controls | 346 | 134 | 9
Education - College/University | Scranton | DCV_VFD2 | Two-Speed Controls | 365 | 695 | 46
Education - Primary School | Scranton | DCV_VFD2 | Two-Speed Controls | 365 | 695 | 46
Education - Secondary School | Scranton | DCV_VFD2 | Two-Speed Controls | 365 | 695 | 46
Grocery | Scranton | DCV_VFD2 | Two-Speed Controls | 459 | 723 | 48
Health - Hospital | Scranton | DCV_VFD2 | Two-Speed Controls | 569 | 51 | 3
Health - Other | Scranton | DCV_VFD2 | Two-Speed Controls | 569 | 51 | 3
Industrial Manufacturing - 1 Shift | Scranton | DCV_VFD2 | Two-Speed Controls | 758 | 38 | 3
Industrial Manufacturing - 2 Shift | Scranton | DCV_VFD2 | Two-Speed Controls | 758 | 38 | 3
Industrial Manufacturing - 3 Shift | Scranton | DCV_VFD2 | Two-Speed Controls | 758 | 38 | 3
Institutional/Public Service | Scranton | DCV_VFD2 | Two-Speed Controls | 813 | 110 | 7
Large Office | Scranton | DCV_VFD2 | Two-Speed Controls | 1073 | 108 | 7
Lodging - Large Hotel | Scranton | DCV_VFD2 | Two-Speed Controls | 569 | 51 | 3
Lodging - Small Hotel | Scranton | DCV_VFD2 | Two-Speed Controls | 569 | 51 | 3
Medium Office | Scranton | DCV_VFD2 | Two-Speed Controls | 1073 | 108 | 7
Multifamily Common Areas | Scranton | DCV_VFD2 | Two-Speed Controls | 127 | 856 | 57
Restaurant - Full Service | Scranton | DCV_VFD2 | Two-Speed Controls | 545 | 221 | 15
Restaurant - Quick Service | Scranton | DCV_VFD2 | Two-Speed Controls | 545 | 221 | 15
Retail - Standalone | Scranton | DCV_VFD2 | Two-Speed Controls | 682 | 154 | 10
Retail - Strip mall | Scranton | DCV_VFD2 | Two-Speed Controls | 728 | 194 | 13
Small Office | Scranton | DCV_VFD2 | Two-Speed Controls | 1073 | 108 | 7
Warehouse - Other | Scranton | DCV_VFD2 | Two-Speed Controls | 346 | 134 | 9
Warehouse - Refrigerated | Scranton | DCV_VFD2 | Two-Speed Controls | 346 | 134 | 9
Data Center - No Economizer | Allentown | DCV_VFD2 | Two-Speed Controls | 347 | 108 | 7
Data Center - With Economizer | Allentown | DCV_VFD2 | Two-Speed Controls | 347 | 108 | 7
Education - College/University | Allentown | DCV_VFD2 | Two-Speed Controls | 400 | 584 | 39
Education - Primary School | Allentown | DCV_VFD2 | Two-Speed Controls | 400 | 584 | 39
Education - Secondary School | Allentown | DCV_VFD2 | Two-Speed Controls | 400 | 584 | 39
Grocery | Allentown | DCV_VFD2 | Two-Speed Controls | 477 | 641 | 42
Health - Hospital | Allentown | DCV_VFD2 | Two-Speed Controls | 574 | 52 | 3
Health - Other | Allentown | DCV_VFD2 | Two-Speed Controls | 574 | 52 | 3
Industrial Manufacturing - 1 Shift | Allentown | DCV_VFD2 | Two-Speed Controls | 765 | 32 | 2
Industrial Manufacturing - 2 Shift | Allentown | DCV_VFD2 | Two-Speed Controls | 765 | 32 | 2
Industrial Manufacturing - 3 Shift | Allentown | DCV_VFD2 | Two-Speed Controls | 765 | 32 | 2
Institutional/Public Service | Allentown | DCV_VFD2 | Two-Speed Controls | 862 | 98 | 6
Large Office | Allentown | DCV_VFD2 | Two-Speed Controls | 1071 | 84 | 6
Lodging - Large Hotel | Allentown | DCV_VFD2 | Two-Speed Controls | 574 | 52 | 3
Lodging - Small Hotel | Allentown | DCV_VFD2 | Two-Speed Controls | 574 | 52 | 3
Medium Office | Allentown | DCV_VFD2 | Two-Speed Controls | 1071 | 84 | 6
Multifamily Common Areas | Allentown | DCV_VFD2 | Two-Speed Controls | 146 | 829 | 55
Restaurant - Full Service | Allentown | DCV_VFD2 | Two-Speed Controls | 558 | 199 | 13
Restaurant - Quick Service | Allentown | DCV_VFD2 | Two-Speed Controls | 558 | 199 | 13
Retail - Standalone | Allentown | DCV_VFD2 | Two-Speed Controls | 692 | 138 | 9
Retail - Strip mall | Allentown | DCV_VFD2 | Two-Speed Controls | 735 | 176 | 12
Small Office | Allentown | DCV_VFD2 | Two-Speed Controls | 1071 | 84 | 6
Warehouse - Other | Allentown | DCV_VFD2 | Two-Speed Controls | 347 | 108 | 7
Warehouse - Refrigerated | Allentown | DCV_VFD2 | Two-Speed Controls | 347 | 108 | 7
Data Center - No Economizer | Philadelphia | DCV_VFD2 | Two-Speed Controls | 349 | 70 | 5
Data Center - With Economizer | Philadelphia | DCV_VFD2 | Two-Speed Controls | 349 | 70 | 5
Education - College/University | Philadelphia | DCV_VFD2 | Two-Speed Controls | 487 | 421 | 28
Education - Primary School | Philadelphia | DCV_VFD2 | Two-Speed Controls | 487 | 421 | 28
Education - Secondary School | Philadelphia | DCV_VFD2 | Two-Speed Controls | 487 | 421 | 28
Grocery | Philadelphia | DCV_VFD2 | Two-Speed Controls | 522 | 519 | 34
Health - Hospital | Philadelphia | DCV_VFD2 | Two-Speed Controls | 589 | 53 | 3
Health - Other | Philadelphia | DCV_VFD2 | Two-Speed Controls | 589 | 53 | 3
Industrial Manufacturing - 1 Shift | Philadelphia | DCV_VFD2 | Two-Speed Controls | 784 | 25 | 2
Industrial Manufacturing - 2 Shift | Philadelphia | DCV_VFD2 | Two-Speed Controls | 784 | 25 | 2
Industrial Manufacturing - 3 Shift | Philadelphia | DCV_VFD2 | Two-Speed Controls | 784 | 25 | 2
Institutional/Public Service | Philadelphia | DCV_VFD2 | Two-Speed Controls | 986 | 80 | 5
Large Office | Philadelphia | DCV_VFD2 | Two-Speed Controls | 1065 | 47 | 3
Lodging - Large Hotel | Philadelphia | DCV_VFD2 | Two-Speed Controls | 589 | 53 | 3
Lodging - Small Hotel | Philadelphia | DCV_VFD2 | Two-Speed Controls | 589 | 53 | 3
Medium Office | Philadelphia | DCV_VFD2 | Two-Speed Controls | 1065 | 47 | 3
Multifamily Common Areas | Philadelphia | DCV_VFD2 | Two-Speed Controls | 191 | 790 | 52
Restaurant - Full Service | Philadelphia | DCV_VFD2 | Two-Speed Controls | 590 | 165 | 11
Restaurant - Quick Service | Philadelphia | DCV_VFD2 | Two-Speed Controls | 590 | 165 | 11
Retail - Standalone | Philadelphia | DCV_VFD2 | Two-Speed Controls | 718 | 115 | 8
Retail - Strip mall | Philadelphia | DCV_VFD2 | Two-Speed Controls | 753 | 149 | 10
Small Office | Philadelphia | DCV_VFD2 | Two-Speed Controls | 1065 | 47 | 3
Warehouse - Other | Philadelphia | DCV_VFD2 | Two-Speed Controls | 349 | 70 | 5
Warehouse - Refrigerated | Philadelphia | DCV_VFD2 | Two-Speed Controls | 349 | 70 | 5
Data Center - No Economizer | Harrisburg | DCV_VFD2 | Two-Speed Controls | 348 | 129 | 9
Data Center - With Economizer | Harrisburg | DCV_VFD2 | Two-Speed Controls | 348 | 129 | 9
Education - College/University | Harrisburg | DCV_VFD2 | Two-Speed Controls | 474 | 673 | 45
Education - Primary School | Harrisburg | DCV_VFD2 | Two-Speed Controls | 474 | 673 | 45
Education - Secondary School | Harrisburg | DCV_VFD2 | Two-Speed Controls | 474 | 673 | 45
Grocery | Harrisburg | DCV_VFD2 | Two-Speed Controls | 515 | 708 | 47
Health - Hospital | Harrisburg | DCV_VFD2 | Two-Speed Controls | 587 | 52 | 3
Health - Other | Harrisburg | DCV_VFD2 | Two-Speed Controls | 587 | 52 | 3
Industrial Manufacturing - 1 Shift | Harrisburg | DCV_VFD2 | Two-Speed Controls | 781 | 37 | 2
Industrial Manufacturing - 2 Shift | Harrisburg | DCV_VFD2 | Two-Speed Controls | 781 | 37 | 2
Industrial Manufacturing - 3 Shift | Harrisburg | DCV_VFD2 | Two-Speed Controls | 781 | 37 | 2
Institutional/Public Service | Harrisburg | DCV_VFD2 | Two-Speed Controls | 967 | 108 | 7
Large Office | Harrisburg | DCV_VFD2 | Two-Speed Controls | 1066 | 104 | 7
Lodging - Large Hotel | Harrisburg | DCV_VFD2 | Two-Speed Controls | 587 | 52 | 3
Lodging - Small Hotel | Harrisburg | DCV_VFD2 | Two-Speed Controls | 587 | 52 | 3
Medium Office | Harrisburg | DCV_VFD2 | Two-Speed Controls | 1066 | 104 | 7
Multifamily Common Areas | Harrisburg | DCV_VFD2 | Two-Speed Controls | 184 | 851 | 56
Restaurant - Full Service | Harrisburg | DCV_VFD2 | Two-Speed Controls | 585 | 217 | 14
Restaurant - Quick Service | Harrisburg | DCV_VFD2 | Two-Speed Controls | 585 | 217 | 14
Retail - Standalone | Harrisburg | DCV_VFD2 | Two-Speed Controls | 714 | 151 | 10
Retail - Strip mall | Harrisburg | DCV_VFD2 | Two-Speed Controls | 750 | 190 | 13
Small Office | Harrisburg | DCV_VFD2 | Two-Speed Controls | 1066 | 104 | 7
Warehouse - Other | Harrisburg | DCV_VFD2 | Two-Speed Controls | 348 | 129 | 9
Warehouse - Refrigerated | Harrisburg | DCV_VFD2 | Two-Speed Controls | 348 | 129 | 9
Data Center - No Economizer | Williamsport | DCV_VFD2 | Two-Speed Controls | 346 | 113 | 7
Data Center - With Economizer | Williamsport | DCV_VFD2 | Two-Speed Controls | 346 | 113 | 7
Education - College/University | Williamsport | DCV_VFD2 | Two-Speed Controls | 397 | 607 | 40
Education - Primary School | Williamsport | DCV_VFD2 | Two-Speed Controls | 397 | 607 | 40
Education - Secondary School | Williamsport | DCV_VFD2 | Two-Speed Controls | 397 | 607 | 40
Grocery | Williamsport | DCV_VFD2 | Two-Speed Controls | 475 | 658 | 44
Health - Hospital | Williamsport | DCV_VFD2 | Two-Speed Controls | 574 | 52 | 3
Health - Other | Williamsport | DCV_VFD2 | Two-Speed Controls | 574 | 52 | 3
Industrial Manufacturing - 1 Shift | Williamsport | DCV_VFD2 | Two-Speed Controls | 765 | 34 | 2
Industrial Manufacturing - 2 Shift | Williamsport | DCV_VFD2 | Two-Speed Controls | 765 | 34 | 2
Industrial Manufacturing - 3 Shift | Williamsport | DCV_VFD2 | Two-Speed Controls | 765 | 34 | 2
Institutional/Public Service | Williamsport | DCV_VFD2 | Two-Speed Controls | 858 | 100 | 7
Large Office | Williamsport | DCV_VFD2 | Two-Speed Controls | 1071 | 89 | 6
Lodging - Large Hotel | Williamsport | DCV_VFD2 | Two-Speed Controls | 574 | 52 | 3
Lodging - Small Hotel | Williamsport | DCV_VFD2 | Two-Speed Controls | 574 | 52 | 3
Medium Office | Williamsport | DCV_VFD2 | Two-Speed Controls | 1071 | 89 | 6
Multifamily Common Areas | Williamsport | DCV_VFD2 | Two-Speed Controls | 144 | 835 | 55
Restaurant - Full Service | Williamsport | DCV_VFD2 | Two-Speed Controls | 557 | 203 | 13
Restaurant - Quick Service | Williamsport | DCV_VFD2 | Two-Speed Controls | 557 | 203 | 13
Retail - Standalone | Williamsport | DCV_VFD2 | Two-Speed Controls | 692 | 141 | 9
Retail - Strip mall | Williamsport | DCV_VFD2 | Two-Speed Controls | 735 | 179 | 12
Small Office | Williamsport | DCV_VFD2 | Two-Speed Controls | 1071 | 89 | 6
Warehouse - Other | Williamsport | DCV_VFD2 | Two-Speed Controls | 346 | 113 | 7
Warehouse - Refrigerated | Williamsport | DCV_VFD2 | Two-Speed Controls | 346 | 113 | 7
Data Center - No Economizer | Bradford | DCV_VFD2 | Two-Speed Controls | 344 | 224 | 15
Data Center - With Economizer | Bradford | DCV_VFD2 | Two-Speed Controls | 344 | 224 | 15
Education - College/University | Bradford | DCV_VFD2 | Two-Speed Controls | 280 | 1081 | 72
Education - Primary School | Bradford | DCV_VFD2 | Two-Speed Controls | 280 | 1081 | 72
Education - Secondary School | Bradford | DCV_VFD2 | Two-Speed Controls | 280 | 1081 | 72
Grocery | Bradford | DCV_VFD2 | Two-Speed Controls | 414 | 1012 | 67
Health - Hospital | Bradford | DCV_VFD2 | Two-Speed Controls | 554 | 50 | 3
Health - Other | Bradford | DCV_VFD2 | Two-Speed Controls | 554 | 50 | 3
Industrial Manufacturing - 1 Shift | Bradford | DCV_VFD2 | Two-Speed Controls | 740 | 56 | 4
Industrial Manufacturing - 2 Shift | Bradford | DCV_VFD2 | Two-Speed Controls | 740 | 56 | 4
Industrial Manufacturing - 3 Shift | Bradford | DCV_VFD2 | Two-Speed Controls | 740 | 56 | 4
Institutional/Public Service | Bradford | DCV_VFD2 | Two-Speed Controls | 692 | 154 | 10
Large Office | Bradford | DCV_VFD2 | Two-Speed Controls | 1079 | 195 | 13
Lodging - Large Hotel | Bradford | DCV_VFD2 | Two-Speed Controls | 554 | 50 | 3
Lodging - Small Hotel | Bradford | DCV_VFD2 | Two-Speed Controls | 554 | 50 | 3
Medium Office | Bradford | DCV_VFD2 | Two-Speed Controls | 1079 | 195 | 13
Multifamily Common Areas | Bradford | DCV_VFD2 | Two-Speed Controls | 83 | 950 | 63
Restaurant - Full Service | Bradford | DCV_VFD2 | Two-Speed Controls | 514 | 301 | 20
Restaurant - Quick Service | Bradford | DCV_VFD2 | Two-Speed Controls | 514 | 301 | 20
Retail - Standalone | Bradford | DCV_VFD2 | Two-Speed Controls | 657 | 209 | 14
Retail - Strip mall | Bradford | DCV_VFD2 | Two-Speed Controls | 711 | 258 | 17
Small Office | Bradford | DCV_VFD2 | Two-Speed Controls | 1079 | 195 | 13
Warehouse - Other | Bradford | DCV_VFD2 | Two-Speed Controls | 344 | 224 | 15
Warehouse - Refrigerated | Bradford | DCV_VFD2 | Two-Speed Controls | 344 | 224 | 15
Data Center - No Economizer | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 346 | 121 | 8
Data Center - With Economizer | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 346 | 121 | 8
Education - College/University | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 390 | 639 | 42
Education - Primary School | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 390 | 639 | 42
Education - Secondary School | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 390 | 639 | 42
Grocery | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 472 | 682 | 45
Health - Hospital | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 573 | 52 | 3
Health - Other | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 573 | 52 | 3
Industrial Manufacturing - 1 Shift | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 763 | 35 | 2
Industrial Manufacturing - 2 Shift | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 763 | 35 | 2
Industrial Manufacturing - 3 Shift | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 763 | 35 | 2
Institutional/Public Service | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 848 | 104 | 7
Large Office | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 1071 | 96 | 6
Lodging - Large Hotel | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 573 | 52 | 3
Lodging - Small Hotel | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 573 | 52 | 3
Medium Office | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 1071 | 96 | 6
Multifamily Common Areas | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 140 | 843 | 56
Restaurant - Full Service | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 554 | 210 | 14
Restaurant - Quick Service | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 554 | 210 | 14
Retail - Standalone | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 689 | 146 | 10
Retail - Strip mall | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 733 | 185 | 12
Small Office | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 1071 | 96 | 6
Warehouse - Other | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 346 | 121 | 8
Warehouse - Refrigerated | Pittsburgh | DCV_VFD2 | Two-Speed Controls | 346 | 121 | 8
Data Center - No Economizer | Erie | DCV_VFD2 | Two-Speed Controls | 346 | 145 | 10
Data Center - With Economizer | Erie | DCV_VFD2 | Two-Speed Controls | 346 | 145 | 10
Education - College/University | Erie | DCV_VFD2 | Two-Speed Controls | 359 | 741 | 49
Education - Primary School | Erie | DCV_VFD2 | Two-Speed Controls | 359 | 741 | 49
Education - Secondary School | Erie | DCV_VFD2 | Two-Speed Controls | 359 | 741 | 49
Grocery | Erie | DCV_VFD2 | Two-Speed Controls | 455 | 758 | 50
Health - Hospital | Erie | DCV_VFD2 | Two-Speed Controls | 568 | 51 | 3
Health - Other | Erie | DCV_VFD2 | Two-Speed Controls | 568 | 51 | 3
Industrial Manufacturing - 1 Shift | Erie | DCV_VFD2 | Two-Speed Controls | 757 | 40 | 3
Industrial Manufacturing - 2 Shift | Erie | DCV_VFD2 | Two-Speed Controls | 757 | 40 | 3
Industrial Manufacturing - 3 Shift | Erie | DCV_VFD2 | Two-Speed Controls | 757 | 40 | 3
Institutional/Public Service | Erie | DCV_VFD2 | Two-Speed Controls | 804 | 116 | 8
Large Office | Erie | DCV_VFD2 | Two-Speed Controls | 1073 | 119 | 8
Lodging - Large Hotel | Erie | DCV_VFD2 | Two-Speed Controls | 568 | 51 | 3
Lodging - Small Hotel | Erie | DCV_VFD2 | Two-Speed Controls | 568 | 51 | 3
Medium Office | Erie | DCV_VFD2 | Two-Speed Controls | 1073 | 119 | 8
Multifamily Common Areas | Erie | DCV_VFD2 | Two-Speed Controls | 124 | 868 | 57
Restaurant - Full Service | Erie | DCV_VFD2 | Two-Speed Controls | 543 | 231 | 15
Restaurant - Quick Service | Erie | DCV_VFD2 | Two-Speed Controls | 543 | 231 | 15
Retail - Standalone | Erie | DCV_VFD2 | Two-Speed Controls | 680 | 160 | 11
Retail - Strip mall | Erie | DCV_VFD2 | Two-Speed Controls | 727 | 202 | 13
Small Office | Erie | DCV_VFD2 | Two-Speed Controls | 1073 | 119 | 8
Warehouse - Other | Erie | DCV_VFD2 | Two-Speed Controls | 346 | 145 | 10
Warehouse - Refrigerated | Erie | DCV_VFD2 | Two-Speed Controls | 346 | 145 | 10
Data Center - No Economizer | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 417 | 143 | 9
Data Center - With Economizer | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 417 | 143 | 9
Education - College/University | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 372 | 825 | 55
Education - Primary School | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 372 | 825 | 55
Education - Secondary School | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 372 | 825 | 55
Grocery | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 470 | 819 | 54
Health - Hospital | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 599 | 18 | 1
Health - Other | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 599 | 18 | 1
Industrial Manufacturing - 1 Shift | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 820 | 36 | 2
Industrial Manufacturing - 2 Shift | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 820 | 36 | 2
Industrial Manufacturing - 3 Shift | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 820 | 36 | 2
Institutional/Public Service | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 938 | 152 | 10
Large Office | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 1178 | 116 | 8
Lodging - Large Hotel | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 599 | 18 | 1
Lodging - Small Hotel | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 599 | 18 | 1
Medium Office | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 1178 | 116 | 8
Multifamily Common Areas | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 136 | 895 | 59
Restaurant - Full Service | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 582 | 221 | 15
Restaurant - Quick Service | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 582 | 221 | 15
Retail - Standalone | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 749 | 159 | 11
Retail - Strip mall | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 749 | 200 | 13
Small Office | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 1178 | 116 | 8
Warehouse - Other | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 417 | 143 | 9
Warehouse - Refrigerated | Binghamton | DCV_VFD3 | Three-Speed Controls or VFD | 417 | 143 | 9
Data Center - No Economizer | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 409 | 409 | 409
Data Center - With Economizer | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 409 | 409 | 409
Education - College/University | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 408 | 408 | 408
Education - Primary School | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 408 | 408 | 408
Education - Secondary School | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 408 | 408 | 408
Grocery | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 487 | 487 | 487
Health - Hospital | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 601 | 601 | 601
Health - Other | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 601 | 601 | 601
Industrial Manufacturing - 1 Shift | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 818 | 818 | 818
Industrial Manufacturing - 2 Shift | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 818 | 818 | 818
Industrial Manufacturing - 3 Shift | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 818 | 818 | 818
Institutional/Public Service | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 978 | 978 | 978
Large Office | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 1160 | 1160 | 1160
Lodging - Large Hotel | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 601 | 601 | 601
Lodging - Small Hotel | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 601 | 601 | 601
Medium Office | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 1160 | 1160 | 1160
Multifamily Common Areas | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 154 | 154 | 154
Restaurant - Full Service | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 592 | 592 | 592
Restaurant - Quick Service | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 592 | 592 | 592
Retail - Standalone | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 750 | 750 | 750
Retail - Strip mall | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 778 | 778 | 778
Small Office | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 1160 | 1160 | 1160
Warehouse - Other | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 409 | 409 | 409
Warehouse - Refrigerated | Scranton | DCV_VFD3 | Three-Speed Controls or VFD | 409 | 409 | 409
Data Center - No Economizer | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 401 | 86 | 6
Data Center - With Economizer | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 401 | 86 | 6
Education - College/University | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 437 | 565 | 37
Education - Primary School | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 437 | 565 | 37
Education - Secondary School | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 437 | 565 | 37
Grocery | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 501 | 625 | 41
Health - Hospital | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Health - Other | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Industrial Manufacturing - 1 Shift | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 817 | 28 | 2
Industrial Manufacturing - 2 Shift | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 817 | 28 | 2
Industrial Manufacturing - 3 Shift | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 817 | 28 | 2
Institutional/Public Service | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 1010 | 114 | 8
Large Office | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 1146 | 68 | 5
Lodging - Large Hotel | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Lodging - Small Hotel | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Medium Office | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 1146 | 68 | 5
Multifamily Common Areas | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 169 | 822 | 54
Restaurant - Full Service | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 600 | 170 | 11
Restaurant - Quick Service | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 600 | 170 | 11
Retail - Standalone | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 751 | 121 | 8
Retail - Strip mall | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 778 | 162 | 11
Small Office | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 1146 | 68 | 5
Warehouse - Other | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 401 | 86 | 6
Warehouse - Refrigerated | Allentown | DCV_VFD3 | Three-Speed Controls or VFD | 401 | 86 | 6
Data Center - No Economizer | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 383 | 51 | 3
Data Center - With Economizer | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 383 | 51 | 3
Education - College/University | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 510 | 406 | 27
Education - Primary School | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 510 | 406 | 27
Education - Secondary School | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 510 | 406 | 27
Grocery | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 536 | 506 | 33
Health - Hospital | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 608 | 20 | 1
Health - Other | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 608 | 20 | 1
Industrial Manufacturing - 1 Shift | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 815 | 23 | 2
Industrial Manufacturing - 2 Shift | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 815 | 23 | 2
Industrial Manufacturing - 3 Shift | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 815 | 23 | 2
Institutional/Public Service | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 1090 | 91 | 6
Large Office | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 1111 | 39 | 3
Lodging - Large Hotel | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 608 | 20 | 1
Lodging - Small Hotel | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 608 | 20 | 1
Medium Office | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 1111 | 39 | 3
Multifamily Common Areas | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 205 | 777 | 51
Restaurant - Full Service | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 620 | 139 | 9
Restaurant - Quick Service | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 620 | 139 | 9
Retail - Standalone | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 753 | 98 | 6
Retail - Strip mall | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 776 | 138 | 9
Small Office | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 1111 | 39 | 3
Warehouse - Other | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 383 | 51 | 3
Warehouse - Refrigerated | Philadelphia | DCV_VFD3 | Three-Speed Controls or VFD | 383 | 51 | 3
Data Center - No Economizer | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 386 | 105 | 7
Data Center - With Economizer | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 386 | 105 | 7
Education - College/University | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 499 | 652 | 43
Education - Primary School | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 499 | 652 | 43
Education - Secondary School | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 499 | 652 | 43
Grocery | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 531 | 690 | 46
Health - Hospital | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 607 | 19 | 1
Health - Other | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 607 | 19 | 1
Industrial Manufacturing - 1 Shift | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 815 | 31 | 2
Industrial Manufacturing - 2 Shift | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 815 | 31 | 2
Industrial Manufacturing - 3 Shift | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 815 | 31 | 2
Institutional/Public Service | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 1078 | 127 | 8
Large Office | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 1116 | 84 | 6
Lodging - Large Hotel | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 607 | 19 | 1
Lodging - Small Hotel | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 607 | 19 | 1
Medium Office | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 1116 | 84 | 6
Multifamily Common Areas | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 200 | 846 | 56
Restaurant - Full Service | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 617 | 187 | 12
Restaurant - Quick Service | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 617 | 187 | 12
Retail - Standalone | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 753 | 134 | 9
Retail - Strip mall | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 776 | 175 | 12
Small Office | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 1116 | 84 | 6
Warehouse - Other | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 386 | 105 | 7
Warehouse - Refrigerated | Harrisburg | DCV_VFD3 | Three-Speed Controls or VFD | 386 | 105 | 7
Data Center - No Economizer | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 402 | 91 | 6
Data Center - With Economizer | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 402 | 91 | 6
Education - College/University | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 435 | 587 | 39
Education - Primary School | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 435 | 587 | 39
Education - Secondary School | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 435 | 587 | 39
Grocery | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 500 | 641 | 42
Health - Hospital | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Health - Other | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Industrial Manufacturing - 1 Shift | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 817 | 29 | 2
Industrial Manufacturing - 2 Shift | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 817 | 29 | 2
Industrial Manufacturing - 3 Shift | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 817 | 29 | 2
Institutional/Public Service | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 1007 | 117 | 8
Large Office | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 1147 | 72 | 5
Lodging - Large Hotel | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Lodging - Small Hotel | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Medium Office | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 1147 | 72 | 5
Multifamily Common Areas | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 168 | 828 | 55
Restaurant - Full Service | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 599 | 175 | 12
Restaurant - Quick Service | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 599 | 175 | 12
Retail - Standalone | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 751 | 124 | 8
Retail - Strip mall | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 778 | 165 | 11
Small Office | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 1147 | 72 | 5
Warehouse - Other | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 402 | 91 | 6
Warehouse - Refrigerated | Williamsport | DCV_VFD3 | Three-Speed Controls or VFD | 402 | 91 | 6
Data Center - No Economizer | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 426 | 193 | 13
Data Center - With Economizer | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 426 | 193 | 13
Education - College/University | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 337 | 1050 | 70
Education - Primary School | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 337 | 1050 | 70
Education - Secondary School | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 337 | 1050 | 70
Grocery | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 453 | 987 | 65
Health - Hospital | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 597 | 17 | 1
Health - Other | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 597 | 17 | 1
Industrial Manufacturing - 1 Shift | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 821 | 43 | 3
Industrial Manufacturing - 2 Shift | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 821 | 43 | 3
Industrial Manufacturing - 3 Shift | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 821 | 43 | 3
Institutional/Public Service | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 899 | 185 | 12
Large Office | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 1195 | 157 | 10
Lodging - Large Hotel | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 597 | 17 | 1
Lodging - Small Hotel | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 597 | 17 | 1
Medium Office | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 1195 | 157 | 10
Multifamily Common Areas | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 118 | 958 | 63
Restaurant - Full Service | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 572 | 265 | 18
Restaurant - Quick Service | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 572 | 265 | 18
Retail - Standalone | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 748 | 192 | 13
Retail - Strip mall | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 780 | 233 | 15
Small Office | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 1195 | 157 | 10
Warehouse - Other | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 426 | 193 | 13
Warehouse - Refrigerated | Bradford | DCV_VFD3 | Three-Speed Controls or VFD | 426 | 193 | 13
Data Center - No Economizer | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 403 | 98 | 6
Data Center - With Economizer | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 403 | 98 | 6
Education - College/University | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 429 | 618 | 41
Education - Primary School | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 429 | 618 | 41
Education - Secondary School | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 429 | 618 | 41
Grocery | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 497 | 664 | 44
Health - Hospital | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Health - Other | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Industrial Manufacturing - 1 Shift | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 818 | 30 | 2
Industrial Manufacturing - 2 Shift | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 818 | 30 | 2
Industrial Manufacturing - 3 Shift | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 818 | 30 | 2
Institutional/Public Service | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 1001 | 122 | 8
Large Office | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 1150 | 78 | 5
Lodging - Large Hotel | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Lodging - Small Hotel | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 603 | 19 | 1
Medium Office | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 1150 | 78 | 5
Multifamily Common Areas | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 165 | 836 | 55
Restaurant - Full Service | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 598 | 181 | 12
Restaurant - Quick Service | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 598 | 181 | 12
Retail - Standalone | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 751 | 129 | 9
Retail - Strip mall | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 778 | 170 | 11
Small Office | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 1150 | 78 | 5
Warehouse - Other | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 403 | 98 | 6
Warehouse - Refrigerated | Pittsburgh | DCV_VFD3 | Three-Speed Controls or VFD | 403 | 98 | 6
Data Center - No Economizer | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 410 | 120 | 8
Data Center - With Economizer | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 410 | 120 | 8
Education - College/University | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 403 | 718 | 48
Education - Primary School | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 403 | 718 | 48
Education - Secondary School | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 403 | 718 | 48
Grocery | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 485 | 739 | 49
Health - Hospital | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 601 | 19 | 1
Health - Other | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 601 | 19 | 1
Industrial Manufacturing - 1 Shift | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 818 | 33 | 2
Industrial Manufacturing - 2 Shift | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 818 | 33 | 2
Industrial Manufacturing - 3 Shift | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 818 | 33 | 2
Institutional/Public Service | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 972 | 137 | 9
Large Office | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 1163 | 96 | 6
Lodging - Large Hotel | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 601 | 19 | 1
Lodging - Small Hotel | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 601 | 19 | 1
Medium Office | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 1163 | 96 | 6
Multifamily Common Areas | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 152 | 865 | 57
Restaurant - Full Service | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 591 | 200 | 13
Restaurant - Quick Service | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 591 | 200 | 13
Retail - Standalone | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 750 | 143 | 10
Retail - Strip mall | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 778 | 184 | 12
Small Office | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 1163 | 96 | 6
Warehouse - Other | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 410 | 120 | 8
Warehouse - Refrigerated | Erie | DCV_VFD3 | Three-Speed Controls or VFD | 410 | 120 | 8
Table 3-61 Upflow and Downflow Ducted | [7 empty] | Table 3-61 Upflow Nonducted and Horizontal Flow
Equipment Type | Configuration | yHVAC_MinCapacity | yHVAC_MaxCapacity | Capacity Range | Concatenate | Minimum NSenCOP |  | Equipment Type | Configuration |  |  | Capacity Range | Concantenate | Minimum NSenCOP
Air-Cooled | Downflow Ducted | 0 | 80000 | <80,000 Btu/h | Air-Cooled Downflow Ducted <80,000 Btu/h | 2.7 |  | Air-Cooled | Upflow NonDucted | 0 | 65000 | <65,000 Btu/h | Air-Cooled Upflow NonDucted <65,000 Btu/h | 2.16
Air-Cooled | Upflow Ducted | 0 | 80000 | <80,000 Btu/h | Air-Cooled Upflow Ducted <80,000 Btu/h | 2.67 |  | Air-Cooled | Horizontal Flow | 0 | 65000 | <65,000 Btu/h | Air-Cooled Horizontal Flow <65,000 Btu/h | 2.65
Air-Cooled | Downflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Air-Cooled Downflow Ducted >=80,000 and <295,000 Btu/h | 2.58 |  | Air-Cooled | Upflow NonDucted | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Air-Cooled Upflow NonDucted >=65,000 and <240,000 Btu/h | 2.04
Air-Cooled | Upflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Air-Cooled Upflow Ducted >=80,000 and <295,000 Btu/h | 2.55 |  | Air-Cooled | Horizontal Flow | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Air-Cooled Horizontal Flow >=65,000 and <240,000 Btu/h | 2.55
Air-Cooled | Downflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Air-Cooled Downflow Ducted >=295,000 and <930,000 Btu/h | 2.36 |  | Air-Cooled | Upflow NonDucted | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Air-Cooled Upflow NonDucted >=240,000 and <760,000 Btu/h | 1.89
Air-Cooled | Upflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Air-Cooled Upflow Ducted >=295,000 and <930,000 Btu/h | 2.33 |  | Air-Cooled | Horizontal Flow | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Air-Cooled Horizontal Flow >=240,000 and <760,000 Btu/h | 2.47
Air-Cooled with Fluid Economizer | Downflow Ducted | 0 | 80000 | <80,000 Btu/h | Air-Cooled with Fluid Economizer Downflow Ducted <80,000 Btu/h | 2.7 |  | Air-Cooled with Fluid Economizer | Upflow NonDucted | 0 | 65000 | <65,000 Btu/h | Air-Cooled with Fluid Economizer Upflow NonDucted <65,000 Btu/h | 2.09
Air-Cooled with Fluid Economizer | Upflow Ducted | 0 | 80000 | <80,000 Btu/h | Air-Cooled with Fluid Economizer Upflow Ducted <80,000 Btu/h | 2.67 |  | Air-Cooled with Fluid Economizer | Horizontal Flow | 0 | 65000 | <65,000 Btu/h | Air-Cooled with Fluid Economizer Horizontal Flow <65,000 Btu/h | 2.65
Air-Cooled with Fluid Economizer | Downflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Air-Cooled with Fluid Economizer Downflow Ducted >=80,000 and <295,000 Btu/h | 2.58 |  | Air-Cooled with Fluid Economizer | Upflow NonDucted | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Air-Cooled with Fluid Economizer Upflow NonDucted >=65,000 and <240,000 Btu/h | 1.99
Air-Cooled with Fluid Economizer | Upflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Air-Cooled with Fluid Economizer Upflow Ducted >=80,000 and <295,000 Btu/h | 2.55 |  | Air-Cooled with Fluid Economizer | Horizontal Flow | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Air-Cooled with Fluid Economizer Horizontal Flow >=65,000 and <240,000 Btu/h | 2.55
Air-Cooled with Fluid Economizer | Downflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Air-Cooled with Fluid Economizer Downflow Ducted >=295,000 and <930,000 Btu/h | 2.36 |  | Air-Cooled with Fluid Economizer | Upflow NonDucted | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Air-Cooled with Fluid Economizer Upflow NonDucted >=240,000 and <760,000 Btu/h | 1.81
Air-Cooled with Fluid Economizer | Upflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Air-Cooled with Fluid Economizer Upflow Ducted >=295,000 and <930,000 Btu/h | 2.33 |  | Air-Cooled with Fluid Economizer | Horizontal Flow | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Air-Cooled with Fluid Economizer Horizontal Flow >=240,000 and <760,000 Btu/h | 2.47
Water-Cooled | Downflow Ducted | 0 | 80000 | <80,000 Btu/h | Water-Cooled Downflow Ducted <80,000 Btu/h | 2.82 |  | Water-Cooled | Upflow NonDucted | 0 | 65000 | <65,000 Btu/h | Water-Cooled Upflow NonDucted <65,000 Btu/h | 2.43
Water-Cooled | Upflow Ducted | 0 | 80000 | <80,000 Btu/h | Water-Cooled Upflow Ducted <80,000 Btu/h | 2.79 |  | Water-Cooled | Horizontal Flow | 0 | 65000 | <65,000 Btu/h | Water-Cooled Horizontal Flow <65,000 Btu/h | 2.79
Water-Cooled | Downflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Water-Cooled Downflow Ducted >=80,000 and <295,000 Btu/h | 2.73 |  | Water-Cooled | Upflow NonDucted | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Water-Cooled Upflow NonDucted >=65,000 and <240,000 Btu/h | 2.32
Water-Cooled | Upflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Water-Cooled Upflow Ducted >=80,000 and <295,000 Btu/h | 2.7 |  | Water-Cooled | Horizontal Flow | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Water-Cooled Horizontal Flow >=65,000 and <240,000 Btu/h | 2.68
Water-Cooled | Downflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Water-Cooled Downflow Ducted >=295,000 and <930,000 Btu/h | 2.67 |  | Water-Cooled | Upflow NonDucted | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Water-Cooled Upflow NonDucted >=240,000 and <760,000 Btu/h | 2.2
Water-Cooled | Upflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Water-Cooled Upflow Ducted >=295,000 and <930,000 Btu/h | 2.64 |  | Water-Cooled | Horizontal Flow | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Water-Cooled Horizontal Flow >=240,000 and <760,000 Btu/h | 2.6
Water-Cooled with Fluid Economizer | Downflow Ducted | 0 | 80000 | <80,000 Btu/h | Water-Cooled with Fluid Economizer Downflow Ducted <80,000 Btu/h | 2.77 |  | Water-Cooled with Fluid Economizer | Upflow NonDucted | 0 | 65000 | <65,000 Btu/h | Water-Cooled with Fluid Economizer Upflow NonDucted <65,000 Btu/h | 2.35
Water-Cooled with Fluid Economizer | Upflow Ducted | 0 | 80000 | <80,000 Btu/h | Water-Cooled with Fluid Economizer Upflow Ducted <80,000 Btu/h | 2.74 |  | Water-Cooled with Fluid Economizer | Horizontal Flow | 0 | 65000 | <65,000 Btu/h | Water-Cooled with Fluid Economizer Horizontal Flow <65,000 Btu/h | 2.71
Water-Cooled with Fluid Economizer | Downflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Water-Cooled with Fluid Economizer Downflow Ducted >=80,000 and <295,000 Btu/h | 2.68 |  | Water-Cooled with Fluid Economizer | Upflow NonDucted | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Water-Cooled with Fluid Economizer Upflow NonDucted >=65,000 and <240,000 Btu/h | 2.24
Water-Cooled with Fluid Economizer | Upflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Water-Cooled with Fluid Economizer Upflow Ducted >=80,000 and <295,000 Btu/h | 2.65 |  | Water-Cooled with Fluid Economizer | Horizontal Flow | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Water-Cooled with Fluid Economizer Horizontal Flow >=65,000 and <240,000 Btu/h | 2.6
Water-Cooled with Fluid Economizer | Downflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Water-Cooled with Fluid Economizer Downflow Ducted >=295,000 and <930,000 Btu/h | 2.61 |  | Water-Cooled with Fluid Economizer | Upflow NonDucted | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Water-Cooled with Fluid Economizer Upflow NonDucted >=240,000 and <760,000 Btu/h | 2.12
Water-Cooled with Fluid Economizer | Upflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Water-Cooled with Fluid Economizer Upflow Ducted >=295,000 and <930,000 Btu/h | 2.58 |  | Water-Cooled with Fluid Economizer | Horizontal Flow | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Water-Cooled with Fluid Economizer Horizontal Flow >=240,000 and <760,000 Btu/h | 2.54
Glyco-Cooled | Downflow Ducted | 0 | 80000 | <80,000 Btu/h | Glyco-Cooled Downflow Ducted <80,000 Btu/h | 2.56 |  | Glyco-Cooled | Upflow NonDucted | 0 | 65000 | <65,000 Btu/h | Glyco-Cooled Upflow NonDucted <65,000 Btu/h | 2.08
Glyco-Cooled | Upflow Ducted | 0 | 80000 | <80,000 Btu/h | Glyco-Cooled Upflow Ducted <80,000 Btu/h | 2.53 |  | Glyco-Cooled | Horizontal Flow | 0 | 65000 | <65,000 Btu/h | Glyco-Cooled Horizontal Flow <65,000 Btu/h | 2.48
Glyco-Cooled | Downflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Glyco-Cooled Downflow Ducted >=80,000 and <295,000 Btu/h | 2.24 |  | Glyco-Cooled | Upflow NonDucted | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Glyco-Cooled Upflow NonDucted >=65,000 and <240,000 Btu/h | 1.9
Glyco-Cooled | Upflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Glyco-Cooled Upflow Ducted >=80,000 and <295,000 Btu/h | 2.21 |  | Glyco-Cooled | Horizontal Flow | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Glyco-Cooled Horizontal Flow >=65,000 and <240,000 Btu/h | 2.18
Glyco-Cooled | Downflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Glyco-Cooled Downflow Ducted >=295,000 and <930,000 Btu/h | 2.21 |  | Glyco-Cooled | Upflow NonDucted | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Glyco-Cooled Upflow NonDucted >=240,000 and <760,000 Btu/h | 1.81
Glyco-Cooled | Upflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Glyco-Cooled Upflow Ducted >=295,000 and <930,000 Btu/h | 2.18 |  | Glyco-Cooled | Horizontal Flow | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Glyco-Cooled Horizontal Flow >=240,000 and <760,000 Btu/h | 2.18
Glyco-Cooled with Fluid Economizer | Downflow Ducted | 0 | 80000 | <80,000 Btu/h | Glyco-Cooled with Fluid Economizer Downflow Ducted <80,000 Btu/h | 2.51 |  | Glyco-Cooled with Fluid Economizer | Upflow NonDucted | 0 | 65000 | <65,000 Btu/h | Glyco-Cooled with Fluid Economizer Upflow NonDucted <65,000 Btu/h | 2
Glyco-Cooled with Fluid Economizer | Upflow Ducted | 0 | 80000 | <80,000 Btu/h | Glyco-Cooled with Fluid Economizer Upflow Ducted <80,000 Btu/h | 2.48 |  | Glyco-Cooled with Fluid Economizer | Horizontal Flow | 0 | 65000 | <65,000 Btu/h | Glyco-Cooled with Fluid Economizer Horizontal Flow <65,000 Btu/h | 2.44
Glyco-Cooled with Fluid Economizer | Downflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Glyco-Cooled with Fluid Economizer Downflow Ducted >=80,000 and <295,000 Btu/h | 2.19 |  | Glyco-Cooled with Fluid Economizer | Upflow NonDucted | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Glyco-Cooled with Fluid Economizer Upflow NonDucted >=65,000 and <240,000 Btu/h | 1.82
Glyco-Cooled with Fluid Economizer | Upflow Ducted | 80000 | 295000 | >=80,000 and <295,000 Btu/h | Glyco-Cooled with Fluid Economizer Upflow Ducted >=80,000 and <295,000 Btu/h | 2.16 |  | Glyco-Cooled with Fluid Economizer | Horizontal Flow | 65000 | 240000 | >=65,000 and <240,000 Btu/h | Glyco-Cooled with Fluid Economizer Horizontal Flow >=65,000 and <240,000 Btu/h | 2.1
Glyco-Cooled with Fluid Economizer | Downflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Glyco-Cooled with Fluid Economizer Downflow Ducted >=295,000 and <930,000 Btu/h | 2.15 |  | Glyco-Cooled with Fluid Economizer | Upflow NonDucted | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Glyco-Cooled with Fluid Economizer Upflow NonDucted >=240,000 and <760,000 Btu/h | 1.73
Glyco-Cooled with Fluid Economizer | Upflow Ducted | 295000 | 930000 | >=295,000 and <930,000 Btu/h | Glyco-Cooled with Fluid Economizer Upflow Ducted >=295,000 and <930,000 Btu/h | 2.12 |  | Glyco-Cooled with Fluid Economizer | Horizontal Flow | 240000 | 760000 | >=240,000 and <760,000 Btu/h | Glyco-Cooled with Fluid Economizer Horizontal Flow >=240,000 and <760,000 Btu/h | 2.1
[8 empty] | Glyco-Cooled with Fluid Economizer | Upflow Non-Ducted / Horizontal | >=240,000 and <760,000 Btu/h | NSenCOP Upflow non-ducted |  | 1.73
[8 empty] | Glyco-Cooled with Fluid Economizer | Upflow Non-Ducted / Horizontal | >=240,000 and <760,000 Btu/h | NSenCOP Horizontal flow |  | 2.1
Note on AZ4: Priyam Parikh: Not in TRM
Note on M27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Archive or delete

## Drop down (hidden)
Drop Down Table 1 | Drop Down Table 2 | Drop Down Table 3 | Drop Down Table 4 | Drop Down Table 5 | Drop Down Table 6 | Drop Down Table 7 | Drop Down Table 8 | Drop Down Table 9 | Drop Down Table 10 | Drop Down Table 11 | Drop Down Table 12 | Drop Down Table 13 | Drop Down Table 14 | Drop Down Table 15 | Drop Down Table 16 | Drop Down Table 17 | Drop Down Table 18 | Drop Down Table 19 | Drop Down Table 20 | Drop Down Table 21 | Drop Down Table 22 | Drop Down Table 23 | Drop Down Table 24 | Drop Down Table 25 | Drop Down Table 26
yBuilding_Type_HVAC | yBuilding Type_Chillers | yBuildingType_GuestRooms | yProject_Type | yEfficiencyKnown | xBuilding_Location | HVAC Equipment Type | Economizer HVAC Equipment Type | Chiller Equipment Type | Geothermal Equipment Type | yGR_EqmtType_Motel | yGR_EqmtType_Hotel | Electric Resistance? | Fuel Switching Equipment Type_Electric | Fuel Switching Equipment Type_NonElectric | PTAC/PTHP Type | yOperating_Schedule | xExpValve | yRefCharge% | yDHPBaseHeatingEquipment Type | yDHPBaseCoolingEquipment Type | yMotorSize | yMotorType | yMotorPoles | y_RACeqmttype | yRAC_options
Assembly | Education - Community College | Hotel | Early Replacement | Nameplate Efficiency Values known | Allentown | Air-Source Air Conditioner | Air-Source Air Conditioner | Air Cooled Chiller | Air-Source Heat Pumps | PTAC with Electric Resistance Heat | PTAC with Electric Resistance Heat | Yes | Air-Source Heat Pumps | Gas Furnace | Standard | 1 Shift, 5 days per week | TXV | 0.6 | Standard Ductless Heat Pump | Standard Ductless Heat Pump | 1 | Open | 2 poles | Room Air Conditioners | Without Louvered Sides
Education - Community College | Education - Secondary School | Motel | End of Useful Life or New Construction | Nameplate Efficiency Values NOT known | Erie | Air-Source Heat Pumps | Air-Source Heat Pumps | Water Cooled Chiller: Positive Displacement or Reciprocating | Water-Source Heat Pumps | PTAC with Gas Heat | PTAC with Gas Heat | No | Electric Furnace | Oil Furnace | Non Standard | 2 Shift, 5 days per week | Orifice | 0.59 | Electric Resistance | Central Air Conditioning | 1.5 | Enclosed | 4 poles | Reverse Cycle Room Air Conditioners | With Louvered Sides
Education - Primary School | Education - University |  |  |  | Harrisburg | Water Cooled Air Conditioners | Water Cooled Air Conditioners | Water Cooled Chiller: Centrifugal | Ground Water Source Heat Pumps | PTHP | PTHP |  | Baseboard Heating | Gas/Propane Steam Boiler |  | 3 Shift, 5 days per week |  | 0.58 | Air-Source Heat Pump | Air-Source Heat Pump | 2 |  | 6 poles | Casement-Only Room Air Conditioners
Education - Relocatable Classroom | Health/Medical - Hospital |  |  |  | Philadelphia | Evaporatively Cooled Air Conditioners | Evaporatively Cooled Air Conditioners |  |  | Ground Source Heat Pumps |  | Central HW Fan Coil with Electric Resistance Heat |  | PTHP | Gas/Propane Hot Water Boiler |  | 24/7 |  | 0.57 | Electric Furnace | Room Air Conditoner | 3 |  | 8 poles | Casement-Slider Room Air Conditioners
Education - Secondary School | Health/Medical - Nursing Home |  |  |  | Pittsburgh | PTAC |  |  |  | Other |  | Central HW Fan Coil with Gas Heat |  |  | Oil Steam Boiler |  |  |  | 0.56 | PTHP | PTAC | 5
Education - University | Lodging - Hotel |  |  |  | Scranton | PTHP | [8 empty] | Oil Hot Water Boiler |  |  |  | 0.55 | New Space/No existing heat/Non-electric Heat | PTHP | 7.5
Grocery | Manufacturing – Bio Tech/High Tech |  |  |  | Williamsport | [16 empty] | 0.54 | New Space/No existing cooling | New Space/No existing cooling | 10
Health/Medical - Hospital | Office - Large | [20 empty] | 0.53 |  | 0.35 | 15
Health/Medical - Nursing Home | Office - Small | [20 empty] | 0.52 |  | 0.34 | 20
Lodging - Hotel | Retail - Multistory Large | [20 empty] | 0.51 |  | 0.33 | Other
Manufacturing – Bio Tech/High Tech | [21 empty] | 0.5 |  | 0.32 | Other
Manufacturing – 1 Shift/Light Industrial | [21 empty] | 0.49 |  | 0.31
Multi-Family (Common Areas) | [21 empty] | 0.48 |  | 0.3
Office - Large | [21 empty] | 0.47 |  | 0.29
Office - Small | [21 empty] | 0.46 |  | 0.28
Restaurant - Fast-Food | [21 empty] | 0.45 |  | 0.27
Restaurant - Sit-Down | [21 empty] | 0.44 |  | 0.26
Retail - Multistory Large | [21 empty] | 0.43 |  | 0.25
Retail - Single-Story Large | [21 empty] | 0.42 |  | 0.24
Retail - Small | [21 empty] | 0.41 |  | 0.23
Storage - Conditioned | [21 empty] | 0.4
Warehouse - Refrigerated | [21 empty] | 0.39
0.38
0.37
0.36
0.22
0.21
0.2
0.19
0.18
0.17
0.16
0.15
0.14
0.13
0.12
0.11
0.1
0.09
0.08
0.07
0.06
0.05
0.04
0.03
0.02
0.01
0
-0.01
-0.02
-0.03
-0.04
-0.05
-0.06
-0.07
-0.08
-0.09
-0.1
-0.11
-0.12
-0.13
-0.14
-0.15
-0.16
-0.17
-0.18
-0.19
-0.2
-0.21
-0.22
-0.23
-0.24
-0.25
-0.26
-0.27
-0.28
-0.29
-0.3
-0.31
-0.32
-0.33
-0.34
-0.35

## Appendix G Front End (hidden)
Adjustment of Programmable Thermostats for Commercial and Industrial Buildings
USER INPUTS | [16 empty] | RESULTS
Location | [16 empty] | Unit kWh Savings per Year
Building Main Type | [6 empty] | #N/A | [9 empty] | #N/A | kWh
Number of Holidays / Shutdown Days | [6 empty] | 0 | [9 empty] | Unit Therms Savings per Year
Cooling | [16 empty] | #N/A | Therms
Cooling System Type | [6 empty] | Central AC | [9 empty] | Peak Summer Demand Reduction
Cooling Capacity (Tons) of the controlled equipment | [6 empty] | 5 | ton | [8 empty] | 0 | kW
Efficiency rating of controlled equipment | [6 empty] | 15 | [9 empty] | Peak Winter Demand Reduction
Efficiency rating Type | [6 empty] | SEER | [9 empty] | 0 | kW
Heating
Heating System Type | [6 empty] | Furnace
Heating Capacity of the controlled equipment | [6 empty] | 5 | kBtu
Efficiency rating of controlled equipment | [6 empty] | 8
Efficiency rating Type | [6 empty] | HSPF
Baseline Cooling Schedule | [8 empty] | Proposed Cooling Schedule
Day/ Hour | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Day/ Hour | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday
1 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 1 | 80 | 80 | 80 | 80 | 80 | 80 | 80
2 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 2 | 80 | 80 | 80 | 80 | 80 | 80 | 80
3 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80
4 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80
5 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80
6 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 6 | 80 | 80 | 80 | 80 | 80 | 80 | 80
7 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 7 | 80 | 80 | 80 | 80 | 80 | 80 | 80
8 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 8 | 77 | 77 | 77 | 77 | 77 | 80 | 80
9 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 9 | 77 | 77 | 77 | 77 | 77 | 80 | 80
10 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 10 | 77 | 77 | 77 | 77 | 77 | 80 | 80
11 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 11 | 77 | 77 | 77 | 77 | 77 | 80 | 80
12 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 12 | 77 | 77 | 77 | 77 | 77 | 80 | 80
13 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 13 | 77 | 77 | 77 | 77 | 77 | 80 | 80
14 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 14 | 77 | 77 | 77 | 77 | 77 | 80 | 80
15 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 15 | 77 | 77 | 77 | 77 | 77 | 80 | 80
16 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 16 | 77 | 77 | 77 | 77 | 77 | 80 | 80
17 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 17 | 77 | 77 | 77 | 77 | 77 | 80 | 80
18 | 72 | 72 | 72 | 72 | 72 | 78 | 78 |  | 18 | 77 | 77 | 77 | 77 | 77 | 80 | 80
19 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 19 | 80 | 80 | 80 | 80 | 80 | 80 | 80
20 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 20 | 80 | 80 | 80 | 80 | 80 | 80 | 80
21 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 21 | 80 | 80 | 80 | 80 | 80 | 80 | 80
22 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 22 | 80 | 80 | 80 | 80 | 80 | 80 | 80
23 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 23 | 80 | 80 | 80 | 80 | 80 | 80 | 80
24 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 24 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Baseline Heating Schedule | [8 empty] | Proposed Heating Schedule
Day/ Hour | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Day/ Hour | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday
1 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 1 | 64 | 64 | 64 | 64 | 64 | 64 | 64
2 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 2 | 64 | 64 | 64 | 64 | 64 | 64 | 64
3 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 3 | 64 | 64 | 64 | 64 | 64 | 64 | 64
4 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 4 | 64 | 64 | 64 | 64 | 64 | 64 | 64
5 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 5 | 64 | 64 | 64 | 64 | 64 | 64 | 64
6 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 6 | 64 | 64 | 64 | 64 | 64 | 64 | 64
7 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 7 | 64 | 64 | 64 | 64 | 64 | 64 | 64
8 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 8 | 70 | 70 | 70 | 70 | 70 | 64 | 64
9 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 9 | 70 | 70 | 70 | 70 | 70 | 64 | 64
10 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 10 | 70 | 70 | 70 | 70 | 70 | 64 | 64
11 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 11 | 70 | 70 | 70 | 70 | 70 | 64 | 64
12 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 12 | 70 | 70 | 70 | 70 | 70 | 64 | 64
13 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 13 | 70 | 70 | 70 | 70 | 70 | 64 | 64
14 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 14 | 70 | 70 | 70 | 70 | 70 | 64 | 64
15 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 15 | 70 | 70 | 70 | 70 | 70 | 64 | 64
16 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 16 | 70 | 70 | 70 | 70 | 70 | 64 | 64
17 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 17 | 70 | 70 | 70 | 70 | 70 | 64 | 64
18 | 70 | 70 | 70 | 70 | 70 | 66 | 66 |  | 18 | 70 | 70 | 70 | 70 | 70 | 64 | 64
19 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 19 | 64 | 64 | 64 | 64 | 64 | 64 | 64
20 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 20 | 64 | 64 | 64 | 64 | 64 | 64 | 64
21 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 21 | 64 | 64 | 64 | 64 | 64 | 64 | 64
22 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 22 | 64 | 64 | 64 | 64 | 64 | 64 | 64
23 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 23 | 64 | 64 | 64 | 64 | 64 | 64 | 64
24 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 24 | 64 | 64 | 64 | 64 | 64 | 64 | 64
SELECT
SELECT
SELECT
ENTER
ENTER
ENTER
Update
Update
ENTER

## Conversions (hidden)
|  |  | Demand efficiency | Energy efficiency; Cool
|  |  | 13.0385 | 14.9011
| to EER | to SEER/IEER | Demand | Efficiency
EER | 1 | 1.1429 | 15 | 17.1429
EER2 | 1 | 1.1429 | 15.6901 | 17.9315
SEER2 | 0.86923 | 1 | 13.7744 | 15.8466
SEER | 0.86923 | 1.1429 | 13.0385 | 14.9011
IEER | 0.86923 | 1 | 13.0385 | 13.0385
kW/ton |  |  | 0.8 | 0.8
Energy efficiency; Heating
8
to HSPF
HSPF | 8
HSPF2 | 9.4316
COP | 27.296
kW/ton | 1.5
AFUE | 9999999999

## Appendix G Calculations (hidden)
Based on DEER Prototypes Simulation Runs using eQuest v3.65. Refer to to detailed results in a separate workbook
Calculations: |  |  | Cooling (Setpoints) |  | Heating (Setpoints)
Equivalent Full Load Hours Cooling (EFLHC) | #N/A | Building Type | Intercept | X Variable | Intercept | X Variable
Equivalent Full Load Hours Heating (EFLH) | #N/A | Education - College/University | 0 | 1.2503e-05 | 0 | 2.649e-05
Number of Holidays | 0 | Education - Other | 0 | 1.2503e-05 | 0 | 2.649e-05
Baseline CDH (Setpoints) | #N/A | Grocery | 0 | 1.1728e-05 | 0 | 1.802e-05
Proposed CDH (Setpoints) | #N/A | Health - Hospital | 0 | 6.7148e-06 | 0 | 1.5012e-05
Delta CDH (Setpoints) | #N/A | Health - Other | 0 | 9.7425e-06 | 0 | 4.7071e-05
Baseline CDH (Setbacks) | 0 | Industrial Manufacturing | 0 | 1.136e-05 | 0 | 1.5588e-05
Proposed CDH (Setbacks) | 0 | Institutional/Public Service | 0 | 1.1125e-05 | 0 | 1.7224e-05
Delta CDH (Setbacks) | 0 | Lodging | 0 | 1.2126e-05 | 0 | 2.2201e-05
Baseline HDH (setpoints) | #N/A | Multifamily (Common Areas) | 0 | 1.1125e-05 | 0 | 1.7224e-05
Proposed HDH (setpoints) | #N/A | Office | 0 | 9.7425e-06 | 0 | 4.7071e-05
Delta HDH (setpoints) | #N/A | Restaurant | 0 | 8.4028e-06 | 0 | 2.1841e-05
Baseline HDH (setbacks) | 0 | Retail | 0 | 1.1728e-05 | 0 | 1.802e-05
Proposed HDH (setbacks) | 0 | Warehouse - Other | 0 | 1.9493e-05 | 0 | 1.9652e-05
Delta HDH (setbacks) | 0 | Warehouse - Refrigerated | 0 | 1.9493e-05 | 0 | 1.9652e-05
Cooling Setpoint Flag | #N/A
Cooling Setback Flag | 0
Heating Setpoint Flag | #N/A
Heating Setback Flag | 0
Cooling kW/ton | 0.80531
Heating kW/ton (HP) | 1.5
Heating kW (Electric Resistance) | 0
Baseline Cooling Energy Use | #N/A
Baseline Heating Energy Use (Heat Pump) | 0
Baseline Heating Energy Use (Electric Resistance) | #N/A
Baseline Heating Energy Use (Furnace) | #N/A
Percent Savings Cooling (Setpoints) | #N/A
Percent Savings Cooling (Setbacks) | #N/A
Percent Savings Heating (Setpoints) | #N/A
Percent Savings Heating (Setbacks) | #N/A
Cooling kWh Savings | #N/A
Heating kWh Savings | #N/A
Heating Therm Savings | #N/A

## CDH & HDH (hidden)
[9 empty] | deCDHTotal/delCDHPeak | #N/A | delHDHTotal/delHDHPeak | #N/A
[9 empty] | delCDHPeak | #N/A | delHDHPeak | #N/A
[9 empty] | delCDHTotal | #N/A | delHDHTotal | #N/A
[9 empty] | Cooling |  | Heating
[8 empty] | Peak | #N/A | #N/A | #N/A | #N/A
[8 empty] | Annual Degree Hours | #N/A | #N/A | #N/A | #N/A | [9 empty] | #N/A
[8 empty] | Setpoints | #N/A | #N/A | #N/A | #N/A | [9 empty] | #N/A | #N/A
[8 empty] | Setbacks | #N/A | #N/A | #N/A | #N/A
Date | Month | WD | Hour | Peak | OAT (oF) | Season | Initial | Final | Baseline CDH | Measure CDH | Baseline HDH | Measure HDH | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
2022-01-01 | 1 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 31 | 20 | 30 | 37 | 36 | 32 | 26 | 23 | 0 | 0
2022-01-01 01:00 | 1 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 31 | 19 | 30 | 36 | 36 | 29 | 24 | 23 | 0 | 0
2022-01-01 02:00 | 1 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 29 | 18 | 30 | 36 | 36 | 29 | 23 | 23 | 0 | 0
2022-01-01 03:00 | 1 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 28 | 17 | 30 | 35 | 34 | 29 | 23 | 22 | 0 | 0
2022-01-01 04:00 | 1 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 27 | 17 | 30 | 35 | 34 | 29 | 23 | 23 | 0 | 0
2022-01-01 05:00 | 1 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 26 | 16 | 30 | 34 | 33 | 30 | 22 | 22 | 0 | 0
2022-01-01 06:00 | 1 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 24 | 16 | 30 | 34 | 33 | 30 | 22 | 23 | 0 | 0
2022-01-01 07:00 | 1 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 24 | 19 | 30 | 34 | 34 | 32 | 22 | 22 | 0 | 0
2022-01-01 08:00 | 1 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 24 | 21 | 30 | 34 | 34 | 31 | 26 | 24 | 0 | 0
2022-01-01 09:00 | 1 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 24 | 24 | 30 | 34 | 35 | 32 | 27 | 26 | 0 | 0
2022-01-01 10:00 | 1 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 24 | 28 | 31 | 35 | 35 | 33 | 31 | 29 | 0 | 0
2022-01-01 11:00 | 1 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 24 | 33 | 31 | 36 | 36 | 34 | 35 | 31 | 0 | 0
2022-01-01 12:00 | 1 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 24 | 37 | 32 | 37 | 37 | 35 | 36 | 32 | 0 | 0
2022-01-01 13:00 | 1 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 25 | 37 | 32 | 37 | 38 | 36 | 39 | 33 | 0 | 0
2022-01-01 14:00 | 1 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 25 | 37 | 31 | 36 | 38 | 36 | 40 | 33 | 0 | 0
2022-01-01 15:00 | 1 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 25 | 37 | 31 | 36 | 37 | 36 | 39 | 34 | 0 | 0
2022-01-01 16:00 | 1 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 22 | 35 | 31 | 35 | 35 | 35 | 37 | 33 | 0 | 0
2022-01-01 17:00 | 1 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 21 | 32 | 31 | 33 | 34 | 34 | 34 | 32 | 0 | 0
2022-01-01 18:00 | 1 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 22 | 30 | 31 | 32 | 33 | 34 | 33 | 32 | 0 | 0
2022-01-01 19:00 | 1 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 21 | 28 | 31 | 32 | 32 | 32 | 32 | 31 | 0 | 0
2022-01-01 20:00 | 1 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 21 | 27 | 32 | 32 | 31 | 32 | 32 | 31 | 0 | 0
2022-01-01 21:00 | 1 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 21 | 25 | 32 | 32 | 29 | 32 | 30 | 31 | 0 | 0
2022-01-01 22:00 | 1 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 22 | 25 | 32 | 31 | 30 | 31 | 29 | 31 | 0 | 0
2022-01-01 23:00 | 1 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 22 | 25 | 31 | 30 | 29 | 31 | 28 | 31 | 0 | 0
2022-01-02 | 1 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 23 | 25 | 31 | 29 | 27 | 31 | 28 | 31 | 0 | 0
2022-01-02 01:00 | 1 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 23 | 25 | 31 | 28 | 26 | 31 | 26 | 31 | 0 | 0
2022-01-02 02:00 | 1 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 23 | 25 | 30 | 26 | 24 | 31 | 25 | 31 | 0 | 0
2022-01-02 03:00 | 1 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 24 | 25 | 30 | 25 | 24 | 31 | 24 | 31 | 0 | 0
2022-01-02 04:00 | 1 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 23 | 25 | 30 | 23 | 23 | 32 | 28 | 31 | 0 | 0
2022-01-02 05:00 | 1 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 23 | 25 | 30 | 22 | 22 | 31 | 29 | 31 | 0 | 0
2022-01-02 06:00 | 1 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 24 | 25 | 30 | 20 | 21 | 30 | 29 | 31 | 0 | 0
2022-01-02 07:00 | 1 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 25 | 25 | 30 | 21 | 22 | 32 | 30 | 31 | 0 | 0
2022-01-02 08:00 | 1 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 26 | 25 | 29 | 22 | 24 | 31 | 30 | 32 | 0 | 0
2022-01-02 09:00 | 1 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 27 | 25 | 29 | 23 | 26 | 32 | 31 | 32 | 0 | 0
2022-01-02 10:00 | 1 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 30 | 25 | 29 | 25 | 27 | 32 | 32 | 30 | 0 | 0
2022-01-02 11:00 | 1 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 31 | 25 | 29 | 27 | 29 | 32 | 32 | 30 | 0 | 0
2022-01-02 12:00 | 1 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 32 | 25 | 29 | 29 | 31 | 33 | 33 | 30 | 0 | 0
2022-01-02 13:00 | 1 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 35 | 25 | 29 | 29 | 33 | 33 | 33 | 30 | 0 | 0
2022-01-02 14:00 | 1 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 36 | 25 | 29 | 30 | 33 | 33 | 33 | 31 | 0 | 0
2022-01-02 15:00 | 1 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 36 | 25 | 29 | 30 | 33 | 33 | 34 | 29 | 0 | 0
2022-01-02 16:00 | 1 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 36 | 25 | 29 | 30 | 30 | 32 | 33 | 29 | 0 | 0
2022-01-02 17:00 | 1 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 36 | 24 | 29 | 30 | 31 | 32 | 33 | 29 | 0 | 0
2022-01-02 18:00 | 1 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 36 | 24 | 29 | 30 | 31 | 33 | 34 | 29 | 0 | 0
2022-01-02 19:00 | 1 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 36 | 24 | 29 | 30 | 30 | 32 | 34 | 29 | 0 | 0
2022-01-02 20:00 | 1 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 35 | 24 | 29 | 30 | 28 | 32 | 34 | 28 | 0 | 0
2022-01-02 21:00 | 1 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 34 | 24 | 29 | 30 | 29 | 31 | 34 | 28 | 0 | 0
2022-01-02 22:00 | 1 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 34 | 24 | 29 | 30 | 30 | 31 | 34 | 28 | 0 | 0
2022-01-02 23:00 | 1 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 34 | 23 | 29 | 30 | 30 | 32 | 33 | 28 | 0 | 0
2022-01-03 | 1 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 33 | 23 | 29 | 30 | 30 | 32 | 33 | 28 | 0 | 0
2022-01-03 01:00 | 1 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 33 | 23 | 28 | 30 | 33 | 31 | 32 | 29 | 0 | 0
2022-01-03 02:00 | 1 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 34 | 24 | 28 | 31 | 34 | 32 | 29 | 29 | 0 | 0
2022-01-03 03:00 | 1 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 34 | 24 | 27 | 31 | 34 | 30 | 28 | 29 | 0 | 0
2022-01-03 04:00 | 1 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 34 | 24 | 27 | 32 | 34 | 30 | 27 | 30 | 0 | 0
2022-01-03 05:00 | 1 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 35 | 24 | 26 | 32 | 34 | 30 | 26 | 31 | 0 | 0
2022-01-03 06:00 | 1 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 35 | 24 | 26 | 33 | 35 | 30 | 26 | 32 | 0 | 0
2022-01-03 07:00 | 1 | 1 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 36 | 24 | 26 | 33 | 37 | 32 | 25 | 34 | 0 | 0
2022-01-03 08:00 | 1 | 1 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 36 | 23 | 25 | 34 | 38 | 32 | 26 | 34 | 0 | 0
2022-01-03 09:00 | 1 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 37 | 23 | 25 | 34 | 38 | 32 | 26 | 35 | 0 | 0
2022-01-03 10:00 | 1 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 38 | 24 | 25 | 34 | 38 | 31 | 27 | 37 | 0 | 0
2022-01-03 11:00 | 1 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 39 | 25 | 24 | 35 | 38 | 32 | 28 | 38 | 0 | 0
2022-01-03 12:00 | 1 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 38 | 26 | 24 | 35 | 39 | 34 | 29 | 39 | 0 | 0
2022-01-03 13:00 | 1 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 38 | 25 | 24 | 35 | 39 | 34 | 30 | 40 | 0 | 0
2022-01-03 14:00 | 1 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 37 | 24 | 25 | 35 | 39 | 35 | 31 | 40 | 0 | 0
2022-01-03 15:00 | 1 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 35 | 23 | 25 | 35 | 39 | 33 | 29 | 39 | 0 | 0
2022-01-03 16:00 | 1 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 35 | 22 | 25 | 36 | 39 | 32 | 28 | 36 | 0 | 0
2022-01-03 17:00 | 1 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 33 | 20 | 24 | 36 | 39 | 31 | 27 | 30 | 0 | 0
2022-01-03 18:00 | 1 | 1 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 33 | 19 | 24 | 37 | 39 | 30 | 25 | 30 | 0 | 0
2022-01-03 19:00 | 1 | 1 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 27 | 18 | 24 | 36 | 38 | 30 | 24 | 29 | 0 | 0
2022-01-03 20:00 | 1 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 23 | 16 | 24 | 36 | 36 | 28 | 24 | 27 | 0 | 0
2022-01-03 21:00 | 1 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 20 | 15 | 24 | 35 | 35 | 27 | 23 | 24 | 0 | 0
2022-01-03 22:00 | 1 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 19 | 14 | 23 | 34 | 35 | 27 | 23 | 26 | 0 | 0
2022-01-03 23:00 | 1 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 18 | 14 | 23 | 32 | 35 | 21 | 22 | 20 | 0 | 0
2022-01-04 | 1 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 18 | 13 | 22 | 31 | 33 | 20 | 21 | 21 | 0 | 0
2022-01-04 01:00 | 1 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 18 | 12 | 21 | 30 | 32 | 20 | 20 | 18 | 0 | 0
2022-01-04 02:00 | 1 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 18 | 12 | 19 | 28 | 31 | 18 | 18 | 20 | 0 | 0
2022-01-04 03:00 | 1 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 18 | 11 | 18 | 27 | 30 | 15 | 17 | 16 | 0 | 0
2022-01-04 04:00 | 1 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 18 | 9 | 16 | 26 | 29 | 14 | 18 | 20 | 0 | 0
2022-01-04 05:00 | 1 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 18 | 7 | 15 | 25 | 27 | 15 | 19 | 20 | 0 | 0
2022-01-04 06:00 | 1 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 18 | 5 | 13 | 24 | 36 | 15 | 18 | 17 | 0 | 0
2022-01-04 07:00 | 1 | 2 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 18 | 7 | 14 | 23 | 26 | 15 | 17 | 15 | 0 | 0
2022-01-04 08:00 | 1 | 2 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 18 | 10 | 15 | 23 | 27 | 15 | 17 | 17 | 0 | 0
2022-01-04 09:00 | 1 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 19 | 12 | 16 | 22 | 28 | 19 | 18 | 22 | 0 | 0
2022-01-04 10:00 | 1 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 21 | 14 | 18 | 24 | 28 | 23 | 19 | 26 | 0 | 0
2022-01-04 11:00 | 1 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 21 | 17 | 20 | 25 | 28 | 26 | 21 | 28 | 0 | 0
2022-01-04 12:00 | 1 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 22 | 19 | 22 | 27 | 30 | 27 | 22 | 29 | 0 | 0
2022-01-04 13:00 | 1 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 24 | 19 | 23 | 27 | 30 | 32 | 23 | 31 | 0 | 0
2022-01-04 14:00 | 1 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 22 | 20 | 24 | 26 | 29 | 32 | 24 | 32 | 0 | 0
2022-01-04 15:00 | 1 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 23 | 20 | 25 | 26 | 29 | 32 | 25 | 31 | 0 | 0
2022-01-04 16:00 | 1 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 22 | 19 | 25 | 25 | 27 | 31 | 26 | 28 | 0 | 0
2022-01-04 17:00 | 1 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 23 | 19 | 24 | 25 | 26 | 30 | 26 | 27 | 0 | 0
2022-01-04 18:00 | 1 | 2 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 23 | 18 | 24 | 24 | 25 | 28 | 26 | 22 | 0 | 0
2022-01-04 19:00 | 1 | 2 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 25 | 18 | 24 | 23 | 24 | 22 | 26 | 16 | 0 | 0
2022-01-04 20:00 | 1 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 27 | 17 | 23 | 22 | 23 | 25 | 23 | 16 | 0 | 0
2022-01-04 21:00 | 1 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 27 | 17 | 23 | 21 | 23 | 26 | 23 | 15 | 0 | 0
2022-01-04 22:00 | 1 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 27 | 17 | 22 | 21 | 22 | 24 | 22 | 16 | 0 | 0
2022-01-04 23:00 | 1 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 27 | 16 | 22 | 20 | 21 | 21 | 22 | 14 | 0 | 0
2022-01-05 | 1 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 28 | 16 | 21 | 20 | 21 | 23 | 22 | 13 | 0 | 0
2022-01-05 01:00 | 1 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 29 | 16 | 22 | 20 | 20 | 21 | 22 | 13 | 0 | 0
2022-01-05 02:00 | 1 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 29 | 15 | 23 | 19 | 20 | 18 | 22 | 13 | 0 | 0
2022-01-05 03:00 | 1 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 29 | 15 | 24 | 19 | 20 | 14 | 22 | 9 | 0 | 0
2022-01-05 04:00 | 1 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 29 | 14 | 24 | 19 | 19 | 15 | 23 | 5 | 0 | 0
2022-01-05 05:00 | 1 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 29 | 12 | 24 | 18 | 18 | 14 | 24 | 9 | 0 | 0
2022-01-05 06:00 | 1 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 30 | 11 | 24 | 18 | 18 | 13 | 24 | 12 | 0 | 0
2022-01-05 07:00 | 1 | 3 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 17 | 30 | 12 | 24 | 18 | 18 | 11 | 24 | 13 | 0 | 0
2022-01-05 08:00 | 1 | 3 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 18 | 30 | 13 | 24 | 19 | 21 | 16 | 26 | 16 | 0 | 0
2022-01-05 09:00 | 1 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 31 | 14 | 24 | 19 | 23 | 20 | 28 | 18 | 0 | 0
2022-01-05 10:00 | 1 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 32 | 16 | 25 | 21 | 25 | 24 | 29 | 22 | 0 | 0
2022-01-05 11:00 | 1 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 27 | 19 | 26 | 24 | 26 | 28 | 30 | 24 | 0 | 0
2022-01-05 12:00 | 1 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 27 | 21 | 27 | 26 | 28 | 30 | 32 | 28 | 0 | 0
2022-01-05 13:00 | 1 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 27 | 21 | 27 | 26 | 28 | 31 | 32 | 30 | 0 | 0
2022-01-05 14:00 | 1 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 24 | 21 | 27 | 27 | 28 | 33 | 33 | 34 | 0 | 0
2022-01-05 15:00 | 1 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 24 | 21 | 27 | 27 | 27 | 33 | 32 | 34 | 0 | 0
2022-01-05 16:00 | 1 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 24 | 19 | 27 | 26 | 25 | 31 | 31 | 34 | 0 | 0
2022-01-05 17:00 | 1 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 22 | 18 | 26 | 26 | 24 | 30 | 30 | 27 | 0 | 0
2022-01-05 18:00 | 1 | 3 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 22 | 16 | 26 | 25 | 23 | 28 | 30 | 24 | 0 | 0
2022-01-05 19:00 | 1 | 3 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 22 | 15 | 25 | 24 | 23 | 26 | 27 | 21 | 0 | 0
2022-01-05 20:00 | 1 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 21 | 13 | 23 | 22 | 21 | 26 | 25 | 21 | 0 | 0
2022-01-05 21:00 | 1 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 21 | 12 | 22 | 21 | 23 | 23 | 23 | 19 | 0 | 0
2022-01-05 22:00 | 1 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 21 | 10 | 20 | 19 | 23 | 21 | 22 | 18 | 0 | 0
2022-01-05 23:00 | 1 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 20 | 9 | 17 | 18 | 21 | 22 | 20 | 15 | 0 | 0
2022-01-06 | 1 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 21 | 7 | 15 | 16 | 20 | 19 | 19 | 13 | 0 | 0
2022-01-06 01:00 | 1 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 21 | 5 | 13 | 15 | 20 | 17 | 18 | 13 | 0 | 0
2022-01-06 02:00 | 1 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 22 | 3 | 12 | 14 | 19 | 19 | 17 | 13 | 0 | 0
2022-01-06 03:00 | 1 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 22 | 1 | 10 | 13 | 18 | 18 | 15 | 14 | 0 | 0
2022-01-06 04:00 | 1 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 22 | -1 | 10 | 13 | 18 | 15 | 15 | 13 | 0 | 0
2022-01-06 05:00 | 1 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 8 | 22 | -2 | 11 | 13 | 17 | 15 | 15 | 13 | 0 | 0
2022-01-06 06:00 | 1 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 7 | 22 | -4 | 11 | 13 | 16 | 14 | 15 | 12 | 0 | 0
2022-01-06 07:00 | 1 | 4 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 11 | 23 | -1 | 14 | 15 | 19 | 15 | 14 | 14 | 0 | 0
2022-01-06 08:00 | 1 | 4 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 15 | 20 | 2 | 16 | 16 | 21 | 19 | 15 | 16 | 0 | 0
2022-01-06 09:00 | 1 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 20 | 5 | 19 | 18 | 25 | 25 | 18 | 16 | 0 | 0
2022-01-06 10:00 | 1 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 21 | 11 | 22 | 22 | 28 | 29 | 20 | 18 | 0 | 0
2022-01-06 11:00 | 1 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 22 | 16 | 25 | 25 | 30 | 35 | 23 | 20 | 0 | 0
2022-01-06 12:00 | 1 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 21 | 22 | 28 | 29 | 31 | 39 | 24 | 25 | 0 | 0
2022-01-06 13:00 | 1 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 20 | 23 | 28 | 30 | 32 | 45 | 26 | 27 | 0 | 0
2022-01-06 14:00 | 1 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 21 | 23 | 29 | 30 | 32 | 46 | 27 | 29 | 0 | 0
2022-01-06 15:00 | 1 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 19 | 24 | 29 | 31 | 31 | 43 | 28 | 28 | 0 | 0
2022-01-06 16:00 | 1 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 18 | 23 | 28 | 29 | 30 | 41 | 26 | 28 | 0 | 0
2022-01-06 17:00 | 1 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 17 | 22 | 28 | 27 | 29 | 41 | 23 | 30 | 0 | 0
2022-01-06 18:00 | 1 | 4 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 17 | 21 | 27 | 25 | 28 | 43 | 22 | 29 | 0 | 0
2022-01-06 19:00 | 1 | 4 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 16 | 21 | 27 | 25 | 27 | 43 | 22 | 31 | 0 | 0
2022-01-06 20:00 | 1 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 14 | 22 | 26 | 26 | 26 | 41 | 21 | 31 | 0 | 0
2022-01-06 21:00 | 1 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 13 | 22 | 26 | 26 | 25 | 40 | 24 | 27 | 0 | 0
2022-01-06 22:00 | 1 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 13 | 22 | 28 | 25 | 25 | 43 | 25 | 26 | 0 | 0
2022-01-06 23:00 | 1 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 11 | 22 | 30 | 25 | 26 | 45 | 26 | 25 | 0 | 0
2022-01-07 | 1 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 11 | 22 | 32 | 24 | 25 | 45 | 25 | 24 | 0 | 0
2022-01-07 01:00 | 1 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 10 | 23 | 32 | 23 | 25 | 45 | 25 | 23 | 0 | 0
2022-01-07 02:00 | 1 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 9 | 23 | 33 | 23 | 24 | 43 | 25 | 24 | 0 | 0
2022-01-07 03:00 | 1 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 9 | 24 | 33 | 22 | 23 | 43 | 25 | 24 | 0 | 0
2022-01-07 04:00 | 1 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 8 | 25 | 34 | 23 | 27 | 40 | 26 | 24 | 0 | 0
2022-01-07 05:00 | 1 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 7 | 25 | 34 | 23 | 27 | 41 | 27 | 25 | 0 | 0
2022-01-07 06:00 | 1 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 7 | 26 | 35 | 24 | 27 | 40 | 28 | 26 | 0 | 0
2022-01-07 07:00 | 1 | 5 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 5 | 28 | 34 | 25 | 31 | 39 | 28 | 27 | 0 | 0
2022-01-07 08:00 | 1 | 5 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 8 | 29 | 32 | 26 | 32 | 38 | 28 | 28 | 0 | 0
2022-01-07 09:00 | 1 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 10 | 31 | 31 | 27 | 34 | 37 | 29 | 29 | 0 | 0
2022-01-07 10:00 | 1 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 12 | 30 | 31 | 29 | 35 | 36 | 31 | 30 | 0 | 0
2022-01-07 11:00 | 1 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 12 | 30 | 31 | 31 | 35 | 35 | 33 | 31 | 0 | 0
2022-01-07 12:00 | 1 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 11 | 29 | 31 | 33 | 35 | 35 | 34 | 41 | 0 | 0
2022-01-07 13:00 | 1 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 13 | 28 | 30 | 33 | 35 | 34 | 34 | 41 | 0 | 0
2022-01-07 14:00 | 1 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 11 | 28 | 29 | 32 | 35 | 34 | 35 | 40 | 0 | 0
2022-01-07 15:00 | 1 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 11 | 27 | 28 | 32 | 35 | 34 | 35 | 40 | 0 | 0
2022-01-07 16:00 | 1 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 9 | 25 | 28 | 32 | 35 | 34 | 33 | 39 | 0 | 0
2022-01-07 17:00 | 1 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 8 | 22 | 27 | 32 | 35 | 34 | 33 | 39 | 0 | 0
2022-01-07 18:00 | 1 | 5 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 8 | 20 | 27 | 32 | 35 | 34 | 32 | 39 | 0 | 0
2022-01-07 19:00 | 1 | 5 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 7 | 19 | 26 | 32 | 35 | 35 | 30 | 38 | 0 | 0
2022-01-07 20:00 | 1 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 7 | 18 | 26 | 32 | 35 | 35 | 32 | 37 | 0 | 0
2022-01-07 21:00 | 1 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 8 | 17 | 25 | 32 | 34 | 34 | 33 | 37 | 0 | 0
2022-01-07 22:00 | 1 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 8 | 16 | 24 | 32 | 34 | 32 | 32 | 37 | 0 | 0
2022-01-07 23:00 | 1 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 8 | 16 | 24 | 33 | 34 | 32 | 30 | 36 | 0 | 0
2022-01-08 | 1 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 7 | 15 | 23 | 33 | 35 | 33 | 29 | 34 | 0 | 0
2022-01-08 01:00 | 1 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 6 | 15 | 22 | 33 | 35 | 32 | 28 | 34 | 0 | 0
2022-01-08 02:00 | 1 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 5 | 14 | 22 | 34 | 35 | 32 | 27 | 33 | 0 | 0
2022-01-08 03:00 | 1 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 4 | 14 | 21 | 34 | 35 | 32 | 26 | 32 | 0 | 0
2022-01-08 04:00 | 1 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 4 | 14 | 21 | 33 | 34 | 31 | 25 | 32 | 0 | 0
2022-01-08 05:00 | 1 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 2 | 13 | 21 | 32 | 34 | 31 | 23 | 32 | 0 | 0
2022-01-08 06:00 | 1 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 2 | 13 | 21 | 31 | 35 | 31 | 23 | 32 | 0 | 0
2022-01-08 07:00 | 1 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 1 | 13 | 21 | 29 | 35 | 31 | 21 | 31 | 0 | 0
2022-01-08 08:00 | 1 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 2 | 13 | 20 | 27 | 35 | 32 | 23 | 31 | 0 | 0
2022-01-08 09:00 | 1 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 4 | 13 | 20 | 25 | 32 | 31 | 25 | 31 | 0 | 0
2022-01-08 10:00 | 1 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 6 | 14 | 20 | 25 | 30 | 31 | 27 | 33 | 0 | 0
2022-01-08 11:00 | 1 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 8 | 14 | 19 | 25 | 28 | 32 | 28 | 34 | 0 | 0
2022-01-08 12:00 | 1 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 10 | 15 | 19 | 25 | 27 | 32 | 29 | 34 | 0 | 0
2022-01-08 13:00 | 1 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 11 | 16 | 20 | 25 | 27 | 32 | 29 | 35 | 0 | 0
2022-01-08 14:00 | 1 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 13 | 18 | 21 | 25 | 28 | 33 | 30 | 35 | 0 | 0
2022-01-08 15:00 | 1 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 12 | 19 | 22 | 25 | 27 | 33 | 29 | 34 | 0 | 0
2022-01-08 16:00 | 1 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 11 | 18 | 22 | 24 | 25 | 33 | 27 | 33 | 0 | 0
2022-01-08 17:00 | 1 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 9 | 16 | 21 | 23 | 24 | 32 | 26 | 33 | 0 | 0
2022-01-08 18:00 | 1 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 9 | 15 | 21 | 22 | 23 | 33 | 26 | 32 | 0 | 0
2022-01-08 19:00 | 1 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 9 | 14 | 21 | 21 | 21 | 32 | 25 | 32 | 0 | 0
2022-01-08 20:00 | 1 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 9 | 13 | 20 | 21 | 19 | 32 | 23 | 33 | 0 | 0
2022-01-08 21:00 | 1 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 10 | 12 | 20 | 20 | 18 | 32 | 22 | 33 | 0 | 0
2022-01-08 22:00 | 1 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 10 | 11 | 19 | 19 | 18 | 32 | 22 | 33 | 0 | 0
2022-01-08 23:00 | 1 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 10 | 10 | 19 | 17 | 18 | 32 | 24 | 33 | 0 | 0
2022-01-09 | 1 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 11 | 9 | 18 | 16 | 17 | 32 | 21 | 33 | 0 | 0
2022-01-09 01:00 | 1 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 11 | 10 | 19 | 16 | 17 | 32 | 22 | 33 | 0 | 0
2022-01-09 02:00 | 1 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 11 | 10 | 19 | 15 | 17 | 31 | 22 | 34 | 0 | 0
2022-01-09 03:00 | 1 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 11 | 11 | 20 | 15 | 16 | 31 | 21 | 33 | 0 | 0
2022-01-09 04:00 | 1 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 13 | 11 | 20 | 14 | 15 | 32 | 21 | 33 | 0 | 0
2022-01-09 05:00 | 1 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 14 | 10 | 19 | 13 | 14 | 32 | 21 | 33 | 0 | 0
2022-01-09 06:00 | 1 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 15 | 10 | 19 | 12 | 14 | 30 | 22 | 33 | 0 | 0
2022-01-09 07:00 | 1 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 14 | 11 | 19 | 13 | 14 | 30 | 21 | 32 | 0 | 0
2022-01-09 08:00 | 1 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 16 | 12 | 19 | 15 | 17 | 30 | 23 | 33 | 0 | 0
2022-01-09 09:00 | 1 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 19 | 13 | 19 | 16 | 19 | 29 | 24 | 34 | 0 | 0
2022-01-09 10:00 | 1 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 22 | 15 | 20 | 17 | 21 | 30 | 25 | 34 | 0 | 0
2022-01-09 11:00 | 1 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 25 | 17 | 20 | 19 | 21 | 31 | 25 | 33 | 0 | 0
2022-01-09 12:00 | 1 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 28 | 19 | 21 | 20 | 22 | 32 | 25 | 34 | 0 | 0
2022-01-09 13:00 | 1 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 30 | 19 | 21 | 20 | 22 | 33 | 24 | 35 | 0 | 0
2022-01-09 14:00 | 1 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 31 | 20 | 21 | 21 | 23 | 33 | 26 | 35 | 0 | 0
2022-01-09 15:00 | 1 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 31 | 20 | 21 | 21 | 22 | 31 | 26 | 34 | 0 | 0
2022-01-09 16:00 | 1 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 32 | 18 | 21 | 20 | 21 | 31 | 25 | 34 | 0 | 0
2022-01-09 17:00 | 1 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 31 | 16 | 22 | 18 | 20 | 31 | 23 | 33 | 0 | 0
2022-01-09 18:00 | 1 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 32 | 14 | 22 | 17 | 19 | 31 | 22 | 32 | 0 | 0
2022-01-09 19:00 | 1 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 32 | 13 | 22 | 16 | 18 | 31 | 21 | 31 | 0 | 0
2022-01-09 20:00 | 1 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 32 | 12 | 22 | 16 | 17 | 32 | 22 | 33 | 0 | 0
2022-01-09 21:00 | 1 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 32 | 11 | 22 | 15 | 15 | 32 | 22 | 32 | 0 | 0
2022-01-09 22:00 | 1 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 32 | 11 | 22 | 15 | 14 | 32 | 21 | 32 | 0 | 0
2022-01-09 23:00 | 1 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 31 | 11 | 21 | 14 | 14 | 33 | 21 | 32 | 0 | 0
2022-01-10 | 1 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 31 | 11 | 21 | 14 | 14 | 34 | 18 | 32 | 0 | 0
2022-01-10 01:00 | 1 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 30 | 11 | 20 | 14 | 14 | 36 | 18 | 32 | 0 | 0
2022-01-10 02:00 | 1 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 9 | 30 | 11 | 19 | 13 | 15 | 35 | 17 | 33 | 0 | 0
2022-01-10 03:00 | 1 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 9 | 30 | 11 | 18 | 13 | 15 | 36 | 17 | 33 | 0 | 0
2022-01-10 04:00 | 1 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 30 | 8 | 17 | 13 | 13 | 38 | 16 | 31 | 0 | 0
2022-01-10 05:00 | 1 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 30 | 6 | 17 | 13 | 14 | 38 | 15 | 31 | 0 | 0
2022-01-10 06:00 | 1 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 30 | 3 | 16 | 13 | 14 | 38 | 13 | 31 | 0 | 0
2022-01-10 07:00 | 1 | 1 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 14 | 30 | 6 | 17 | 14 | 15 | 37 | 13 | 31 | 0 | 0
2022-01-10 08:00 | 1 | 1 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 16 | 30 | 9 | 18 | 14 | 18 | 38 | 15 | 31 | 0 | 0
2022-01-10 09:00 | 1 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 17 | 31 | 12 | 19 | 15 | 21 | 39 | 19 | 32 | 0 | 0
2022-01-10 10:00 | 1 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 32 | 15 | 23 | 17 | 23 | 38 | 23 | 33 | 0 | 0
2022-01-10 11:00 | 1 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 32 | 19 | 26 | 20 | 26 | 40 | 25 | 34 | 0 | 0
2022-01-10 12:00 | 1 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 31 | 22 | 30 | 22 | 26 | 40 | 27 | 35 | 0 | 0
2022-01-10 13:00 | 1 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 32 | 23 | 32 | 22 | 27 | 40 | 29 | 35 | 0 | 0
2022-01-10 14:00 | 1 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 32 | 24 | 34 | 23 | 26 | 38 | 31 | 34 | 0 | 0
2022-01-10 15:00 | 1 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 31 | 25 | 36 | 23 | 24 | 36 | 29 | 34 | 0 | 0
2022-01-10 16:00 | 1 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 30 | 24 | 36 | 23 | 22 | 35 | 28 | 34 | 0 | 0
2022-01-10 17:00 | 1 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 29 | 24 | 36 | 24 | 22 | 34 | 27 | 34 | 0 | 0
2022-01-10 18:00 | 1 | 1 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 28 | 23 | 36 | 24 | 22 | 32 | 27 | 33 | 0 | 0
2022-01-10 19:00 | 1 | 1 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 25 | 23 | 36 | 24 | 21 | 33 | 26 | 33 | 0 | 0
2022-01-10 20:00 | 1 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 24 | 24 | 37 | 24 | 21 | 33 | 27 | 33 | 0 | 0
2022-01-10 21:00 | 1 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 24 | 24 | 37 | 24 | 22 | 31 | 27 | 33 | 0 | 0
2022-01-10 22:00 | 1 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 23 | 24 | 38 | 24 | 24 | 32 | 28 | 33 | 0 | 0
2022-01-10 23:00 | 1 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 23 | 25 | 40 | 23 | 24 | 29 | 28 | 33 | 0 | 0
2022-01-11 | 1 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 23 | 25 | 41 | 23 | 24 | 29 | 28 | 34 | 0 | 0
2022-01-11 01:00 | 1 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 22 | 26 | 42 | 23 | 24 | 29 | 29 | 34 | 0 | 0
2022-01-11 02:00 | 1 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 20 | 27 | 42 | 23 | 24 | 29 | 30 | 33 | 0 | 0
2022-01-11 03:00 | 1 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 20 | 28 | 43 | 23 | 24 | 29 | 31 | 33 | 0 | 0
2022-01-11 04:00 | 1 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 20 | 29 | 43 | 23 | 23 | 29 | 31 | 33 | 0 | 0
2022-01-11 05:00 | 1 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 21 | 30 | 43 | 24 | 23 | 29 | 31 | 33 | 0 | 0
2022-01-11 06:00 | 1 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 20 | 31 | 43 | 24 | 23 | 29 | 34 | 33 | 0 | 0
2022-01-11 07:00 | 1 | 2 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 20 | 33 | 44 | 25 | 23 | 30 | 36 | 33 | 0 | 0
2022-01-11 08:00 | 1 | 2 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 21 | 36 | 46 | 25 | 23 | 32 | 38 | 33 | 0 | 0
2022-01-11 09:00 | 1 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 22 | 38 | 47 | 26 | 26 | 31 | 41 | 34 | 0 | 0
2022-01-11 10:00 | 1 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 23 | 39 | 49 | 26 | 32 | 32 | 43 | 34 | 0 | 0
2022-01-11 11:00 | 1 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 26 | 40 | 50 | 27 | 34 | 32 | 49 | 34 | 0 | 0
2022-01-11 12:00 | 1 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 28 | 41 | 52 | 27 | 36 | 32 | 49 | 35 | 0 | 0
2022-01-11 13:00 | 1 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 30 | 42 | 53 | 28 | 37 | 31 | 50 | 36 | 0 | 0
2022-01-11 14:00 | 1 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 31 | 43 | 53 | 29 | 35 | 30 | 51 | 36 | 0 | 0
2022-01-11 15:00 | 1 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 31 | 44 | 54 | 30 | 33 | 29 | 52 | 35 | 0 | 0
2022-01-11 16:00 | 1 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 29 | 45 | 48 | 30 | 33 | 29 | 52 | 34 | 0 | 0
2022-01-11 17:00 | 1 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 28 | 47 | 42 | 29 | 33 | 29 | 53 | 33 | 0 | 0
2022-01-11 18:00 | 1 | 2 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 29 | 48 | 36 | 29 | 32 | 30 | 54 | 33 | 0 | 0
2022-01-11 19:00 | 1 | 2 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 28 | 42 | 35 | 29 | 32 | 31 | 55 | 32 | 0 | 0
2022-01-11 20:00 | 1 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 28 | 36 | 33 | 28 | 32 | 30 | 53 | 32 | 0 | 0
2022-01-11 21:00 | 1 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 27 | 30 | 32 | 28 | 32 | 29 | 53 | 32 | 0 | 0
2022-01-11 22:00 | 1 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 27 | 27 | 30 | 28 | 32 | 29 | 53 | 32 | 0 | 0
2022-01-11 23:00 | 1 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 29 | 25 | 27 | 29 | 32 | 29 | 48 | 33 | 0 | 0
2022-01-12 | 1 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 30 | 22 | 25 | 29 | 32 | 29 | 43 | 33 | 0 | 0
2022-01-12 01:00 | 1 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 30 | 20 | 24 | 30 | 32 | 30 | 37 | 32 | 0 | 0
2022-01-12 02:00 | 1 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 31 | 19 | 22 | 32 | 31 | 29 | 35 | 32 | 0 | 0
2022-01-12 03:00 | 1 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 31 | 17 | 21 | 33 | 31 | 29 | 33 | 30 | 0 | 0
2022-01-12 04:00 | 1 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 32 | 15 | 20 | 33 | 32 | 29 | 32 | 31 | 0 | 0
2022-01-12 05:00 | 1 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 32 | 13 | 18 | 33 | 30 | 30 | 30 | 32 | 0 | 0
2022-01-12 06:00 | 1 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 33 | 11 | 17 | 33 | 29 | 28 | 29 | 32 | 0 | 0
2022-01-12 07:00 | 1 | 3 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 33 | 10 | 17 | 33 | 29 | 28 | 28 | 31 | 0 | 0
2022-01-12 08:00 | 1 | 3 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 35 | 10 | 17 | 33 | 31 | 28 | 27 | 31 | 0 | 0
2022-01-12 09:00 | 1 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 38 | 9 | 17 | 33 | 33 | 30 | 26 | 31 | 0 | 0
2022-01-12 10:00 | 1 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 39 | 10 | 18 | 34 | 33 | 29 | 28 | 31 | 0 | 0
2022-01-12 11:00 | 1 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 41 | 12 | 18 | 35 | 35 | 30 | 29 | 32 | 0 | 0
2022-01-12 12:00 | 1 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 42 | 13 | 19 | 36 | 35 | 30 | 29 | 33 | 0 | 0
2022-01-12 13:00 | 1 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 44 | 13 | 20 | 36 | 35 | 31 | 29 | 35 | 0 | 0
2022-01-12 14:00 | 1 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 44 | 13 | 20 | 35 | 36 | 31 | 28 | 35 | 0 | 0
2022-01-12 15:00 | 1 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 44 | 13 | 21 | 35 | 35 | 31 | 27 | 34 | 0 | 0
2022-01-12 16:00 | 1 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 42 | 13 | 21 | 33 | 33 | 32 | 26 | 34 | 0 | 0
2022-01-12 17:00 | 1 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 40 | 12 | 21 | 30 | 29 | 32 | 25 | 33 | 0 | 0
2022-01-12 18:00 | 1 | 3 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 39 | 12 | 21 | 28 | 28 | 32 | 24 | 34 | 0 | 0
2022-01-12 19:00 | 1 | 3 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 39 | 12 | 21 | 27 | 26 | 31 | 23 | 35 | 0 | 0
2022-01-12 20:00 | 1 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 39 | 11 | 20 | 27 | 27 | 32 | 22 | 35 | 0 | 0
2022-01-12 21:00 | 1 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 38 | 11 | 20 | 26 | 26 | 31 | 21 | 37 | 0 | 0
2022-01-12 22:00 | 1 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 36 | 9 | 19 | 25 | 27 | 31 | 20 | 37 | 0 | 0
2022-01-12 23:00 | 1 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 35 | 6 | 18 | 24 | 24 | 32 | 20 | 36 | 0 | 0
2022-01-13 | 1 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 35 | 4 | 17 | 23 | 25 | 32 | 19 | 36 | 0 | 0
2022-01-13 01:00 | 1 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 34 | 5 | 17 | 23 | 25 | 32 | 17 | 36 | 0 | 0
2022-01-13 02:00 | 1 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 33 | 7 | 18 | 24 | 25 | 32 | 17 | 35 | 0 | 0
2022-01-13 03:00 | 1 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 33 | 8 | 18 | 24 | 23 | 32 | 16 | 35 | 0 | 0
2022-01-13 04:00 | 1 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 32 | 8 | 18 | 24 | 24 | 32 | 14 | 35 | 0 | 0
2022-01-13 05:00 | 1 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 32 | 7 | 19 | 24 | 20 | 32 | 14 | 35 | 0 | 0
2022-01-13 06:00 | 1 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 30 | 7 | 19 | 24 | 24 | 32 | 15 | 36 | 0 | 0
2022-01-13 07:00 | 1 | 4 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 15 | 29 | 10 | 21 | 25 | 24 | 32 | 14 | 37 | 0 | 0
2022-01-13 08:00 | 1 | 4 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 18 | 28 | 12 | 22 | 27 | 27 | 33 | 17 | 37 | 0 | 0
2022-01-13 09:00 | 1 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 27 | 15 | 24 | 28 | 33 | 33 | 19 | 38 | 0 | 0
2022-01-13 10:00 | 1 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 26 | 18 | 27 | 31 | 37 | 34 | 21 | 40 | 0 | 0
2022-01-13 11:00 | 1 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 26 | 20 | 30 | 33 | 42 | 37 | 23 | 40 | 0 | 0
2022-01-13 12:00 | 1 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 25 | 23 | 33 | 36 | 44 | 40 | 25 | 41 | 0 | 0
2022-01-13 13:00 | 1 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 21 | 25 | 35 | 36 | 44 | 38 | 28 | 41 | 0 | 0
2022-01-13 14:00 | 1 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 17 | 27 | 38 | 37 | 45 | 40 | 32 | 42 | 0 | 0
2022-01-13 15:00 | 1 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 15 | 29 | 40 | 37 | 44 | 42 | 31 | 42 | 0 | 0
2022-01-13 16:00 | 1 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 12 | 28 | 39 | 38 | 44 | 40 | 29 | 40 | 0 | 0
2022-01-13 17:00 | 1 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 10 | 26 | 37 | 40 | 44 | 36 | 28 | 37 | 0 | 0
2022-01-13 18:00 | 1 | 4 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 9 | 25 | 36 | 41 | 44 | 36 | 28 | 35 | 0 | 0
2022-01-13 19:00 | 1 | 4 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 9 | 25 | 36 | 43 | 44 | 35 | 29 | 33 | 0 | 0
2022-01-13 20:00 | 1 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 9 | 25 | 35 | 44 | 45 | 34 | 31 | 30 | 0 | 0
2022-01-13 21:00 | 1 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 8 | 25 | 35 | 46 | 47 | 32 | 32 | 28 | 0 | 0
2022-01-13 22:00 | 1 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 7 | 25 | 36 | 46 | 50 | 32 | 33 | 30 | 0 | 0
2022-01-13 23:00 | 1 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 6 | 26 | 36 | 47 | 51 | 32 | 33 | 26 | 0 | 0
2022-01-14 | 1 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 4 | 26 | 37 | 47 | 51 | 32 | 33 | 25 | 0 | 0
2022-01-14 01:00 | 1 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 2 | 27 | 37 | 45 | 50 | 31 | 34 | 22 | 0 | 0
2022-01-14 02:00 | 1 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 2 | 27 | 37 | 43 | 48 | 30 | 35 | 23 | 0 | 0
2022-01-14 03:00 | 1 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 1 | 28 | 37 | 41 | 49 | 31 | 36 | 22 | 0 | 0
2022-01-14 04:00 | 1 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | -1 | 29 | 37 | 41 | 42 | 35 | 39 | 22 | 0 | 0
2022-01-14 05:00 | 1 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 0 | 29 | 36 | 40 | 40 | 38 | 40 | 21 | 0 | 0
2022-01-14 06:00 | 1 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 0 | 30 | 36 | 40 | 39 | 38 | 41 | 20 | 0 | 0
2022-01-14 07:00 | 1 | 5 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | -1 | 30 | 36 | 39 | 39 | 38 | 43 | 20 | 0 | 0
2022-01-14 08:00 | 1 | 5 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 0 | 31 | 37 | 38 | 41 | 41 | 43 | 22 | 0 | 0
2022-01-14 09:00 | 1 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 3 | 31 | 37 | 37 | 42 | 45 | 44 | 26 | 0 | 0
2022-01-14 10:00 | 1 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 5 | 32 | 38 | 38 | 41 | 48 | 46 | 30 | 0 | 0
2022-01-14 11:00 | 1 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 6 | 32 | 39 | 39 | 42 | 51 | 47 | 32 | 0 | 0
2022-01-14 12:00 | 1 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 7 | 33 | 40 | 40 | 42 | 52 | 48 | 36 | 0 | 0
2022-01-14 13:00 | 1 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 8 | 33 | 39 | 40 | 42 | 53 | 44 | 38 | 0 | 0
2022-01-14 14:00 | 1 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 8 | 34 | 37 | 40 | 41 | 52 | 41 | 38 | 0 | 0
2022-01-14 15:00 | 1 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 8 | 34 | 36 | 40 | 40 | 51 | 39 | 39 | 0 | 0
2022-01-14 16:00 | 1 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 6 | 34 | 35 | 38 | 38 | 51 | 39 | 39 | 0 | 0
2022-01-14 17:00 | 1 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 5 | 34 | 35 | 36 | 36 | 47 | 39 | 38 | 0 | 0
2022-01-14 18:00 | 1 | 5 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 3 | 34 | 34 | 34 | 34 | 47 | 39 | 37 | 0 | 0
2022-01-14 19:00 | 1 | 5 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 2 | 34 | 34 | 33 | 35 | 47 | 39 | 36 | 0 | 0
2022-01-14 20:00 | 1 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 0 | 33 | 33 | 33 | 31 | 47 | 39 | 35 | 0 | 0
2022-01-14 21:00 | 1 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | -1 | 33 | 33 | 32 | 32 | 47 | 39 | 35 | 0 | 0
2022-01-14 22:00 | 1 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | -2 | 33 | 33 | 31 | 32 | 47 | 39 | 35 | 0 | 0
2022-01-14 23:00 | 1 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | -4 | 32 | 34 | 30 | 31 | 45 | 39 | 35 | 0 | 0
2022-01-15 | 1 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | -4 | 32 | 34 | 29 | 30 | 45 | 40 | 35 | 0 | 0
2022-01-15 01:00 | 1 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | -4 | 31 | 34 | 29 | 31 | 46 | 40 | 35 | 0 | 0
2022-01-15 02:00 | 1 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | -6 | 31 | 34 | 29 | 30 | 46 | 40 | 34 | 0 | 0
2022-01-15 03:00 | 1 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | -7 | 30 | 34 | 29 | 29 | 46 | 40 | 34 | 0 | 0
2022-01-15 04:00 | 1 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | -6 | 30 | 34 | 29 | 29 | 46 | 40 | 34 | 0 | 0
2022-01-15 05:00 | 1 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | -7 | 29 | 34 | 29 | 29 | 46 | 39 | 34 | 0 | 0
2022-01-15 06:00 | 1 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | -6 | 29 | 34 | 29 | 30 | 46 | 39 | 34 | 0 | 0
2022-01-15 07:00 | 1 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | -6 | 29 | 34 | 29 | 30 | 47 | 40 | 34 | 0 | 0
2022-01-15 08:00 | 1 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | -4 | 29 | 35 | 30 | 31 | 45 | 40 | 35 | 0 | 0
2022-01-15 09:00 | 1 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 0 | 29 | 35 | 30 | 33 | 46 | 40 | 36 | 0 | 0
2022-01-15 10:00 | 1 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 3 | 31 | 37 | 31 | 34 | 45 | 40 | 37 | 0 | 0
2022-01-15 11:00 | 1 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 6 | 33 | 38 | 33 | 35 | 46 | 40 | 38 | 0 | 0
2022-01-15 12:00 | 1 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 7 | 35 | 40 | 34 | 35 | 45 | 40 | 38 | 0 | 0
2022-01-15 13:00 | 1 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 10 | 37 | 40 | 34 | 35 | 45 | 40 | 39 | 0 | 0
2022-01-15 14:00 | 1 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 10 | 38 | 40 | 34 | 35 | 46 | 43 | 39 | 0 | 0
2022-01-15 15:00 | 1 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 11 | 40 | 40 | 34 | 33 | 45 | 44 | 44 | 0 | 0
2022-01-15 16:00 | 1 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 9 | 37 | 38 | 34 | 32 | 43 | 42 | 44 | 0 | 0
2022-01-15 17:00 | 1 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 9 | 33 | 36 | 33 | 31 | 42 | 38 | 44 | 0 | 0
2022-01-15 18:00 | 1 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 8 | 30 | 34 | 33 | 32 | 41 | 36 | 40 | 0 | 0
2022-01-15 19:00 | 1 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 10 | 29 | 33 | 32 | 32 | 39 | 35 | 42 | 0 | 0
2022-01-15 20:00 | 1 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 10 | 29 | 33 | 32 | 30 | 39 | 34 | 42 | 0 | 0
2022-01-15 21:00 | 1 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 11 | 28 | 32 | 31 | 29 | 36 | 32 | 41 | 0 | 0
2022-01-15 22:00 | 1 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 11 | 28 | 30 | 31 | 28 | 34 | 30 | 42 | 0 | 0
2022-01-15 23:00 | 1 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 12 | 27 | 28 | 31 | 30 | 34 | 31 | 40 | 0 | 0
2022-01-16 | 1 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 12 | 27 | 26 | 31 | 29 | 33 | 30 | 38 | 0 | 0
2022-01-16 01:00 | 1 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 13 | 25 | 25 | 30 | 28 | 33 | 30 | 38 | 0 | 0
2022-01-16 02:00 | 1 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 14 | 24 | 25 | 30 | 27 | 32 | 29 | 38 | 0 | 0
2022-01-16 03:00 | 1 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 14 | 22 | 24 | 29 | 29 | 31 | 27 | 37 | 0 | 0
2022-01-16 04:00 | 1 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 15 | 21 | 25 | 29 | 29 | 31 | 27 | 37 | 0 | 0
2022-01-16 05:00 | 1 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 15 | 20 | 26 | 30 | 29 | 31 | 28 | 37 | 0 | 0
2022-01-16 06:00 | 1 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 15 | 19 | 27 | 30 | 34 | 32 | 28 | 36 | 0 | 0
2022-01-16 07:00 | 1 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 16 | 22 | 32 | 30 | 34 | 29 | 26 | 35 | 0 | 0
2022-01-16 08:00 | 1 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 17 | 26 | 38 | 31 | 37 | 29 | 28 | 35 | 0 | 0
2022-01-16 09:00 | 1 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 18 | 29 | 43 | 31 | 39 | 32 | 30 | 35 | 0 | 0
2022-01-16 10:00 | 1 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 20 | 34 | 45 | 33 | 38 | 29 | 31 | 35 | 0 | 0
2022-01-16 11:00 | 1 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 21 | 39 | 48 | 35 | 38 | 32 | 35 | 35 | 0 | 0
2022-01-16 12:00 | 1 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 23 | 44 | 50 | 37 | 40 | 30 | 37 | 34 | 0 | 0
2022-01-16 13:00 | 1 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 24 | 44 | 50 | 39 | 41 | 32 | 40 | 33 | 0 | 0
2022-01-16 14:00 | 1 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 25 | 44 | 50 | 40 | 41 | 33 | 43 | 33 | 0 | 0
2022-01-16 15:00 | 1 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 26 | 44 | 50 | 42 | 41 | 33 | 44 | 31 | 0 | 0
2022-01-16 16:00 | 1 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 24 | 42 | 49 | 40 | 37 | 32 | 41 | 31 | 0 | 0
2022-01-16 17:00 | 1 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 22 | 40 | 48 | 38 | 37 | 30 | 37 | 29 | 0 | 0
2022-01-16 18:00 | 1 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 21 | 38 | 47 | 36 | 34 | 29 | 37 | 27 | 0 | 0
2022-01-16 19:00 | 1 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 23 | 39 | 47 | 36 | 32 | 28 | 34 | 26 | 0 | 0
2022-01-16 20:00 | 1 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 22 | 39 | 46 | 35 | 33 | 28 | 35 | 24 | 0 | 0
2022-01-16 21:00 | 1 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 23 | 40 | 46 | 35 | 32 | 28 | 36 | 23 | 0 | 0
2022-01-16 22:00 | 1 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 24 | 39 | 46 | 34 | 32 | 27 | 37 | 22 | 0 | 0
2022-01-16 23:00 | 1 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 24 | 38 | 45 | 34 | 31 | 24 | 37 | 19 | 0 | 0
2022-01-17 | 1 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 25 | 37 | 45 | 33 | 29 | 23 | 37 | 19 | 0 | 0
2022-01-17 01:00 | 1 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 24 | 36 | 45 | 31 | 36 | 22 | 37 | 18 | 0 | 0
2022-01-17 02:00 | 1 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 26 | 36 | 45 | 28 | 34 | 22 | 36 | 18 | 0 | 0
2022-01-17 03:00 | 1 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 25 | 35 | 45 | 26 | 32 | 21 | 36 | 17 | 0 | 0
2022-01-17 04:00 | 1 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 27 | 35 | 45 | 26 | 30 | 21 | 35 | 16 | 0 | 0
2022-01-17 05:00 | 1 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 26 | 34 | 45 | 25 | 28 | 20 | 34 | 14 | 0 | 0
2022-01-17 06:00 | 1 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 26 | 34 | 45 | 25 | 27 | 21 | 34 | 15 | 0 | 0
2022-01-17 07:00 | 1 | 1 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 18 | 27 | 34 | 44 | 23 | 24 | 21 | 33 | 14 | 0 | 0
2022-01-17 08:00 | 1 | 1 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 30 | 35 | 44 | 22 | 23 | 23 | 35 | 17 | 0 | 0
2022-01-17 09:00 | 1 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 33 | 35 | 43 | 20 | 22 | 25 | 38 | 21 | 0 | 0
2022-01-17 10:00 | 1 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 36 | 35 | 44 | 21 | 22 | 30 | 40 | 24 | 0 | 0
2022-01-17 11:00 | 1 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 39 | 36 | 44 | 23 | 24 | 31 | 42 | 26 | 0 | 0
2022-01-17 12:00 | 1 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 41 | 36 | 45 | 24 | 24 | 35 | 42 | 30 | 0 | 0
2022-01-17 13:00 | 1 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 42 | 35 | 46 | 23 | 25 | 36 | 43 | 28 | 0 | 0
2022-01-17 14:00 | 1 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 43 | 34 | 48 | 23 | 24 | 37 | 44 | 30 | 0 | 0
2022-01-17 15:00 | 1 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 42 | 33 | 49 | 22 | 23 | 36 | 44 | 29 | 0 | 0
2022-01-17 16:00 | 1 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 17 | 41 | 33 | 46 | 21 | 21 | 37 | 41 | 27 | 0 | 0
2022-01-17 17:00 | 1 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 15 | 41 | 33 | 44 | 21 | 20 | 36 | 40 | 26 | 0 | 0
2022-01-17 18:00 | 1 | 1 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 41 | 33 | 41 | 20 | 18 | 34 | 38 | 25 | 0 | 0
2022-01-17 19:00 | 1 | 1 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 41 | 34 | 41 | 19 | 17 | 35 | 38 | 23 | 0 | 0
2022-01-17 20:00 | 1 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 43 | 34 | 40 | 17 | 15 | 34 | 38 | 23 | 0 | 0
2022-01-17 21:00 | 1 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 42 | 35 | 40 | 16 | 13 | 34 | 38 | 23 | 0 | 0
2022-01-17 22:00 | 1 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 9 | 42 | 36 | 40 | 15 | 12 | 34 | 38 | 23 | 0 | 0
2022-01-17 23:00 | 1 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 8 | 43 | 36 | 39 | 14 | 12 | 33 | 38 | 24 | 0 | 0
2022-01-18 | 1 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 7 | 43 | 37 | 39 | 13 | 11 | 33 | 38 | 26 | 0 | 0
2022-01-18 01:00 | 1 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 7 | 42 | 37 | 38 | 12 | 11 | 32 | 38 | 27 | 0 | 0
2022-01-18 02:00 | 1 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 6 | 42 | 36 | 38 | 12 | 10 | 33 | 38 | 28 | 0 | 0
2022-01-18 03:00 | 1 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 6 | 41 | 36 | 37 | 11 | 10 | 34 | 38 | 29 | 0 | 0
2022-01-18 04:00 | 1 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 5 | 40 | 36 | 36 | 11 | 9 | 34 | 38 | 29 | 0 | 0
2022-01-18 05:00 | 1 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 4 | 40 | 36 | 36 | 10 | 9 | 35 | 38 | 29 | 0 | 0
2022-01-18 06:00 | 1 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 3 | 41 | 36 | 35 | 10 | 8 | 35 | 38 | 29 | 0 | 0
2022-01-18 07:00 | 1 | 2 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 5 | 40 | 35 | 35 | 10 | 9 | 36 | 38 | 29 | 0 | 0
2022-01-18 08:00 | 1 | 2 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 7 | 40 | 35 | 35 | 11 | 10 | 38 | 38 | 26 | 0 | 0
2022-01-18 09:00 | 1 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 9 | 41 | 34 | 35 | 11 | 12 | 39 | 39 | 26 | 0 | 0
2022-01-18 10:00 | 1 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 11 | 45 | 33 | 35 | 13 | 14 | 42 | 39 | 27 | 0 | 0
2022-01-18 11:00 | 1 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 13 | 47 | 33 | 34 | 15 | 15 | 44 | 39 | 27 | 0 | 0
2022-01-18 12:00 | 1 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 15 | 49 | 32 | 34 | 17 | 17 | 45 | 39 | 28 | 0 | 0
2022-01-18 13:00 | 1 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 16 | 48 | 32 | 34 | 17 | 18 | 44 | 40 | 29 | 0 | 0
2022-01-18 14:00 | 1 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 16 | 48 | 31 | 34 | 18 | 19 | 40 | 40 | 29 | 0 | 0
2022-01-18 15:00 | 1 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 17 | 48 | 31 | 34 | 18 | 18 | 39 | 40 | 30 | 0 | 0
2022-01-18 16:00 | 1 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 15 | 46 | 30 | 34 | 18 | 17 | 38 | 40 | 30 | 0 | 0
2022-01-18 17:00 | 1 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 12 | 46 | 30 | 34 | 17 | 16 | 37 | 39 | 30 | 0 | 0
2022-01-18 18:00 | 1 | 2 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 44 | 29 | 34 | 17 | 14 | 36 | 39 | 30 | 0 | 0
2022-01-18 19:00 | 1 | 2 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 9 | 45 | 29 | 34 | 16 | 14 | 35 | 39 | 30 | 0 | 0
2022-01-18 20:00 | 1 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 9 | 44 | 29 | 34 | 16 | 13 | 35 | 39 | 31 | 0 | 0
2022-01-18 21:00 | 1 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 8 | 45 | 29 | 34 | 15 | 13 | 34 | 39 | 31 | 0 | 0
2022-01-18 22:00 | 1 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 7 | 45 | 29 | 34 | 14 | 12 | 33 | 38 | 31 | 0 | 0
2022-01-18 23:00 | 1 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 6 | 46 | 28 | 34 | 14 | 11 | 33 | 36 | 32 | 0 | 0
2022-01-19 | 1 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 5 | 46 | 28 | 34 | 13 | 11 | 33 | 36 | 32 | 0 | 0
2022-01-19 01:00 | 1 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 4 | 46 | 28 | 34 | 12 | 10 | 32 | 37 | 32 | 0 | 0
2022-01-19 02:00 | 1 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 4 | 46 | 27 | 34 | 11 | 10 | 32 | 36 | 32 | 0 | 0
2022-01-19 03:00 | 1 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 3 | 46 | 27 | 34 | 10 | 9 | 32 | 36 | 34 | 0 | 0
2022-01-19 04:00 | 1 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 3 | 46 | 27 | 34 | 10 | 8 | 32 | 36 | 33 | 0 | 0
2022-01-19 05:00 | 1 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 4 | 47 | 26 | 33 | 9 | 8 | 32 | 36 | 33 | 0 | 0
2022-01-19 06:00 | 1 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 4 | 47 | 26 | 33 | 9 | 8 | 32 | 36 | 32 | 0 | 0
2022-01-19 07:00 | 1 | 3 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 6 | 47 | 26 | 33 | 10 | 9 | 31 | 35 | 32 | 0 | 0
2022-01-19 08:00 | 1 | 3 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 9 | 46 | 26 | 33 | 12 | 12 | 31 | 36 | 32 | 0 | 0
2022-01-19 09:00 | 1 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 11 | 47 | 26 | 33 | 13 | 15 | 34 | 36 | 30 | 0 | 0
2022-01-19 10:00 | 1 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 15 | 47 | 26 | 33 | 17 | 17 | 34 | 36 | 29 | 0 | 0
2022-01-19 11:00 | 1 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 18 | 49 | 26 | 33 | 21 | 21 | 36 | 36 | 29 | 0 | 0
2022-01-19 12:00 | 1 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 49 | 26 | 33 | 25 | 22 | 39 | 36 | 28 | 0 | 0
2022-01-19 13:00 | 1 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 48 | 26 | 33 | 26 | 24 | 40 | 36 | 28 | 0 | 0
2022-01-19 14:00 | 1 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 48 | 26 | 33 | 27 | 25 | 39 | 37 | 28 | 0 | 0
2022-01-19 15:00 | 1 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 48 | 26 | 33 | 28 | 26 | 40 | 37 | 29 | 0 | 0
2022-01-19 16:00 | 1 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 47 | 26 | 33 | 27 | 24 | 40 | 36 | 29 | 0 | 0
2022-01-19 17:00 | 1 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 48 | 26 | 32 | 25 | 22 | 37 | 36 | 29 | 0 | 0
2022-01-19 18:00 | 1 | 3 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 47 | 26 | 32 | 24 | 22 | 36 | 35 | 29 | 0 | 0
2022-01-19 19:00 | 1 | 3 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 48 | 26 | 32 | 23 | 21 | 34 | 35 | 28 | 0 | 0
2022-01-19 20:00 | 1 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 47 | 25 | 31 | 23 | 21 | 34 | 35 | 29 | 0 | 0
2022-01-19 21:00 | 1 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 48 | 25 | 31 | 22 | 20 | 33 | 35 | 29 | 0 | 0
2022-01-19 22:00 | 1 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 48 | 25 | 31 | 23 | 20 | 31 | 34 | 30 | 0 | 0
2022-01-19 23:00 | 1 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 48 | 24 | 32 | 24 | 21 | 29 | 34 | 30 | 0 | 0
2022-01-20 | 1 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 48 | 24 | 32 | 25 | 21 | 28 | 34 | 29 | 0 | 0
2022-01-20 01:00 | 1 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 47 | 24 | 32 | 26 | 20 | 28 | 34 | 29 | 0 | 0
2022-01-20 02:00 | 1 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 47 | 24 | 32 | 27 | 25 | 27 | 34 | 29 | 0 | 0
2022-01-20 03:00 | 1 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 46 | 24 | 32 | 28 | 26 | 27 | 34 | 28 | 0 | 0
2022-01-20 04:00 | 1 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 45 | 24 | 31 | 28 | 27 | 27 | 34 | 28 | 0 | 0
2022-01-20 05:00 | 1 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 45 | 24 | 31 | 28 | 27 | 28 | 34 | 28 | 0 | 0
2022-01-20 06:00 | 1 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 45 | 24 | 30 | 28 | 27 | 28 | 34 | 28 | 0 | 0
2022-01-20 07:00 | 1 | 4 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 44 | 24 | 30 | 28 | 28 | 28 | 34 | 27 | 0 | 0
2022-01-20 08:00 | 1 | 4 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 46 | 23 | 29 | 29 | 28 | 28 | 34 | 28 | 0 | 0
2022-01-20 09:00 | 1 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 47 | 23 | 29 | 29 | 28 | 28 | 34 | 28 | 0 | 0
2022-01-20 10:00 | 1 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 48 | 23 | 29 | 30 | 27 | 28 | 33 | 30 | 0 | 0
2022-01-20 11:00 | 1 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 47 | 23 | 30 | 30 | 27 | 28 | 34 | 31 | 0 | 0
2022-01-20 12:00 | 1 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 37 | 23 | 30 | 31 | 27 | 30 | 35 | 30 | 0 | 0
2022-01-20 13:00 | 1 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 36 | 23 | 29 | 32 | 28 | 29 | 35 | 31 | 0 | 0
2022-01-20 14:00 | 1 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 35 | 23 | 29 | 32 | 28 | 30 | 34 | 32 | 0 | 0
2022-01-20 15:00 | 1 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 34 | 23 | 28 | 33 | 28 | 30 | 34 | 32 | 0 | 0
2022-01-20 16:00 | 1 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 33 | 22 | 28 | 32 | 28 | 30 | 33 | 31 | 0 | 0
2022-01-20 17:00 | 1 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 31 | 21 | 28 | 31 | 28 | 29 | 31 | 31 | 0 | 0
2022-01-20 18:00 | 1 | 4 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 31 | 20 | 28 | 30 | 27 | 28 | 30 | 31 | 0 | 0
2022-01-20 19:00 | 1 | 4 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 30 | 20 | 28 | 30 | 27 | 28 | 29 | 30 | 0 | 0
2022-01-20 20:00 | 1 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 29 | 20 | 28 | 30 | 27 | 26 | 27 | 30 | 0 | 0
2022-01-20 21:00 | 1 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 29 | 20 | 28 | 30 | 27 | 27 | 26 | 29 | 0 | 0
2022-01-20 22:00 | 1 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 28 | 20 | 28 | 30 | 27 | 28 | 26 | 27 | 0 | 0
2022-01-20 23:00 | 1 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 28 | 19 | 29 | 30 | 27 | 29 | 26 | 21 | 0 | 0
2022-01-21 | 1 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 28 | 19 | 29 | 30 | 26 | 29 | 26 | 19 | 0 | 0
2022-01-21 01:00 | 1 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 29 | 19 | 29 | 30 | 26 | 29 | 26 | 19 | 0 | 0
2022-01-21 02:00 | 1 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 29 | 19 | 29 | 30 | 26 | 29 | 27 | 20 | 0 | 0
2022-01-21 03:00 | 1 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 29 | 19 | 29 | 30 | 26 | 27 | 27 | 21 | 0 | 0
2022-01-21 04:00 | 1 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 29 | 19 | 29 | 30 | 26 | 26 | 27 | 22 | 0 | 0
2022-01-21 05:00 | 1 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 30 | 19 | 28 | 30 | 26 | 24 | 27 | 22 | 0 | 0
2022-01-21 06:00 | 1 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 29 | 19 | 28 | 30 | 26 | 23 | 27 | 23 | 0 | 0
2022-01-21 07:00 | 1 | 5 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 30 | 19 | 29 | 31 | 26 | 21 | 28 | 20 | 0 | 0
2022-01-21 08:00 | 1 | 5 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 30 | 20 | 29 | 31 | 28 | 22 | 29 | 23 | 0 | 0
2022-01-21 09:00 | 1 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 30 | 20 | 30 | 32 | 30 | 25 | 29 | 30 | 0 | 0
2022-01-21 10:00 | 1 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 31 | 21 | 30 | 32 | 30 | 26 | 29 | 30 | 0 | 0
2022-01-21 11:00 | 1 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 32 | 23 | 31 | 32 | 31 | 27 | 31 | 30 | 0 | 0
2022-01-21 12:00 | 1 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 33 | 24 | 31 | 32 | 32 | 28 | 34 | 31 | 0 | 0
2022-01-21 13:00 | 1 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 36 | 24 | 31 | 32 | 33 | 29 | 35 | 29 | 0 | 0
2022-01-21 14:00 | 1 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 37 | 24 | 32 | 32 | 39 | 31 | 35 | 30 | 0 | 0
2022-01-21 15:00 | 1 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 37 | 24 | 32 | 32 | 32 | 32 | 33 | 30 | 0 | 0
2022-01-21 16:00 | 1 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 36 | 22 | 30 | 32 | 32 | 30 | 32 | 27 | 0 | 0
2022-01-21 17:00 | 1 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 34 | 21 | 28 | 31 | 31 | 27 | 31 | 26 | 0 | 0
2022-01-21 18:00 | 1 | 5 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 32 | 19 | 26 | 31 | 31 | 26 | 31 | 22 | 0 | 0
2022-01-21 19:00 | 1 | 5 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 31 | 18 | 26 | 30 | 31 | 26 | 30 | 20 | 0 | 0
2022-01-21 20:00 | 1 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 29 | 16 | 27 | 28 | 29 | 26 | 29 | 18 | 0 | 0
2022-01-21 21:00 | 1 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 29 | 15 | 27 | 27 | 28 | 25 | 27 | 15 | 0 | 0
2022-01-21 22:00 | 1 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 29 | 17 | 28 | 27 | 27 | 25 | 27 | 15 | 0 | 0
2022-01-21 23:00 | 1 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 29 | 18 | 30 | 27 | 26 | 26 | 24 | 16 | 0 | 0
2022-01-22 | 1 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 31 | 20 | 31 | 27 | 25 | 25 | 23 | 15 | 0 | 0
2022-01-22 01:00 | 1 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 31 | 21 | 31 | 27 | 24 | 25 | 22 | 16 | 0 | 0
2022-01-22 02:00 | 1 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 31 | 21 | 31 | 26 | 24 | 25 | 25 | 15 | 0 | 0
2022-01-22 03:00 | 1 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 33 | 22 | 31 | 26 | 24 | 26 | 24 | 14 | 0 | 0
2022-01-22 04:00 | 1 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 34 | 22 | 31 | 26 | 24 | 26 | 27 | 15 | 0 | 0
2022-01-22 05:00 | 1 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 35 | 22 | 31 | 25 | 23 | 26 | 26 | 17 | 0 | 0
2022-01-22 06:00 | 1 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 35 | 22 | 31 | 25 | 22 | 26 | 25 | 18 | 0 | 0
2022-01-22 07:00 | 1 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 36 | 24 | 32 | 25 | 24 | 27 | 27 | 22 | 0 | 0
2022-01-22 08:00 | 1 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 39 | 25 | 32 | 26 | 25 | 28 | 30 | 22 | 0 | 0
2022-01-22 09:00 | 1 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 41 | 27 | 33 | 26 | 26 | 28 | 32 | 21 | 0 | 0
2022-01-22 10:00 | 1 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 43 | 27 | 33 | 25 | 28 | 28 | 33 | 21 | 0 | 0
2022-01-22 11:00 | 1 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 45 | 28 | 33 | 24 | 28 | 28 | 36 | 22 | 0 | 0
2022-01-22 12:00 | 1 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 48 | 28 | 33 | 23 | 29 | 28 | 37 | 22 | 0 | 0
2022-01-22 13:00 | 1 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 48 | 28 | 33 | 23 | 27 | 28 | 35 | 23 | 0 | 0
2022-01-22 14:00 | 1 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 47 | 28 | 32 | 22 | 26 | 30 | 35 | 24 | 0 | 0
2022-01-22 15:00 | 1 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 39 | 28 | 32 | 22 | 24 | 28 | 35 | 24 | 0 | 0
2022-01-22 16:00 | 1 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 39 | 28 | 32 | 21 | 22 | 28 | 35 | 24 | 0 | 0
2022-01-22 17:00 | 1 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 37 | 27 | 31 | 20 | 20 | 27 | 34 | 24 | 0 | 0
2022-01-22 18:00 | 1 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 36 | 27 | 31 | 19 | 19 | 27 | 34 | 24 | 0 | 0
2022-01-22 19:00 | 1 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 33 | 27 | 31 | 18 | 18 | 27 | 34 | 24 | 0 | 0
2022-01-22 20:00 | 1 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 31 | 26 | 32 | 17 | 16 | 26 | 34 | 24 | 0 | 0
2022-01-22 21:00 | 1 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 30 | 26 | 32 | 16 | 15 | 25 | 34 | 24 | 0 | 0
2022-01-22 22:00 | 1 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 9 | 28 | 26 | 31 | 15 | 14 | 26 | 35 | 24 | 0 | 0
2022-01-22 23:00 | 1 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 8 | 28 | 26 | 30 | 14 | 12 | 26 | 34 | 25 | 0 | 0
2022-01-23 | 1 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 7 | 27 | 26 | 29 | 13 | 11 | 26 | 35 | 25 | 0 | 0
2022-01-23 01:00 | 1 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 6 | 26 | 26 | 28 | 12 | 10 | 26 | 35 | 26 | 0 | 0
2022-01-23 02:00 | 1 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 5 | 25 | 25 | 28 | 12 | 9 | 27 | 34 | 26 | 0 | 0
2022-01-23 03:00 | 1 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 4 | 24 | 25 | 27 | 11 | 9 | 24 | 34 | 26 | 0 | 0
2022-01-23 04:00 | 1 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 3 | 23 | 24 | 25 | 11 | 8 | 22 | 34 | 27 | 0 | 0
2022-01-23 05:00 | 1 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 3 | 23 | 23 | 24 | 11 | 7 | 21 | 34 | 27 | 0 | 0
2022-01-23 06:00 | 1 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 2 | 20 | 22 | 22 | 11 | 7 | 19 | 34 | 28 | 0 | 0
2022-01-23 07:00 | 1 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 3 | 19 | 20 | 21 | 11 | 8 | 18 | 32 | 28 | 0 | 0
2022-01-23 08:00 | 1 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 4 | 21 | 17 | 20 | 11 | 10 | 17 | 34 | 28 | 0 | 0
2022-01-23 09:00 | 1 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 5 | 21 | 15 | 19 | 11 | 12 | 16 | 35 | 28 | 0 | 0
2022-01-23 10:00 | 1 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 7 | 21 | 15 | 18 | 13 | 14 | 15 | 36 | 27 | 0 | 0
2022-01-23 11:00 | 1 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 22 | 14 | 18 | 15 | 16 | 16 | 34 | 27 | 0 | 0
2022-01-23 12:00 | 1 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 23 | 14 | 17 | 17 | 18 | 16 | 35 | 26 | 0 | 0
2022-01-23 13:00 | 1 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 24 | 13 | 17 | 18 | 20 | 15 | 30 | 25 | 0 | 0
2022-01-23 14:00 | 1 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 24 | 12 | 17 | 19 | 18 | 14 | 29 | 22 | 0 | 0
2022-01-23 15:00 | 1 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 23 | 11 | 17 | 20 | 18 | 13 | 30 | 21 | 0 | 0
2022-01-23 16:00 | 1 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 21 | 10 | 17 | 19 | 18 | 11 | 28 | 17 | 0 | 0
2022-01-23 17:00 | 1 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 19 | 9 | 16 | 19 | 18 | 10 | 26 | 16 | 0 | 0
2022-01-23 18:00 | 1 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 17 | 8 | 16 | 18 | 18 | 10 | 25 | 15 | 0 | 0
2022-01-23 19:00 | 1 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 17 | 8 | 16 | 18 | 16 | 8 | 23 | 13 | 0 | 0
2022-01-23 20:00 | 1 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 15 | 7 | 16 | 17 | 16 | 8 | 21 | 13 | 0 | 0
2022-01-23 21:00 | 1 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 16 | 7 | 16 | 17 | 17 | 6 | 19 | 11 | 0 | 0
2022-01-23 22:00 | 1 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 14 | 7 | 15 | 18 | 17 | 5 | 18 | 11 | 0 | 0
2022-01-23 23:00 | 1 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 13 | 6 | 15 | 18 | 17 | 5 | 18 | 10 | 0 | 0
2022-01-24 | 1 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 13 | 6 | 14 | 19 | 18 | 4 | 17 | 10 | 0 | 0
2022-01-24 01:00 | 1 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 12 | 6 | 14 | 19 | 21 | 2 | 16 | 9 | 0 | 0
2022-01-24 02:00 | 1 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 12 | 5 | 15 | 20 | 21 | 1 | 16 | 9 | 0 | 0
2022-01-24 03:00 | 1 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 10 | 5 | 15 | 20 | 21 | 0 | 16 | 8 | 0 | 0
2022-01-24 04:00 | 1 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 10 | 5 | 15 | 20 | 22 | -1 | 15 | 8 | 0 | 0
2022-01-24 05:00 | 1 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 11 | 4 | 14 | 20 | 21 | -1 | 15 | 7 | 0 | 0
2022-01-24 06:00 | 1 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 10 | 4 | 14 | 20 | 21 | -2 | 14 | 6 | 0 | 0
2022-01-24 07:00 | 1 | 1 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 15 | 12 | 4 | 13 | 20 | 23 | -2 | 14 | 8 | 0 | 0
2022-01-24 08:00 | 1 | 1 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 15 | 16 | 4 | 13 | 21 | 23 | 0 | 15 | 10 | 0 | 0
2022-01-24 09:00 | 1 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 16 | 17 | 4 | 12 | 21 | 24 | 3 | 18 | 11 | 0 | 0
2022-01-24 10:00 | 1 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 17 | 19 | 5 | 13 | 22 | 26 | 4 | 17 | 13 | 0 | 0
2022-01-24 11:00 | 1 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 18 | 22 | 6 | 14 | 24 | 28 | 6 | 18 | 14 | 0 | 0
2022-01-24 12:00 | 1 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 23 | 7 | 15 | 25 | 29 | 9 | 20 | 14 | 0 | 0
2022-01-24 13:00 | 1 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 25 | 7 | 16 | 26 | 31 | 9 | 20 | 15 | 0 | 0
2022-01-24 14:00 | 1 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 25 | 8 | 17 | 27 | 32 | 10 | 20 | 15 | 0 | 0
2022-01-24 15:00 | 1 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 24 | 8 | 18 | 28 | 32 | 9 | 20 | 12 | 0 | 0
2022-01-24 16:00 | 1 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 24 | 7 | 16 | 27 | 31 | 9 | 20 | 11 | 0 | 0
2022-01-24 17:00 | 1 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 23 | 7 | 15 | 25 | 30 | 10 | 19 | 8 | 0 | 0
2022-01-24 18:00 | 1 | 1 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 21 | 6 | 13 | 24 | 30 | 8 | 18 | 8 | 0 | 0
2022-01-24 19:00 | 1 | 1 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 20 | 6 | 14 | 24 | 30 | 8 | 18 | 6 | 0 | 0
2022-01-24 20:00 | 1 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 21 | 7 | 14 | 24 | 29 | 5 | 18 | 5 | 0 | 0
2022-01-24 21:00 | 1 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 20 | 7 | 15 | 24 | 29 | 7 | 18 | 1 | 0 | 0
2022-01-24 22:00 | 1 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 20 | 7 | 15 | 23 | 28 | 6 | 18 | 1 | 0 | 0
2022-01-24 23:00 | 1 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 20 | 7 | 15 | 21 | 27 | 6 | 17 | 1 | 0 | 0
2022-01-25 | 1 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 20 | 7 | 15 | 20 | 25 | 5 | 17 | 1 | 0 | 0
2022-01-25 01:00 | 1 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 20 | 7 | 14 | 19 | 25 | 6 | 17 | -3 | 0 | 0
2022-01-25 02:00 | 1 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 20 | 8 | 13 | 19 | 23 | 6 | 16 | -3 | 0 | 0
2022-01-25 03:00 | 1 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 20 | 8 | 12 | 18 | 23 | 6 | 16 | -3 | 0 | 0
2022-01-25 04:00 | 1 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 20 | 8 | 13 | 18 | 25 | 6 | 17 | -2 | 0 | 0
2022-01-25 05:00 | 1 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 12 | 20 | 8 | 14 | 17 | 23 | 5 | 16 | -1 | 0 | 0
2022-01-25 06:00 | 1 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 21 | 8 | 15 | 17 | 24 | 4 | 15 | 0 | 0 | 0
2022-01-25 07:00 | 1 | 2 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 14 | 21 | 9 | 17 | 19 | 25 | 3 | 14 | 0 | 0 | 0
2022-01-25 08:00 | 1 | 2 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 16 | 22 | 10 | 18 | 21 | 28 | 5 | 18 | 2 | 0 | 0
2022-01-25 09:00 | 1 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 22 | 11 | 20 | 23 | 31 | 9 | 20 | 5 | 0 | 0
2022-01-25 10:00 | 1 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 23 | 12 | 21 | 26 | 32 | 11 | 22 | 11 | 0 | 0
2022-01-25 11:00 | 1 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 23 | 14 | 23 | 28 | 34 | 16 | 23 | 12 | 0 | 0
2022-01-25 12:00 | 1 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 24 | 15 | 24 | 31 | 35 | 17 | 23 | 16 | 0 | 0
2022-01-25 13:00 | 1 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 24 | 16 | 24 | 32 | 36 | 19 | 23 | 17 | 0 | 0
2022-01-25 14:00 | 1 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 26 | 18 | 24 | 32 | 37 | 19 | 23 | 20 | 0 | 0
2022-01-25 15:00 | 1 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 26 | 19 | 24 | 33 | 35 | 19 | 23 | 15 | 0 | 0
2022-01-25 16:00 | 1 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 27 | 18 | 24 | 33 | 34 | 17 | 22 | 13 | 0 | 0
2022-01-25 17:00 | 1 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 27 | 17 | 23 | 33 | 34 | 17 | 22 | 12 | 0 | 0
2022-01-25 18:00 | 1 | 2 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 29 | 16 | 23 | 33 | 33 | 16 | 23 | 9 | 0 | 0
2022-01-25 19:00 | 1 | 2 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 31 | 15 | 23 | 33 | 33 | 15 | 23 | 7 | 0 | 0
2022-01-25 20:00 | 1 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 32 | 15 | 23 | 32 | 33 | 14 | 23 | 8 | 0 | 0
2022-01-25 21:00 | 1 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 32 | 14 | 23 | 32 | 35 | 14 | 23 | 8 | 0 | 0
2022-01-25 22:00 | 1 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 32 | 14 | 23 | 33 | 36 | 13 | 22 | 8 | 0 | 0
2022-01-25 23:00 | 1 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 32 | 14 | 23 | 33 | 36 | 11 | 22 | 6 | 0 | 0
2022-01-26 | 1 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 32 | 14 | 23 | 34 | 37 | 10 | 21 | 7 | 0 | 0
2022-01-26 01:00 | 1 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 32 | 14 | 23 | 34 | 36 | 10 | 20 | 7 | 0 | 0
2022-01-26 02:00 | 1 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 33 | 14 | 23 | 35 | 37 | 10 | 19 | 5 | 0 | 0
2022-01-26 03:00 | 1 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 32 | 14 | 23 | 35 | 38 | 10 | 19 | 7 | 0 | 0
2022-01-26 04:00 | 1 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 32 | 14 | 22 | 35 | 39 | 9 | 18 | 6 | 0 | 0
2022-01-26 05:00 | 1 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 32 | 13 | 21 | 36 | 39 | 10 | 19 | 8 | 0 | 0
2022-01-26 06:00 | 1 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 32 | 13 | 20 | 36 | 40 | 9 | 20 | 8 | 0 | 0
2022-01-26 07:00 | 1 | 3 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 32 | 13 | 20 | 37 | 42 | 10 | 21 | 10 | 0 | 0
2022-01-26 08:00 | 1 | 3 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 32 | 14 | 21 | 37 | 43 | 10 | 22 | 16 | 0 | 0
2022-01-26 09:00 | 1 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 32 | 14 | 21 | 38 | 46 | 13 | 24 | 19 | 0 | 0
2022-01-26 10:00 | 1 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 32 | 15 | 21 | 38 | 58 | 17 | 26 | 20 | 0 | 0
2022-01-26 11:00 | 1 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 32 | 15 | 22 | 39 | 59 | 21 | 27 | 22 | 0 | 0
2022-01-26 12:00 | 1 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 32 | 16 | 22 | 39 | 60 | 22 | 27 | 23 | 0 | 0
2022-01-26 13:00 | 1 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 33 | 16 | 22 | 40 | 64 | 25 | 28 | 24 | 0 | 0
2022-01-26 14:00 | 1 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 33 | 16 | 23 | 41 | 63 | 24 | 29 | 24 | 0 | 0
2022-01-26 15:00 | 1 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 32 | 16 | 23 | 42 | 61 | 25 | 29 | 24 | 0 | 0
2022-01-26 16:00 | 1 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 31 | 15 | 22 | 43 | 59 | 24 | 27 | 22 | 0 | 0
2022-01-26 17:00 | 1 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 31 | 15 | 22 | 43 | 58 | 22 | 26 | 20 | 0 | 0
2022-01-26 18:00 | 1 | 3 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 30 | 14 | 21 | 44 | 56 | 20 | 25 | 18 | 0 | 0
2022-01-26 19:00 | 1 | 3 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 29 | 14 | 21 | 45 | 56 | 19 | 25 | 16 | 0 | 0
2022-01-26 20:00 | 1 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 29 | 13 | 20 | 47 | 56 | 18 | 25 | 14 | 0 | 0
2022-01-26 21:00 | 1 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 28 | 13 | 20 | 48 | 57 | 16 | 25 | 13 | 0 | 0
2022-01-26 22:00 | 1 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 28 | 13 | 20 | 48 | 56 | 14 | 25 | 11 | 0 | 0
2022-01-26 23:00 | 1 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 27 | 13 | 20 | 49 | 55 | 11 | 25 | 6 | 0 | 0
2022-01-27 | 1 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 27 | 13 | 20 | 49 | 55 | 12 | 25 | 3 | 0 | 0
2022-01-27 01:00 | 1 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 27 | 13 | 20 | 49 | 56 | 8 | 25 | 1 | 0 | 0
2022-01-27 02:00 | 1 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 26 | 13 | 20 | 48 | 55 | 8 | 25 | 0 | 0 | 0
2022-01-27 03:00 | 1 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 25 | 13 | 20 | 48 | 54 | 7 | 25 | -1 | 0 | 0
2022-01-27 04:00 | 1 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 25 | 13 | 20 | 47 | 55 | 3 | 25 | -3 | 0 | 0
2022-01-27 05:00 | 1 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 25 | 13 | 20 | 46 | 54 | 4 | 25 | -2 | 0 | 0
2022-01-27 06:00 | 1 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 25 | 13 | 20 | 45 | 55 | 4 | 25 | -2 | 0 | 0
2022-01-27 07:00 | 1 | 4 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 24 | 13 | 20 | 43 | 54 | 6 | 25 | -3 | 0 | 0
2022-01-27 08:00 | 1 | 4 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 24 | 14 | 21 | 42 | 54 | 8 | 26 | 1 | 0 | 0
2022-01-27 09:00 | 1 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 24 | 14 | 21 | 40 | 53 | 13 | 26 | 6 | 0 | 0
2022-01-27 10:00 | 1 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 24 | 15 | 23 | 40 | 54 | 20 | 28 | 9 | 0 | 0
2022-01-27 11:00 | 1 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 23 | 17 | 24 | 39 | 54 | 19 | 29 | 14 | 0 | 0
2022-01-27 12:00 | 1 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 23 | 18 | 26 | 39 | 48 | 20 | 30 | 16 | 0 | 0
2022-01-27 13:00 | 1 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 21 | 19 | 26 | 39 | 47 | 22 | 30 | 19 | 0 | 0
2022-01-27 14:00 | 1 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 18 | 21 | 25 | 38 | 46 | 22 | 32 | 23 | 0 | 0
2022-01-27 15:00 | 1 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 16 | 22 | 25 | 38 | 43 | 23 | 31 | 21 | 0 | 0
2022-01-27 16:00 | 1 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 14 | 21 | 25 | 37 | 42 | 22 | 28 | 19 | 0 | 0
2022-01-27 17:00 | 1 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 12 | 21 | 24 | 37 | 41 | 21 | 26 | 15 | 0 | 0
2022-01-27 18:00 | 1 | 4 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 10 | 20 | 24 | 36 | 40 | 19 | 25 | 12 | 0 | 0
2022-01-27 19:00 | 1 | 4 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 8 | 20 | 24 | 35 | 41 | 18 | 23 | 10 | 0 | 0
2022-01-27 20:00 | 1 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 5 | 20 | 23 | 35 | 40 | 19 | 23 | 9 | 0 | 0
2022-01-27 21:00 | 1 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 3 | 20 | 23 | 34 | 40 | 18 | 24 | 7 | 0 | 0
2022-01-27 22:00 | 1 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 2 | 19 | 23 | 34 | 38 | 14 | 23 | 5 | 0 | 0
2022-01-27 23:00 | 1 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 2 | 18 | 23 | 33 | 37 | 14 | 24 | 3 | 0 | 0
2022-01-28 | 1 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 1 | 17 | 23 | 33 | 36 | 14 | 24 | 0 | 0 | 0
2022-01-28 01:00 | 1 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 1 | 16 | 23 | 32 | 35 | 11 | 24 | -1 | 0 | 0
2022-01-28 02:00 | 1 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 2 | 16 | 22 | 32 | 34 | 10 | 25 | -1 | 0 | 0
2022-01-28 03:00 | 1 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 2 | 15 | 22 | 31 | 34 | 9 | 25 | -3 | 0 | 0
2022-01-28 04:00 | 1 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 2 | 15 | 21 | 30 | 33 | 9 | 24 | -1 | 0 | 0
2022-01-28 05:00 | 1 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 3 | 15 | 19 | 29 | 32 | 9 | 23 | 1 | 0 | 0
2022-01-28 06:00 | 1 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 3 | 15 | 18 | 28 | 31 | 10 | 25 | -1 | 0 | 0
2022-01-28 07:00 | 1 | 5 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 2 | 14 | 18 | 26 | 32 | 10 | 25 | -3 | 0 | 0
2022-01-28 08:00 | 1 | 5 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 3 | 14 | 18 | 25 | 33 | 14 | 26 | 1 | 0 | 0
2022-01-28 09:00 | 1 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 4 | 13 | 18 | 23 | 34 | 18 | 27 | 5 | 0 | 0
2022-01-28 10:00 | 1 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 6 | 14 | 18 | 24 | 32 | 21 | 28 | 9 | 0 | 0
2022-01-28 11:00 | 1 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 7 | 15 | 19 | 26 | 33 | 25 | 28 | 14 | 0 | 0
2022-01-28 12:00 | 1 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 8 | 16 | 19 | 27 | 32 | 27 | 29 | 17 | 0 | 0
2022-01-28 13:00 | 1 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 8 | 15 | 19 | 28 | 32 | 25 | 29 | 19 | 0 | 0
2022-01-28 14:00 | 1 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 9 | 15 | 19 | 29 | 33 | 25 | 30 | 20 | 0 | 0
2022-01-28 15:00 | 1 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 9 | 14 | 19 | 30 | 31 | 26 | 29 | 20 | 0 | 0
2022-01-28 16:00 | 1 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 8 | 14 | 18 | 30 | 30 | 26 | 27 | 20 | 0 | 0
2022-01-28 17:00 | 1 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 6 | 14 | 18 | 29 | 28 | 26 | 25 | 19 | 0 | 0
2022-01-28 18:00 | 1 | 5 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 5 | 14 | 17 | 29 | 28 | 25 | 25 | 18 | 0 | 0
2022-01-28 19:00 | 1 | 5 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 5 | 13 | 17 | 29 | 28 | 25 | 24 | 16 | 0 | 0
2022-01-28 20:00 | 1 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 3 | 12 | 17 | 30 | 29 | 26 | 23 | 13 | 0 | 0
2022-01-28 21:00 | 1 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 2 | 11 | 17 | 30 | 29 | 25 | 23 | 11 | 0 | 0
2022-01-28 22:00 | 1 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 1 | 10 | 17 | 29 | 30 | 25 | 22 | 12 | 0 | 0
2022-01-28 23:00 | 1 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 1 | 10 | 17 | 29 | 30 | 24 | 20 | 13 | 0 | 0
2022-01-29 | 1 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 1 | 9 | 17 | 28 | 29 | 24 | 20 | 14 | 0 | 0
2022-01-29 01:00 | 1 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 0 | 9 | 17 | 28 | 31 | 25 | 16 | 15 | 0 | 0
2022-01-29 02:00 | 1 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 0 | 9 | 17 | 29 | 32 | 25 | 18 | 14 | 0 | 0
2022-01-29 03:00 | 1 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 0 | 9 | 17 | 29 | 32 | 25 | 16 | 14 | 0 | 0
2022-01-29 04:00 | 1 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 0 | 9 | 17 | 30 | 33 | 24 | 15 | 14 | 0 | 0
2022-01-29 05:00 | 1 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 0 | 9 | 16 | 30 | 38 | 24 | 15 | 15 | 0 | 0
2022-01-29 06:00 | 1 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 0 | 9 | 16 | 31 | 33 | 23 | 16 | 12 | 0 | 0
2022-01-29 07:00 | 1 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 2 | 9 | 16 | 32 | 33 | 22 | 17 | 14 | 0 | 0
2022-01-29 08:00 | 1 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 2 | 10 | 15 | 34 | 34 | 24 | 19 | 16 | 0 | 0
2022-01-29 09:00 | 1 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 5 | 10 | 15 | 35 | 36 | 26 | 21 | 19 | 0 | 0
2022-01-29 10:00 | 1 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 7 | 11 | 16 | 37 | 39 | 28 | 22 | 22 | 0 | 0
2022-01-29 11:00 | 1 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 10 | 12 | 18 | 40 | 42 | 30 | 23 | 28 | 0 | 0
2022-01-29 12:00 | 1 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 11 | 13 | 19 | 42 | 42 | 32 | 24 | 35 | 0 | 0
2022-01-29 13:00 | 1 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 11 | 13 | 19 | 42 | 42 | 32 | 24 | 34 | 0 | 0
2022-01-29 14:00 | 1 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 12 | 13 | 18 | 41 | 43 | 31 | 26 | 34 | 0 | 0
2022-01-29 15:00 | 1 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 12 | 13 | 18 | 41 | 43 | 32 | 24 | 33 | 0 | 0
2022-01-29 16:00 | 1 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 12 | 12 | 18 | 40 | 42 | 31 | 24 | 31 | 0 | 0
2022-01-29 17:00 | 1 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 12 | 11 | 18 | 39 | 41 | 31 | 22 | 29 | 0 | 0
2022-01-29 18:00 | 1 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 12 | 10 | 18 | 38 | 38 | 32 | 22 | 28 | 0 | 0
2022-01-29 19:00 | 1 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 11 | 9 | 18 | 37 | 38 | 31 | 22 | 27 | 0 | 0
2022-01-29 20:00 | 1 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 12 | 9 | 19 | 35 | 38 | 31 | 20 | 27 | 0 | 0
2022-01-29 21:00 | 1 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 11 | 8 | 19 | 34 | 39 | 31 | 21 | 30 | 0 | 0
2022-01-29 22:00 | 1 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 9 | 8 | 19 | 33 | 37 | 32 | 20 | 30 | 0 | 0
2022-01-29 23:00 | 1 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 10 | 8 | 19 | 31 | 35 | 32 | 20 | 30 | 0 | 0
2022-01-30 | 1 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 10 | 8 | 19 | 30 | 35 | 33 | 19 | 30 | 0 | 0
2022-01-30 01:00 | 1 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 7 | 8 | 19 | 30 | 33 | 32 | 18 | 28 | 0 | 0
2022-01-30 02:00 | 1 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 7 | 8 | 20 | 29 | 31 | 35 | 17 | 28 | 0 | 0
2022-01-30 03:00 | 1 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 9 | 8 | 20 | 29 | 29 | 35 | 16 | 27 | 0 | 0
2022-01-30 04:00 | 1 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 9 | 7 | 19 | 29 | 29 | 38 | 15 | 27 | 0 | 0
2022-01-30 05:00 | 1 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 8 | 7 | 19 | 28 | 28 | 39 | 14 | 27 | 0 | 0
2022-01-30 06:00 | 1 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 9 | 6 | 18 | 28 | 28 | 40 | 13 | 28 | 0 | 0
2022-01-30 07:00 | 1 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 9 | 7 | 18 | 28 | 27 | 39 | 13 | 29 | 0 | 0
2022-01-30 08:00 | 1 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 9 | 9 | 18 | 28 | 29 | 39 | 15 | 29 | 0 | 0
2022-01-30 09:00 | 1 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 12 | 10 | 18 | 28 | 29 | 38 | 15 | 30 | 0 | 0
2022-01-30 10:00 | 1 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 15 | 11 | 18 | 28 | 30 | 39 | 17 | 30 | 0 | 0
2022-01-30 11:00 | 1 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 18 | 12 | 19 | 28 | 33 | 40 | 20 | 31 | 0 | 0
2022-01-30 12:00 | 1 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 18 | 13 | 19 | 28 | 33 | 39 | 20 | 31 | 0 | 0
2022-01-30 13:00 | 1 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 20 | 12 | 18 | 29 | 35 | 38 | 22 | 31 | 0 | 0
2022-01-30 14:00 | 1 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 21 | 12 | 18 | 29 | 35 | 37 | 23 | 32 | 0 | 0
2022-01-30 15:00 | 1 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 20 | 11 | 17 | 30 | 33 | 37 | 22 | 33 | 0 | 0
2022-01-30 16:00 | 1 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 20 | 10 | 17 | 30 | 32 | 35 | 19 | 32 | 0 | 0
2022-01-30 17:00 | 1 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 18 | 9 | 16 | 30 | 30 | 34 | 17 | 32 | 0 | 0
2022-01-30 18:00 | 1 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 16 | 8 | 16 | 30 | 31 | 32 | 16 | 31 | 0 | 0
2022-01-30 19:00 | 1 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 15 | 7 | 16 | 30 | 31 | 32 | 13 | 32 | 0 | 0
2022-01-30 20:00 | 1 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 13 | 6 | 16 | 30 | 31 | 32 | 12 | 31 | 0 | 0
2022-01-30 21:00 | 1 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 14 | 5 | 16 | 30 | 31 | 31 | 12 | 31 | 0 | 0
2022-01-30 22:00 | 1 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 15 | 5 | 16 | 29 | 30 | 30 | 12 | 30 | 0 | 0
2022-01-30 23:00 | 1 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 15 | 5 | 16 | 29 | 30 | 29 | 12 | 30 | 0 | 0
2022-01-31 | 1 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 15 | 5 | 16 | 28 | 30 | 29 | 13 | 32 | 0 | 0
2022-01-31 01:00 | 1 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 14 | 5 | 15 | 27 | 30 | 28 | 13 | 33 | 0 | 0
2022-01-31 02:00 | 1 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 14 | 5 | 15 | 26 | 30 | 28 | 13 | 32 | 0 | 0
2022-01-31 03:00 | 1 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 14 | 5 | 14 | 25 | 27 | 27 | 13 | 32 | 0 | 0
2022-01-31 04:00 | 1 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 14 | 5 | 14 | 25 | 25 | 27 | 13 | 32 | 0 | 0
2022-01-31 05:00 | 1 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 13 | 4 | 13 | 26 | 24 | 28 | 13 | 32 | 0 | 0
2022-01-31 06:00 | 1 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 11 | 4 | 13 | 26 | 23 | 30 | 13 | 30 | 0 | 0
2022-01-31 07:00 | 1 | 1 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 12 | 4 | 13 | 27 | 24 | 29 | 13 | 29 | 0 | 0
2022-01-31 08:00 | 1 | 1 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 14 | 5 | 13 | 27 | 26 | 30 | 13 | 29 | 0 | 0
2022-01-31 09:00 | 1 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 17 | 5 | 13 | 28 | 29 | 30 | 14 | 30 | 0 | 0
2022-01-31 10:00 | 1 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 20 | 6 | 14 | 29 | 29 | 31 | 15 | 30 | 0 | 0
2022-01-31 11:00 | 1 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 21 | 8 | 14 | 29 | 31 | 32 | 17 | 31 | 0 | 0
2022-01-31 12:00 | 1 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 21 | 9 | 15 | 30 | 33 | 32 | 18 | 31 | 0 | 0
2022-01-31 13:00 | 1 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 22 | 9 | 15 | 31 | 33 | 31 | 18 | 31 | 0 | 0
2022-01-31 14:00 | 1 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 23 | 9 | 14 | 32 | 33 | 32 | 19 | 31 | 0 | 0
2022-01-31 15:00 | 1 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 23 | 9 | 14 | 33 | 33 | 32 | 18 | 31 | 0 | 0
2022-01-31 16:00 | 1 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 22 | 7 | 14 | 33 | 33 | 32 | 15 | 30 | 0 | 0
2022-01-31 17:00 | 1 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 19 | 4 | 13 | 34 | 34 | 32 | 14 | 29 | 0 | 0
2022-01-31 18:00 | 1 | 1 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 18 | 2 | 13 | 34 | 34 | 29 | 12 | 28 | 0 | 0
2022-01-31 19:00 | 1 | 1 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 17 | 1 | 13 | 34 | 32 | 29 | 11 | 27 | 0 | 0
2022-01-31 20:00 | 1 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 16 | 1 | 12 | 33 | 31 | 29 | 11 | 26 | 0 | 0
2022-01-31 21:00 | 1 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 20 | 8 | 18 | 34 | 30 | 29 | 17 | 27 | 0 | 0
2022-01-31 22:00 | 1 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 24 | 14 | 24 | 35 | 30 | 28 | 22 | 27 | 0 | 0
2022-01-31 23:00 | 1 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 28 | 21 | 30 | 36 | 29 | 28 | 27 | 28 | 0 | 0
2022-02-01 | 2 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 32 | 28 | 36 | 37 | 28 | 27 | 33 | 29 | 0 | 0
2022-02-01 01:00 | 2 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 36 | 35 | 41 | 37 | 28 | 26 | 38 | 29 | 0 | 0
2022-02-01 02:00 | 2 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 40 | 41 | 47 | 38 | 27 | 26 | 44 | 30 | 0 | 0
2022-02-01 03:00 | 2 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 44 | 48 | 53 | 39 | 26 | 25 | 49 | 30 | 0 | 0
2022-02-01 04:00 | 2 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 41 | 48 | 53 | 40 | 25 | 23 | 49 | 31 | 0 | 0
2022-02-01 05:00 | 2 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 39 | 49 | 52 | 40 | 24 | 22 | 49 | 31 | 0 | 0
2022-02-01 06:00 | 2 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 35 | 49 | 51 | 40 | 26 | 22 | 49 | 31 | 0 | 0
2022-02-01 07:00 | 2 | 2 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 28 | 49 | 51 | 38 | 27 | 21 | 48 | 31 | 0 | 0
2022-02-01 08:00 | 2 | 2 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 24 | 48 | 52 | 41 | 28 | 21 | 47 | 31 | 0 | 0
2022-02-01 09:00 | 2 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 23 | 48 | 54 | 41 | 28 | 22 | 47 | 32 | 0 | 0
2022-02-01 10:00 | 2 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 22 | 48 | 55 | 46 | 30 | 24 | 48 | 32 | 0 | 0
2022-02-01 11:00 | 2 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 21 | 48 | 53 | 48 | 30 | 26 | 50 | 32 | 0 | 0
2022-02-01 12:00 | 2 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 23 | 48 | 45 | 50 | 30 | 28 | 50 | 33 | 0 | 0
2022-02-01 13:00 | 2 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 26 | 48 | 43 | 54 | 31 | 28 | 51 | 33 | 0 | 0
2022-02-01 14:00 | 2 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 26 | 49 | 42 | 54 | 32 | 30 | 52 | 33 | 0 | 0
2022-02-01 15:00 | 2 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 26 | 49 | 41 | 51 | 32 | 32 | 53 | 32 | 0 | 0
2022-02-01 16:00 | 2 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 24 | 49 | 37 | 50 | 30 | 31 | 53 | 31 | 0 | 0
2022-02-01 17:00 | 2 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 21 | 49 | 34 | 50 | 26 | 27 | 54 | 31 | 0 | 0
2022-02-01 18:00 | 2 | 2 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 19 | 49 | 32 | 47 | 25 | 28 | 52 | 31 | 0 | 0
2022-02-01 19:00 | 2 | 2 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 18 | 49 | 31 | 46 | 24 | 26 | 51 | 31 | 0 | 0
2022-02-01 20:00 | 2 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 17 | 50 | 31 | 44 | 24 | 25 | 52 | 31 | 0 | 0
2022-02-01 21:00 | 2 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 17 | 51 | 30 | 43 | 24 | 25 | 53 | 30 | 0 | 0
2022-02-01 22:00 | 2 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 17 | 51 | 29 | 55 | 22 | 24 | 52 | 30 | 0 | 0
2022-02-01 23:00 | 2 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 16 | 50 | 28 | 59 | 21 | 23 | 51 | 28 | 0 | 0
2022-02-02 | 2 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 15 | 49 | 28 | 58 | 21 | 23 | 50 | 28 | 0 | 0
2022-02-02 01:00 | 2 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 15 | 49 | 28 | 58 | 21 | 23 | 50 | 28 | 0 | 0
2022-02-02 02:00 | 2 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 15 | 49 | 28 | 56 | 20 | 23 | 51 | 28 | 0 | 0
2022-02-02 03:00 | 2 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 14 | 49 | 29 | 52 | 20 | 23 | 50 | 26 | 0 | 0
2022-02-02 04:00 | 2 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 14 | 35 | 29 | 51 | 20 | 23 | 49 | 26 | 0 | 0
2022-02-02 05:00 | 2 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 15 | 33 | 30 | 53 | 20 | 23 | 50 | 27 | 0 | 0
2022-02-02 06:00 | 2 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 12 | 33 | 28 | 50 | 21 | 24 | 50 | 26 | 0 | 0
2022-02-02 07:00 | 2 | 3 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 13 | 32 | 27 | 51 | 21 | 25 | 48 | 25 | 0 | 0
2022-02-02 08:00 | 2 | 3 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 14 | 32 | 27 | 49 | 21 | 27 | 49 | 26 | 0 | 0
2022-02-02 09:00 | 2 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 17 | 31 | 27 | 51 | 23 | 30 | 42 | 26 | 0 | 0
2022-02-02 10:00 | 2 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 23 | 29 | 27 | 52 | 25 | 35 | 39 | 27 | 0 | 0
2022-02-02 11:00 | 2 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 29 | 27 | 27 | 52 | 27 | 39 | 37 | 27 | 0 | 0
2022-02-02 12:00 | 2 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 32 | 29 | 29 | 51 | 31 | 40 | 35 | 27 | 0 | 0
2022-02-02 13:00 | 2 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 34 | 28 | 29 | 48 | 31 | 41 | 35 | 27 | 0 | 0
2022-02-02 14:00 | 2 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 31 | 27 | 29 | 44 | 30 | 41 | 34 | 25 | 0 | 0
2022-02-02 15:00 | 2 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 30 | 27 | 28 | 41 | 30 | 41 | 33 | 25 | 0 | 0
2022-02-02 16:00 | 2 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 29 | 27 | 27 | 39 | 28 | 39 | 32 | 24 | 0 | 0
2022-02-02 17:00 | 2 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 28 | 26 | 26 | 39 | 25 | 39 | 31 | 23 | 0 | 0
2022-02-02 18:00 | 2 | 3 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 25 | 26 | 37 | 23 | 38 | 30 | 22 | 0 | 0
2022-02-02 19:00 | 2 | 3 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 29 | 24 | 26 | 36 | 22 | 37 | 29 | 21 | 0 | 0
2022-02-02 20:00 | 2 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 28 | 23 | 24 | 35 | 22 | 35 | 28 | 20 | 0 | 0
2022-02-02 21:00 | 2 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 28 | 23 | 24 | 34 | 21 | 34 | 27 | 18 | 0 | 0
2022-02-02 22:00 | 2 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 29 | 22 | 23 | 34 | 22 | 33 | 26 | 19 | 0 | 0
2022-02-02 23:00 | 2 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 29 | 21 | 25 | 33 | 22 | 34 | 25 | 18 | 0 | 0
2022-02-03 | 2 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 30 | 21 | 25 | 32 | 22 | 34 | 24 | 16 | 0 | 0
2022-02-03 01:00 | 2 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 31 | 20 | 25 | 31 | 22 | 34 | 23 | 14 | 0 | 0
2022-02-03 02:00 | 2 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 32 | 19 | 25 | 30 | 21 | 34 | 22 | 10 | 0 | 0
2022-02-03 03:00 | 2 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 33 | 20 | 25 | 30 | 22 | 35 | 20 | 11 | 0 | 0
2022-02-03 04:00 | 2 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 33 | 20 | 24 | 29 | 22 | 35 | 20 | 9 | 0 | 0
2022-02-03 05:00 | 2 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 33 | 20 | 23 | 29 | 23 | 35 | 19 | 8 | 0 | 0
2022-02-03 06:00 | 2 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 33 | 20 | 23 | 27 | 25 | 35 | 18 | 7 | 0 | 0
2022-02-03 07:00 | 2 | 4 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 34 | 21 | 22 | 27 | 27 | 36 | 18 | 4 | 0 | 0
2022-02-03 08:00 | 2 | 4 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 34 | 22 | 22 | 30 | 30 | 37 | 21 | 7 | 0 | 0
2022-02-03 09:00 | 2 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 34 | 24 | 22 | 32 | 34 | 38 | 23 | 10 | 0 | 0
2022-02-03 10:00 | 2 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 34 | 27 | 21 | 34 | 35 | 38 | 25 | 15 | 0 | 0
2022-02-03 11:00 | 2 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 34 | 30 | 21 | 37 | 40 | 38 | 28 | 17 | 0 | 0
2022-02-03 12:00 | 2 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 35 | 33 | 21 | 37 | 44 | 38 | 30 | 19 | 0 | 0
2022-02-03 13:00 | 2 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 36 | 33 | 22 | 37 | 36 | 40 | 33 | 22 | 0 | 0
2022-02-03 14:00 | 2 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 37 | 32 | 22 | 36 | 35 | 41 | 33 | 21 | 0 | 0
2022-02-03 15:00 | 2 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 37 | 33 | 24 | 35 | 36 | 42 | 32 | 21 | 0 | 0
2022-02-03 16:00 | 2 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 38 | 31 | 24 | 36 | 35 | 42 | 31 | 20 | 0 | 0
2022-02-03 17:00 | 2 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 39 | 30 | 22 | 35 | 31 | 42 | 31 | 15 | 0 | 0
2022-02-03 18:00 | 2 | 4 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 39 | 29 | 22 | 34 | 30 | 42 | 30 | 15 | 0 | 0
2022-02-03 19:00 | 2 | 4 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 41 | 29 | 20 | 33 | 28 | 39 | 29 | 8 | 0 | 0
2022-02-03 20:00 | 2 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 42 | 29 | 18 | 33 | 26 | 36 | 30 | 8 | 0 | 0
2022-02-03 21:00 | 2 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 41 | 29 | 17 | 33 | 25 | 34 | 30 | 5 | 0 | 0
2022-02-03 22:00 | 2 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 42 | 30 | 18 | 33 | 24 | 33 | 30 | 4 | 0 | 0
2022-02-03 23:00 | 2 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 42 | 31 | 18 | 34 | 24 | 30 | 31 | 2 | 0 | 0
2022-02-04 | 2 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 42 | 31 | 18 | 34 | 23 | 29 | 32 | 1 | 0 | 0
2022-02-04 01:00 | 2 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 39 | 32 | 19 | 34 | 24 | 28 | 32 | -1 | 0 | 0
2022-02-04 02:00 | 2 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 33 | 32 | 19 | 34 | 21 | 27 | 31 | -2 | 0 | 0
2022-02-04 03:00 | 2 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 31 | 30 | 19 | 34 | 23 | 26 | 32 | -2 | 0 | 0
2022-02-04 04:00 | 2 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 30 | 28 | 19 | 34 | 24 | 26 | 33 | -4 | 0 | 0
2022-02-04 05:00 | 2 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 29 | 28 | 19 | 34 | 25 | 24 | 32 | -6 | 0 | 0
2022-02-04 06:00 | 2 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 28 | 23 | 19 | 34 | 25 | 24 | 33 | -5 | 0 | 0
2022-02-04 07:00 | 2 | 5 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 27 | 19 | 19 | 34 | 26 | 23 | 32 | -4 | 0 | 0
2022-02-04 08:00 | 2 | 5 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 25 | 19 | 19 | 35 | 30 | 23 | 32 | 0 | 0 | 0
2022-02-04 09:00 | 2 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 25 | 19 | 19 | 35 | 33 | 23 | 32 | 2 | 0 | 0
2022-02-04 10:00 | 2 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 26 | 20 | 19 | 36 | 37 | 24 | 33 | 9 | 0 | 0
2022-02-04 11:00 | 2 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 27 | 20 | 20 | 37 | 38 | 25 | 29 | 15 | 0 | 0
2022-02-04 12:00 | 2 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 26 | 20 | 21 | 37 | 40 | 26 | 26 | 18 | 0 | 0
2022-02-04 13:00 | 2 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 25 | 19 | 20 | 35 | 42 | 27 | 25 | 21 | 0 | 0
2022-02-04 14:00 | 2 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 24 | 19 | 20 | 33 | 42 | 27 | 24 | 21 | 0 | 0
2022-02-04 15:00 | 2 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 26 | 20 | 20 | 32 | 44 | 26 | 23 | 22 | 0 | 0
2022-02-04 16:00 | 2 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 22 | 16 | 20 | 31 | 43 | 26 | 21 | 22 | 0 | 0
2022-02-04 17:00 | 2 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 20 | 15 | 19 | 30 | 40 | 24 | 20 | 19 | 0 | 0
2022-02-04 18:00 | 2 | 5 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 18 | 15 | 19 | 29 | 38 | 23 | 19 | 15 | 0 | 0
2022-02-04 19:00 | 2 | 5 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 16 | 15 | 18 | 28 | 37 | 23 | 18 | 13 | 0 | 0
2022-02-04 20:00 | 2 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 15 | 14 | 18 | 28 | 37 | 22 | 18 | 10 | 0 | 0
2022-02-04 21:00 | 2 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 14 | 13 | 18 | 27 | 35 | 21 | 18 | 5 | 0 | 0
2022-02-04 22:00 | 2 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 13 | 12 | 18 | 26 | 33 | 20 | 17 | 6 | 0 | 0
2022-02-04 23:00 | 2 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 13 | 12 | 17 | 25 | 34 | 19 | 16 | 4 | 0 | 0
2022-02-05 | 2 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 12 | 9 | 18 | 25 | 33 | 18 | 15 | 4 | 0 | 0
2022-02-05 01:00 | 2 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 11 | 6 | 17 | 24 | 34 | 18 | 14 | 5 | 0 | 0
2022-02-05 02:00 | 2 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 11 | 6 | 18 | 21 | 32 | 18 | 13 | 6 | 0 | 0
2022-02-05 03:00 | 2 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 11 | 6 | 19 | 22 | 32 | 18 | 13 | 6 | 0 | 0
2022-02-05 04:00 | 2 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 10 | 4 | 19 | 21 | 30 | 20 | 12 | 7 | 0 | 0
2022-02-05 05:00 | 2 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 9 | 7 | 19 | 21 | 28 | 20 | 11 | 9 | 0 | 0
2022-02-05 06:00 | 2 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 8 | 7 | 18 | 20 | 31 | 21 | 9 | 9 | 0 | 0
2022-02-05 07:00 | 2 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 10 | 7 | 17 | 20 | 30 | 21 | 11 | 10 | 0 | 0
2022-02-05 08:00 | 2 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 13 | 9 | 17 | 23 | 35 | 22 | 14 | 11 | 0 | 0
2022-02-05 09:00 | 2 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 15 | 10 | 19 | 26 | 37 | 23 | 16 | 13 | 0 | 0
2022-02-05 10:00 | 2 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 18 | 13 | 20 | 27 | 40 | 25 | 17 | 18 | 0 | 0
2022-02-05 11:00 | 2 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 18 | 13 | 19 | 27 | 42 | 26 | 19 | 23 | 0 | 0
2022-02-05 12:00 | 2 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 21 | 13 | 20 | 29 | 45 | 28 | 19 | 25 | 0 | 0
2022-02-05 13:00 | 2 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 23 | 14 | 21 | 27 | 44 | 30 | 19 | 26 | 0 | 0
2022-02-05 14:00 | 2 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 24 | 13 | 23 | 30 | 44 | 32 | 19 | 25 | 0 | 0
2022-02-05 15:00 | 2 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 26 | 11 | 22 | 29 | 43 | 35 | 20 | 28 | 0 | 0
2022-02-05 16:00 | 2 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 27 | 10 | 21 | 26 | 43 | 35 | 20 | 28 | 0 | 0
2022-02-05 17:00 | 2 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 28 | 9 | 20 | 25 | 42 | 34 | 19 | 28 | 0 | 0
2022-02-05 18:00 | 2 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 29 | 9 | 20 | 23 | 40 | 32 | 18 | 27 | 0 | 0
2022-02-05 19:00 | 2 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 29 | 5 | 19 | 22 | 40 | 32 | 17 | 26 | 0 | 0
2022-02-05 20:00 | 2 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 30 | 4 | 19 | 20 | 36 | 32 | 16 | 26 | 0 | 0
2022-02-05 21:00 | 2 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 30 | 3 | 19 | 19 | 37 | 32 | 15 | 26 | 0 | 0
2022-02-05 22:00 | 2 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 30 | 1 | 19 | 19 | 36 | 32 | 14 | 26 | 0 | 0
2022-02-05 23:00 | 2 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 30 | -2 | 19 | 16 | 36 | 31 | 12 | 26 | 0 | 0
2022-02-06 | 2 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 31 | -1 | 20 | 14 | 36 | 30 | 11 | 26 | 0 | 0
2022-02-06 01:00 | 2 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 31 | -3 | 20 | 13 | 37 | 27 | 9 | 25 | 0 | 0
2022-02-06 02:00 | 2 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 30 | -3 | 19 | 11 | 35 | 26 | 8 | 25 | 0 | 0
2022-02-06 03:00 | 2 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 30 | -4 | 21 | 10 | 33 | 24 | 7 | 25 | 0 | 0
2022-02-06 04:00 | 2 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 30 | -4 | 22 | 9 | 31 | 21 | 6 | 25 | 0 | 0
2022-02-06 05:00 | 2 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 9 | 26 | -5 | 23 | 9 | 29 | 19 | 5 | 25 | 0 | 0
2022-02-06 06:00 | 2 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 8 | 24 | -5 | 24 | 8 | 31 | 17 | 4 | 25 | 0 | 0
2022-02-06 07:00 | 2 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 8 | 21 | -6 | 20 | 8 | 32 | 16 | 4 | 25 | 0 | 0
2022-02-06 08:00 | 2 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 9 | 19 | -4 | 15 | 11 | 37 | 17 | 5 | 25 | 0 | 0
2022-02-06 09:00 | 2 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 19 | -1 | 16 | 12 | 40 | 19 | 7 | 27 | 0 | 0
2022-02-06 10:00 | 2 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 19 | 0 | 15 | 14 | 44 | 19 | 8 | 28 | 0 | 0
2022-02-06 11:00 | 2 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 19 | 3 | 18 | 15 | 48 | 19 | 10 | 30 | 0 | 0
2022-02-06 12:00 | 2 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 19 | 3 | 19 | 18 | 48 | 19 | 12 | 30 | 0 | 0
2022-02-06 13:00 | 2 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 19 | 2 | 19 | 20 | 48 | 20 | 13 | 31 | 0 | 0
2022-02-06 14:00 | 2 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 18 | 3 | 18 | 20 | 48 | 19 | 13 | 33 | 0 | 0
2022-02-06 15:00 | 2 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 18 | 3 | 19 | 20 | 46 | 19 | 13 | 33 | 0 | 0
2022-02-06 16:00 | 2 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 18 | 1 | 18 | 19 | 43 | 19 | 13 | 33 | 0 | 0
2022-02-06 17:00 | 2 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 16 | -1 | 17 | 17 | 40 | 17 | 11 | 31 | 0 | 0
2022-02-06 18:00 | 2 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 14 | -2 | 17 | 16 | 38 | 15 | 11 | 32 | 0 | 0
2022-02-06 19:00 | 2 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 12 | -3 | 16 | 14 | 36 | 14 | 10 | 31 | 0 | 0
2022-02-06 20:00 | 2 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 11 | -4 | 16 | 13 | 35 | 13 | 8 | 30 | 0 | 0
2022-02-06 21:00 | 2 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 11 | 11 | -4 | 16 | 12 | 35 | 11 | 7 | 28 | 0 | 0
2022-02-06 22:00 | 2 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 10 | -6 | 15 | 11 | 34 | 9 | 6 | 27 | 0 | 0
2022-02-06 23:00 | 2 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 10 | 9 | -7 | 15 | 10 | 33 | 8 | 5 | 27 | 0 | 0
2022-02-07 | 2 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 9 | 8 | -7 | 15 | 9 | 32 | 8 | 4 | 24 | 0 | 0
2022-02-07 01:00 | 2 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 8 | 8 | -7 | 15 | 8 | 31 | 8 | 3 | 24 | 0 | 0
2022-02-07 02:00 | 2 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 7 | 7 | -8 | 15 | 7 | 31 | 7 | 3 | 23 | 0 | 0
2022-02-07 03:00 | 2 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 6 | 6 | -10 | 15 | 7 | 31 | 6 | 1 | 22 | 0 | 0
2022-02-07 04:00 | 2 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 6 | 6 | -9 | 15 | 7 | 31 | 6 | 1 | 21 | 0 | 0
2022-02-07 05:00 | 2 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 5 | 5 | -8 | 15 | 6 | 30 | 6 | 1 | 21 | 0 | 0
2022-02-07 06:00 | 2 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 5 | 6 | -8 | 15 | 5 | 31 | 6 | 2 | 21 | 0 | 0
2022-02-07 07:00 | 2 | 1 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 6 | 7 | -6 | 15 | 7 | 32 | 8 | 2 | 21 | 0 | 0
2022-02-07 08:00 | 2 | 1 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 9 | 10 | -4 | 16 | 10 | 37 | 11 | 4 | 21 | 0 | 0
2022-02-07 09:00 | 2 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 11 | 11 | 3 | 17 | 13 | 41 | 15 | 6 | 22 | 0 | 0
2022-02-07 10:00 | 2 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 14 | 13 | 7 | 19 | 17 | 46 | 18 | 9 | 22 | 0 | 0
2022-02-07 11:00 | 2 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 17 | 17 | 10 | 21 | 20 | 49 | 21 | 12 | 23 | 0 | 0
2022-02-07 12:00 | 2 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 20 | 13 | 21 | 22 | 50 | 24 | 15 | 23 | 0 | 0
2022-02-07 13:00 | 2 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 22 | 16 | 20 | 23 | 51 | 26 | 18 | 24 | 0 | 0
2022-02-07 14:00 | 2 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 25 | 18 | 22 | 25 | 50 | 28 | 20 | 23 | 0 | 0
2022-02-07 15:00 | 2 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 26 | 18 | 22 | 27 | 48 | 29 | 20 | 22 | 0 | 0
2022-02-07 16:00 | 2 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 26 | 18 | 20 | 25 | 45 | 29 | 20 | 21 | 0 | 0
2022-02-07 17:00 | 2 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 24 | 18 | 18 | 25 | 43 | 27 | 18 | 20 | 0 | 0
2022-02-07 18:00 | 2 | 1 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 22 | 18 | 16 | 24 | 40 | 25 | 18 | 17 | 0 | 0
2022-02-07 19:00 | 2 | 1 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 22 | 18 | 15 | 25 | 39 | 25 | 18 | 16 | 0 | 0
2022-02-07 20:00 | 2 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 22 | 18 | 15 | 24 | 38 | 24 | 19 | 14 | 0 | 0
2022-02-07 21:00 | 2 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 22 | 17 | 15 | 24 | 35 | 23 | 19 | 16 | 0 | 0
2022-02-07 22:00 | 2 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 22 | 18 | 15 | 26 | 32 | 23 | 19 | 15 | 0 | 0
2022-02-07 23:00 | 2 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 22 | 18 | 15 | 26 | 31 | 24 | 19 | 14 | 0 | 0
2022-02-08 | 2 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 22 | 18 | 16 | 27 | 30 | 25 | 20 | 14 | 0 | 0
2022-02-08 01:00 | 2 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 22 | 18 | 15 | 28 | 29 | 22 | 21 | 13 | 0 | 0
2022-02-08 02:00 | 2 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 22 | 18 | 14 | 27 | 27 | 21 | 22 | 11 | 0 | 0
2022-02-08 03:00 | 2 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 21 | 17 | 14 | 28 | 25 | 20 | 22 | 9 | 0 | 0
2022-02-08 04:00 | 2 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 21 | 17 | 14 | 28 | 25 | 19 | 22 | 8 | 0 | 0
2022-02-08 05:00 | 2 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 20 | 16 | 15 | 27 | 25 | 19 | 23 | 6 | 0 | 0
2022-02-08 06:00 | 2 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 20 | 14 | 15 | 27 | 25 | 19 | 22 | 6 | 0 | 0
2022-02-08 07:00 | 2 | 2 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 20 | 12 | 16 | 28 | 25 | 19 | 22 | 9 | 0 | 0
2022-02-08 08:00 | 2 | 2 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 24 | 11 | 18 | 32 | 25 | 22 | 25 | 11 | 0 | 0
2022-02-08 09:00 | 2 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 25 | 12 | 20 | 32 | 25 | 25 | 27 | 13 | 0 | 0
2022-02-08 10:00 | 2 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 26 | 13 | 22 | 34 | 25 | 27 | 25 | 16 | 0 | 0
2022-02-08 11:00 | 2 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 28 | 16 | 24 | 35 | 25 | 30 | 25 | 17 | 0 | 0
2022-02-08 12:00 | 2 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 29 | 17 | 23 | 34 | 25 | 31 | 26 | 19 | 0 | 0
2022-02-08 13:00 | 2 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 30 | 18 | 24 | 34 | 23 | 32 | 25 | 20 | 0 | 0
2022-02-08 14:00 | 2 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 30 | 19 | 23 | 34 | 21 | 32 | 26 | 18 | 0 | 0
2022-02-08 15:00 | 2 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 32 | 19 | 24 | 33 | 20 | 33 | 25 | 19 | 0 | 0
2022-02-08 16:00 | 2 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 30 | 18 | 22 | 32 | 21 | 34 | 24 | 18 | 0 | 0
2022-02-08 17:00 | 2 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 27 | 17 | 21 | 31 | 21 | 33 | 22 | 18 | 0 | 0
2022-02-08 18:00 | 2 | 2 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 27 | 15 | 20 | 30 | 22 | 32 | 21 | 17 | 0 | 0
2022-02-08 19:00 | 2 | 2 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 27 | 14 | 19 | 28 | 22 | 32 | 20 | 17 | 0 | 0
2022-02-08 20:00 | 2 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 25 | 11 | 17 | 28 | 22 | 32 | 20 | 17 | 0 | 0
2022-02-08 21:00 | 2 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 27 | 10 | 15 | 28 | 22 | 31 | 19 | 18 | 0 | 0
2022-02-08 22:00 | 2 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 27 | 7 | 14 | 28 | 23 | 31 | 19 | 18 | 0 | 0
2022-02-08 23:00 | 2 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 27 | 7 | 13 | 27 | 23 | 31 | 18 | 18 | 0 | 0
2022-02-09 | 2 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 27 | 7 | 12 | 24 | 21 | 29 | 18 | 19 | 0 | 0
2022-02-09 01:00 | 2 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 27 | 6 | 13 | 23 | 21 | 27 | 15 | 19 | 0 | 0
2022-02-09 02:00 | 2 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 27 | 9 | 11 | 20 | 21 | 27 | 15 | 19 | 0 | 0
2022-02-09 03:00 | 2 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 25 | 11 | 11 | 19 | 21 | 27 | 14 | 19 | 0 | 0
2022-02-09 04:00 | 2 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 25 | 15 | 10 | 18 | 21 | 26 | 13 | 19 | 0 | 0
2022-02-09 05:00 | 2 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 26 | 16 | 9 | 17 | 21 | 27 | 14 | 18 | 0 | 0
2022-02-09 06:00 | 2 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 26 | 16 | 9 | 16 | 21 | 27 | 15 | 19 | 0 | 0
2022-02-09 07:00 | 2 | 3 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 25 | 18 | 9 | 19 | 21 | 27 | 16 | 19 | 0 | 0
2022-02-09 08:00 | 2 | 3 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 26 | 21 | 9 | 22 | 22 | 27 | 19 | 19 | 0 | 0
2022-02-09 09:00 | 2 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 27 | 23 | 10 | 27 | 22 | 27 | 24 | 21 | 0 | 0
2022-02-09 10:00 | 2 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 28 | 27 | 11 | 30 | 23 | 27 | 26 | 21 | 0 | 0
2022-02-09 11:00 | 2 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 29 | 27 | 13 | 32 | 25 | 27 | 29 | 23 | 0 | 0
2022-02-09 12:00 | 2 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 30 | 28 | 13 | 33 | 24 | 27 | 32 | 24 | 0 | 0
2022-02-09 13:00 | 2 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 31 | 29 | 13 | 36 | 24 | 27 | 32 | 27 | 0 | 0
2022-02-09 14:00 | 2 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 30 | 28 | 14 | 37 | 24 | 28 | 32 | 29 | 0 | 0
2022-02-09 15:00 | 2 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 30 | 28 | 15 | 38 | 23 | 27 | 33 | 28 | 0 | 0
2022-02-09 16:00 | 2 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 27 | 27 | 16 | 38 | 24 | 25 | 33 | 27 | 0 | 0
2022-02-09 17:00 | 2 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 24 | 27 | 14 | 37 | 22 | 24 | 32 | 26 | 0 | 0
2022-02-09 18:00 | 2 | 3 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 24 | 27 | 13 | 34 | 22 | 23 | 31 | 25 | 0 | 0
2022-02-09 19:00 | 2 | 3 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 24 | 26 | 13 | 33 | 22 | 21 | 31 | 23 | 0 | 0
2022-02-09 20:00 | 2 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 23 | 26 | 14 | 33 | 22 | 20 | 31 | 22 | 0 | 0
2022-02-09 21:00 | 2 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 22 | 25 | 14 | 34 | 21 | 19 | 31 | 22 | 0 | 0
2022-02-09 22:00 | 2 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 22 | 24 | 14 | 33 | 18 | 16 | 32 | 22 | 0 | 0
2022-02-09 23:00 | 2 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 21 | 22 | 14 | 34 | 18 | 14 | 31 | 21 | 0 | 0
2022-02-10 | 2 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 18 | 21 | 14 | 34 | 16 | 14 | 31 | 21 | 0 | 0
2022-02-10 01:00 | 2 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 17 | 20 | 15 | 33 | 15 | 13 | 31 | 21 | 0 | 0
2022-02-10 02:00 | 2 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 15 | 19 | 14 | 32 | 14 | 10 | 30 | 21 | 0 | 0
2022-02-10 03:00 | 2 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 13 | 19 | 14 | 30 | 14 | 7 | 28 | 21 | 0 | 0
2022-02-10 04:00 | 2 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 11 | 18 | 14 | 25 | 13 | 4 | 27 | 21 | 0 | 0
2022-02-10 05:00 | 2 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 9 | 16 | 14 | 31 | 11 | 2 | 28 | 21 | 0 | 0
2022-02-10 06:00 | 2 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 8 | 15 | 15 | 30 | 11 | 1 | 27 | 22 | 0 | 0
2022-02-10 07:00 | 2 | 4 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 8 | 13 | 16 | 34 | 12 | -1 | 26 | 22 | 0 | 0
2022-02-10 08:00 | 2 | 4 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 9 | 14 | 17 | 35 | 13 | 1 | 27 | 22 | 0 | 0
2022-02-10 09:00 | 2 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 10 | 14 | 18 | 36 | 15 | 4 | 27 | 23 | 0 | 0
2022-02-10 10:00 | 2 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 13 | 17 | 20 | 35 | 16 | 6 | 26 | 24 | 0 | 0
2022-02-10 11:00 | 2 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 15 | 20 | 22 | 37 | 17 | 8 | 26 | 25 | 0 | 0
2022-02-10 12:00 | 2 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 16 | 22 | 21 | 38 | 19 | 10 | 28 | 27 | 0 | 0
2022-02-10 13:00 | 2 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 17 | 23 | 22 | 39 | 21 | 12 | 29 | 31 | 0 | 0
2022-02-10 14:00 | 2 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 18 | 24 | 23 | 40 | 22 | 13 | 29 | 33 | 0 | 0
2022-02-10 15:00 | 2 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 18 | 24 | 23 | 39 | 23 | 14 | 28 | 33 | 0 | 0
2022-02-10 16:00 | 2 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 16 | 24 | 21 | 39 | 21 | 13 | 28 | 32 | 0 | 0
2022-02-10 17:00 | 2 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 13 | 21 | 20 | 36 | 21 | 12 | 26 | 30 | 0 | 0
2022-02-10 18:00 | 2 | 4 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 12 | 19 | 19 | 32 | 20 | 12 | 24 | 25 | 0 | 0
2022-02-10 19:00 | 2 | 4 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 11 | 18 | 21 | 29 | 20 | 11 | 23 | 26 | 0 | 0
2022-02-10 20:00 | 2 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 11 | 17 | 21 | 28 | 20 | 11 | 21 | 22 | 0 | 0
2022-02-10 21:00 | 2 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 10 | 17 | 21 | 30 | 20 | 11 | 20 | 22 | 0 | 0
2022-02-10 22:00 | 2 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 8 | 17 | 22 | 30 | 20 | 11 | 18 | 19 | 0 | 0
2022-02-10 23:00 | 2 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 8 | 16 | 23 | 27 | 18 | 12 | 18 | 19 | 0 | 0
2022-02-11 | 2 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 6 | 16 | 24 | 27 | 18 | 11 | 20 | 19 | 0 | 0
2022-02-11 01:00 | 2 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 7 | 16 | 25 | 27 | 18 | 9 | 20 | 20 | 0 | 0
2022-02-11 02:00 | 2 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 7 | 15 | 26 | 26 | 17 | 8 | 20 | 20 | 0 | 0
2022-02-11 03:00 | 2 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 7 | 15 | 26 | 25 | 17 | 6 | 20 | 22 | 0 | 0
2022-02-11 04:00 | 2 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 5 | 14 | 27 | 25 | 17 | 9 | 19 | 22 | 0 | 0
2022-02-11 05:00 | 2 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 6 | 14 | 26 | 25 | 18 | 8 | 19 | 22 | 0 | 0
2022-02-11 06:00 | 2 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 5 | 16 | 26 | 24 | 19 | 8 | 19 | 23 | 0 | 0
2022-02-11 07:00 | 2 | 5 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 7 | 18 | 26 | 23 | 20 | 4 | 20 | 23 | 0 | 0
2022-02-11 08:00 | 2 | 5 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 8 | 20 | 25 | 27 | 21 | 10 | 21 | 24 | 0 | 0
2022-02-11 09:00 | 2 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 11 | 22 | 26 | 30 | 21 | 14 | 24 | 25 | 0 | 0
2022-02-11 10:00 | 2 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 15 | 24 | 26 | 33 | 23 | 16 | 29 | 27 | 0 | 0
2022-02-11 11:00 | 2 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 15 | 28 | 27 | 35 | 24 | 19 | 32 | 30 | 0 | 0
2022-02-11 12:00 | 2 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 20 | 30 | 29 | 37 | 25 | 22 | 33 | 31 | 0 | 0
2022-02-11 13:00 | 2 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 21 | 31 | 28 | 38 | 26 | 24 | 35 | 34 | 0 | 0
2022-02-11 14:00 | 2 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 23 | 31 | 31 | 39 | 27 | 26 | 35 | 36 | 0 | 0
2022-02-11 15:00 | 2 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 24 | 30 | 29 | 38 | 28 | 26 | 34 | 37 | 0 | 0
2022-02-11 16:00 | 2 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 22 | 28 | 29 | 37 | 28 | 26 | 34 | 37 | 0 | 0
2022-02-11 17:00 | 2 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 20 | 28 | 28 | 37 | 27 | 24 | 33 | 38 | 0 | 0
2022-02-11 18:00 | 2 | 5 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 19 | 27 | 27 | 36 | 27 | 22 | 32 | 37 | 0 | 0
2022-02-11 19:00 | 2 | 5 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 18 | 27 | 27 | 36 | 27 | 20 | 32 | 35 | 0 | 0
2022-02-11 20:00 | 2 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 18 | 27 | 29 | 33 | 27 | 19 | 32 | 36 | 0 | 0
2022-02-11 21:00 | 2 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 18 | 27 | 29 | 32 | 27 | 18 | 32 | 34 | 0 | 0
2022-02-11 22:00 | 2 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 15 | 27 | 29 | 32 | 24 | 17 | 30 | 36 | 0 | 0
2022-02-11 23:00 | 2 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 15 | 28 | 28 | 33 | 25 | 15 | 30 | 36 | 0 | 0
2022-02-12 | 2 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 16 | 27 | 28 | 34 | 25 | 15 | 30 | 36 | 0 | 0
2022-02-12 01:00 | 2 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 16 | 26 | 28 | 33 | 26 | 14 | 29 | 35 | 0 | 0
2022-02-12 02:00 | 2 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 13 | 26 | 28 | 34 | 26 | 14 | 30 | 37 | 0 | 0
2022-02-12 03:00 | 2 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 14 | 26 | 26 | 34 | 27 | 10 | 31 | 38 | 0 | 0
2022-02-12 04:00 | 2 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 13 | 26 | 26 | 34 | 28 | 7 | 30 | 39 | 0 | 0
2022-02-12 05:00 | 2 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 13 | 27 | 25 | 34 | 28 | 6 | 31 | 38 | 0 | 0
2022-02-12 06:00 | 2 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 13 | 28 | 25 | 34 | 28 | 9 | 32 | 39 | 0 | 0
2022-02-12 07:00 | 2 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 13 | 29 | 25 | 34 | 29 | 11 | 32 | 38 | 0 | 0
2022-02-12 08:00 | 2 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 16 | 29 | 27 | 34 | 29 | 13 | 33 | 39 | 0 | 0
2022-02-12 09:00 | 2 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 17 | 30 | 29 | 35 | 30 | 17 | 34 | 39 | 0 | 0
2022-02-12 10:00 | 2 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 21 | 30 | 30 | 36 | 32 | 20 | 33 | 39 | 0 | 0
2022-02-12 11:00 | 2 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 22 | 23 | 31 | 36 | 32 | 24 | 34 | 40 | 0 | 0
2022-02-12 12:00 | 2 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 24 | 22 | 32 | 35 | 33 | 26 | 33 | 40 | 0 | 0
2022-02-12 13:00 | 2 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 24 | 20 | 30 | 35 | 32 | 26 | 33 | 41 | 0 | 0
2022-02-12 14:00 | 2 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 24 | 19 | 31 | 35 | 33 | 28 | 32 | 40 | 0 | 0
2022-02-12 15:00 | 2 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 22 | 18 | 32 | 33 | 32 | 28 | 33 | 42 | 0 | 0
2022-02-12 16:00 | 2 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 22 | 17 | 31 | 31 | 31 | 27 | 33 | 39 | 0 | 0
2022-02-12 17:00 | 2 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 21 | 15 | 28 | 29 | 31 | 27 | 31 | 38 | 0 | 0
2022-02-12 18:00 | 2 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 20 | 12 | 26 | 28 | 30 | 26 | 29 | 37 | 0 | 0
2022-02-12 19:00 | 2 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 20 | 10 | 22 | 26 | 30 | 26 | 27 | 36 | 0 | 0
2022-02-12 20:00 | 2 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 20 | 10 | 22 | 25 | 30 | 25 | 24 | 35 | 0 | 0
2022-02-12 21:00 | 2 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 20 | 10 | 20 | 23 | 31 | 25 | 22 | 34 | 0 | 0
2022-02-12 22:00 | 2 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 20 | 9 | 19 | 22 | 31 | 24 | 20 | 34 | 0 | 0
2022-02-12 23:00 | 2 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 20 | 9 | 18 | 20 | 31 | 23 | 18 | 34 | 0 | 0
2022-02-13 | 2 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 19 | 9 | 19 | 19 | 31 | 22 | 16 | 33 | 0 | 0
2022-02-13 01:00 | 2 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 19 | 9 | 20 | 19 | 31 | 22 | 16 | 32 | 0 | 0
2022-02-13 02:00 | 2 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 18 | 9 | 21 | 19 | 30 | 22 | 16 | 32 | 0 | 0
2022-02-13 03:00 | 2 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 18 | 9 | 21 | 19 | 31 | 20 | 15 | 31 | 0 | 0
2022-02-13 04:00 | 2 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 18 | 9 | 23 | 19 | 31 | 20 | 15 | 31 | 0 | 0
2022-02-13 05:00 | 2 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 18 | 8 | 26 | 19 | 31 | 20 | 14 | 32 | 0 | 0
2022-02-13 06:00 | 2 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 18 | 8 | 27 | 19 | 31 | 19 | 15 | 32 | 0 | 0
2022-02-13 07:00 | 2 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 18 | 9 | 27 | 18 | 31 | 18 | 15 | 32 | 0 | 0
2022-02-13 08:00 | 2 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 18 | 9 | 29 | 19 | 33 | 18 | 16 | 32 | 0 | 0
2022-02-13 09:00 | 2 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 20 | 11 | 30 | 20 | 35 | 18 | 17 | 32 | 0 | 0
2022-02-13 10:00 | 2 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 22 | 12 | 33 | 21 | 37 | 19 | 18 | 32 | 0 | 0
2022-02-13 11:00 | 2 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 24 | 13 | 34 | 21 | 37 | 21 | 19 | 33 | 0 | 0
2022-02-13 12:00 | 2 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 23 | 12 | 33 | 21 | 40 | 22 | 20 | 33 | 0 | 0
2022-02-13 13:00 | 2 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 24 | 12 | 33 | 22 | 42 | 25 | 19 | 32 | 0 | 0
2022-02-13 14:00 | 2 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 22 | 13 | 35 | 22 | 44 | 27 | 20 | 32 | 0 | 0
2022-02-13 15:00 | 2 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 21 | 12 | 35 | 22 | 44 | 26 | 20 | 32 | 0 | 0
2022-02-13 16:00 | 2 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 19 | 12 | 37 | 22 | 42 | 26 | 20 | 31 | 0 | 0
2022-02-13 17:00 | 2 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 18 | 12 | 37 | 22 | 40 | 25 | 20 | 29 | 0 | 0
2022-02-13 18:00 | 2 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 16 | 12 | 40 | 21 | 39 | 22 | 19 | 29 | 0 | 0
2022-02-13 19:00 | 2 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 16 | 11 | 39 | 21 | 37 | 21 | 19 | 29 | 0 | 0
2022-02-13 20:00 | 2 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 16 | 12 | 41 | 21 | 35 | 19 | 19 | 28 | 0 | 0
2022-02-13 21:00 | 2 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 14 | 12 | 41 | 21 | 34 | 20 | 19 | 27 | 0 | 0
2022-02-13 22:00 | 2 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 14 | 11 | 40 | 21 | 32 | 18 | 20 | 26 | 0 | 0
2022-02-13 23:00 | 2 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 13 | 11 | 41 | 21 | 31 | 21 | 20 | 26 | 0 | 0
2022-02-14 | 2 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 14 | 10 | 42 | 20 | 30 | 22 | 20 | 26 | 0 | 0
2022-02-14 01:00 | 2 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 14 | 9 | 42 | 19 | 29 | 22 | 21 | 26 | 0 | 0
2022-02-14 02:00 | 2 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 14 | 8 | 42 | 19 | 28 | 22 | 21 | 25 | 0 | 0
2022-02-14 03:00 | 2 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 14 | 7 | 38 | 18 | 29 | 22 | 21 | 24 | 0 | 0
2022-02-14 04:00 | 2 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 15 | 7 | 38 | 18 | 27 | 22 | 20 | 23 | 0 | 0
2022-02-14 05:00 | 2 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 15 | 7 | 37 | 18 | 28 | 23 | 19 | 23 | 0 | 0
2022-02-14 06:00 | 2 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 15 | 4 | 36 | 17 | 27 | 24 | 18 | 24 | 0 | 0
2022-02-14 07:00 | 2 | 1 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 18 | 17 | 2 | 35 | 17 | 30 | 25 | 19 | 25 | 0 | 0
2022-02-14 08:00 | 2 | 1 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 19 | 5 | 35 | 19 | 33 | 26 | 20 | 25 | 0 | 0
2022-02-14 09:00 | 2 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 21 | 12 | 35 | 21 | 34 | 27 | 21 | 27 | 0 | 0
2022-02-14 10:00 | 2 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 23 | 18 | 37 | 23 | 33 | 29 | 22 | 29 | 0 | 0
2022-02-14 11:00 | 2 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 26 | 21 | 39 | 25 | 33 | 31 | 23 | 30 | 0 | 0
2022-02-14 12:00 | 2 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 26 | 25 | 38 | 28 | 33 | 33 | 24 | 31 | 0 | 0
2022-02-14 13:00 | 2 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 27 | 27 | 41 | 29 | 35 | 36 | 26 | 31 | 0 | 0
2022-02-14 14:00 | 2 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 28 | 28 | 38 | 33 | 34 | 37 | 28 | 33 | 0 | 0
2022-02-14 15:00 | 2 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 28 | 30 | 38 | 33 | 32 | 38 | 29 | 33 | 0 | 0
2022-02-14 16:00 | 2 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 26 | 29 | 38 | 34 | 31 | 38 | 28 | 32 | 0 | 0
2022-02-14 17:00 | 2 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 24 | 29 | 36 | 31 | 30 | 36 | 26 | 30 | 0 | 0
2022-02-14 18:00 | 2 | 1 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 22 | 27 | 34 | 30 | 29 | 35 | 24 | 28 | 0 | 0
2022-02-14 19:00 | 2 | 1 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 22 | 27 | 32 | 29 | 28 | 35 | 23 | 28 | 0 | 0
2022-02-14 20:00 | 2 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 22 | 27 | 32 | 27 | 28 | 33 | 24 | 27 | 0 | 0
2022-02-14 21:00 | 2 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 22 | 27 | 33 | 27 | 27 | 34 | 24 | 26 | 0 | 0
2022-02-14 22:00 | 2 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 24 | 29 | 33 | 29 | 25 | 35 | 23 | 25 | 0 | 0
2022-02-14 23:00 | 2 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 25 | 29 | 33 | 27 | 24 | 34 | 26 | 22 | 0 | 0
2022-02-15 | 2 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 26 | 31 | 34 | 25 | 24 | 33 | 27 | 22 | 0 | 0
2022-02-15 01:00 | 2 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 26 | 32 | 34 | 24 | 22 | 33 | 26 | 20 | 0 | 0
2022-02-15 02:00 | 2 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 28 | 32 | 33 | 24 | 22 | 36 | 29 | 19 | 0 | 0
2022-02-15 03:00 | 2 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 29 | 30 | 33 | 23 | 22 | 38 | 28 | 19 | 0 | 0
2022-02-15 04:00 | 2 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 29 | 32 | 34 | 25 | 23 | 43 | 28 | 18 | 0 | 0
2022-02-15 05:00 | 2 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 30 | 33 | 33 | 25 | 23 | 43 | 28 | 17 | 0 | 0
2022-02-15 06:00 | 2 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 30 | 33 | 33 | 24 | 23 | 43 | 29 | 18 | 0 | 0
2022-02-15 07:00 | 2 | 2 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 33 | 32 | 33 | 25 | 25 | 45 | 29 | 19 | 0 | 0
2022-02-15 08:00 | 2 | 2 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 37 | 33 | 33 | 36 | 29 | 45 | 32 | 21 | 0 | 0
2022-02-15 09:00 | 2 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 39 | 34 | 33 | 39 | 33 | 46 | 38 | 22 | 0 | 0
2022-02-15 10:00 | 2 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 42 | 36 | 35 | 43 | 38 | 47 | 40 | 23 | 0 | 0
2022-02-15 11:00 | 2 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 44 | 37 | 36 | 45 | 42 | 49 | 42 | 24 | 0 | 0
2022-02-15 12:00 | 2 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 44 | 38 | 34 | 46 | 46 | 52 | 42 | 25 | 0 | 0
2022-02-15 13:00 | 2 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 44 | 35 | 33 | 45 | 46 | 53 | 41 | 28 | 0 | 0
2022-02-15 14:00 | 2 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 47 | 35 | 33 | 44 | 47 | 53 | 41 | 26 | 0 | 0
2022-02-15 15:00 | 2 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 45 | 34 | 33 | 44 | 44 | 53 | 44 | 27 | 0 | 0
2022-02-15 16:00 | 2 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 44 | 34 | 33 | 44 | 43 | 52 | 42 | 25 | 0 | 0
2022-02-15 17:00 | 2 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 44 | 33 | 33 | 43 | 40 | 51 | 41 | 24 | 0 | 0
2022-02-15 18:00 | 2 | 2 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 44 | 32 | 33 | 41 | 39 | 50 | 41 | 23 | 0 | 0
2022-02-15 19:00 | 2 | 2 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 45 | 31 | 33 | 40 | 38 | 49 | 38 | 22 | 0 | 0
2022-02-15 20:00 | 2 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 44 | 30 | 32 | 40 | 37 | 47 | 39 | 22 | 0 | 0
2022-02-15 21:00 | 2 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 44 | 29 | 33 | 39 | 35 | 46 | 39 | 21 | 0 | 0
2022-02-15 22:00 | 2 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 43 | 28 | 33 | 39 | 37 | 45 | 38 | 21 | 0 | 0
2022-02-15 23:00 | 2 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 43 | 27 | 33 | 39 | 40 | 45 | 36 | 21 | 0 | 0
2022-02-16 | 2 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 42 | 26 | 32 | 37 | 40 | 45 | 37 | 21 | 0 | 0
2022-02-16 01:00 | 2 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 42 | 26 | 32 | 38 | 39 | 45 | 37 | 21 | 0 | 0
2022-02-16 02:00 | 2 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 42 | 26 | 31 | 39 | 38 | 45 | 36 | 20 | 0 | 0
2022-02-16 03:00 | 2 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 42 | 25 | 30 | 38 | 37 | 45 | 36 | 20 | 0 | 0
2022-02-16 04:00 | 2 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 40 | 22 | 29 | 34 | 39 | 44 | 34 | 20 | 0 | 0
2022-02-16 05:00 | 2 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 38 | 20 | 27 | 37 | 39 | 43 | 33 | 19 | 0 | 0
2022-02-16 06:00 | 2 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 38 | 20 | 25 | 36 | 37 | 44 | 33 | 18 | 0 | 0
2022-02-16 07:00 | 2 | 3 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 37 | 20 | 25 | 36 | 37 | 42 | 33 | 17 | 0 | 0
2022-02-16 08:00 | 2 | 3 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 37 | 20 | 25 | 36 | 39 | 44 | 33 | 19 | 0 | 0
2022-02-16 09:00 | 2 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 37 | 21 | 25 | 37 | 41 | 44 | 32 | 20 | 0 | 0
2022-02-16 10:00 | 2 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 36 | 23 | 26 | 37 | 42 | 45 | 30 | 21 | 0 | 0
2022-02-16 11:00 | 2 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 36 | 23 | 26 | 38 | 43 | 46 | 30 | 23 | 0 | 0
2022-02-16 12:00 | 2 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 37 | 23 | 26 | 39 | 44 | 45 | 31 | 25 | 0 | 0
2022-02-16 13:00 | 2 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 36 | 24 | 26 | 40 | 46 | 46 | 32 | 27 | 0 | 0
2022-02-16 14:00 | 2 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 38 | 26 | 27 | 39 | 47 | 46 | 32 | 28 | 0 | 0
2022-02-16 15:00 | 2 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 37 | 27 | 26 | 39 | 47 | 45 | 32 | 27 | 0 | 0
2022-02-16 16:00 | 2 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 36 | 25 | 24 | 38 | 45 | 44 | 32 | 28 | 0 | 0
2022-02-16 17:00 | 2 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 34 | 23 | 22 | 36 | 43 | 44 | 31 | 25 | 0 | 0
2022-02-16 18:00 | 2 | 3 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 33 | 21 | 22 | 34 | 40 | 43 | 30 | 25 | 0 | 0
2022-02-16 19:00 | 2 | 3 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 31 | 22 | 22 | 33 | 39 | 42 | 29 | 27 | 0 | 0
2022-02-16 20:00 | 2 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 30 | 23 | 21 | 32 | 36 | 42 | 28 | 26 | 0 | 0
2022-02-16 21:00 | 2 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 29 | 23 | 20 | 31 | 35 | 42 | 26 | 28 | 0 | 0
2022-02-16 22:00 | 2 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 28 | 22 | 20 | 31 | 33 | 41 | 24 | 27 | 0 | 0
2022-02-16 23:00 | 2 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 28 | 22 | 19 | 28 | 32 | 41 | 24 | 27 | 0 | 0
2022-02-17 | 2 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 27 | 22 | 18 | 29 | 31 | 41 | 23 | 28 | 0 | 0
2022-02-17 01:00 | 2 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 26 | 23 | 17 | 28 | 30 | 39 | 24 | 28 | 0 | 0
2022-02-17 02:00 | 2 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 26 | 23 | 16 | 26 | 30 | 38 | 24 | 29 | 0 | 0
2022-02-17 03:00 | 2 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 25 | 22 | 15 | 26 | 29 | 36 | 26 | 29 | 0 | 0
2022-02-17 04:00 | 2 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 24 | 22 | 15 | 25 | 26 | 35 | 28 | 30 | 0 | 0
2022-02-17 05:00 | 2 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 24 | 22 | 14 | 25 | 27 | 35 | 28 | 29 | 0 | 0
2022-02-17 06:00 | 2 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 24 | 20 | 13 | 25 | 25 | 35 | 29 | 28 | 0 | 0
2022-02-17 07:00 | 2 | 4 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 23 | 19 | 14 | 26 | 28 | 35 | 30 | 30 | 0 | 0
2022-02-17 08:00 | 2 | 4 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 23 | 25 | 18 | 32 | 30 | 35 | 32 | 37 | 0 | 0
2022-02-17 09:00 | 2 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 24 | 29 | 21 | 36 | 33 | 35 | 35 | 42 | 0 | 0
2022-02-17 10:00 | 2 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 25 | 33 | 24 | 39 | 37 | 35 | 36 | 40 | 0 | 0
2022-02-17 11:00 | 2 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 27 | 36 | 25 | 43 | 40 | 35 | 39 | 39 | 0 | 0
2022-02-17 12:00 | 2 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 27 | 40 | 25 | 45 | 42 | 35 | 40 | 40 | 0 | 0
2022-02-17 13:00 | 2 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 29 | 41 | 25 | 50 | 43 | 35 | 42 | 39 | 0 | 0
2022-02-17 14:00 | 2 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 30 | 41 | 24 | 51 | 46 | 35 | 44 | 39 | 0 | 0
2022-02-17 15:00 | 2 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 30 | 41 | 26 | 50 | 45 | 35 | 44 | 38 | 0 | 0
2022-02-17 16:00 | 2 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 29 | 39 | 23 | 50 | 42 | 34 | 43 | 37 | 0 | 0
2022-02-17 17:00 | 2 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 29 | 38 | 21 | 47 | 42 | 33 | 41 | 35 | 0 | 0
2022-02-17 18:00 | 2 | 4 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 27 | 35 | 22 | 42 | 40 | 33 | 39 | 30 | 0 | 0
2022-02-17 19:00 | 2 | 4 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 26 | 34 | 21 | 37 | 38 | 33 | 37 | 32 | 0 | 0
2022-02-17 20:00 | 2 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 26 | 31 | 20 | 34 | 37 | 32 | 36 | 30 | 0 | 0
2022-02-17 21:00 | 2 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 25 | 30 | 19 | 33 | 36 | 32 | 33 | 27 | 0 | 0
2022-02-17 22:00 | 2 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 24 | 28 | 18 | 33 | 34 | 31 | 34 | 29 | 0 | 0
2022-02-17 23:00 | 2 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 24 | 28 | 18 | 30 | 33 | 31 | 32 | 32 | 0 | 0
2022-02-18 | 2 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 24 | 26 | 18 | 30 | 33 | 31 | 33 | 31 | 0 | 0
2022-02-18 01:00 | 2 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 24 | 26 | 17 | 31 | 32 | 31 | 30 | 32 | 0 | 0
2022-02-18 02:00 | 2 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 24 | 26 | 16 | 33 | 32 | 31 | 33 | 30 | 0 | 0
2022-02-18 03:00 | 2 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 24 | 22 | 15 | 33 | 31 | 31 | 34 | 30 | 0 | 0
2022-02-18 04:00 | 2 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 24 | 20 | 14 | 34 | 30 | 31 | 33 | 29 | 0 | 0
2022-02-18 05:00 | 2 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 24 | 18 | 13 | 33 | 28 | 30 | 33 | 27 | 0 | 0
2022-02-18 06:00 | 2 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 23 | 16 | 11 | 33 | 29 | 30 | 32 | 26 | 0 | 0
2022-02-18 07:00 | 2 | 5 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 23 | 16 | 13 | 33 | 31 | 30 | 33 | 28 | 0 | 0
2022-02-18 08:00 | 2 | 5 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 24 | 21 | 17 | 38 | 37 | 30 | 34 | 31 | 0 | 0
2022-02-18 09:00 | 2 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 26 | 33 | 19 | 44 | 42 | 31 | 36 | 34 | 0 | 0
2022-02-18 10:00 | 2 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 27 | 38 | 22 | 44 | 48 | 31 | 36 | 36 | 0 | 0
2022-02-18 11:00 | 2 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 29 | 40 | 23 | 45 | 52 | 31 | 38 | 37 | 0 | 0
2022-02-18 12:00 | 2 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 32 | 40 | 23 | 47 | 55 | 32 | 40 | 39 | 0 | 0
2022-02-18 13:00 | 2 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 33 | 40 | 23 | 48 | 57 | 32 | 41 | 43 | 0 | 0
2022-02-18 14:00 | 2 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 34 | 41 | 23 | 49 | 53 | 33 | 42 | 45 | 0 | 0
2022-02-18 15:00 | 2 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 36 | 41 | 22 | 50 | 54 | 33 | 43 | 45 | 0 | 0
2022-02-18 16:00 | 2 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 33 | 40 | 20 | 47 | 53 | 34 | 42 | 43 | 0 | 0
2022-02-18 17:00 | 2 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 32 | 36 | 20 | 43 | 48 | 34 | 39 | 38 | 0 | 0
2022-02-18 18:00 | 2 | 5 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 31 | 30 | 20 | 36 | 44 | 34 | 39 | 34 | 0 | 0
2022-02-18 19:00 | 2 | 5 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 31 | 27 | 20 | 34 | 44 | 35 | 34 | 35 | 0 | 0
2022-02-18 20:00 | 2 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 30 | 24 | 20 | 32 | 42 | 35 | 33 | 39 | 0 | 0
2022-02-18 21:00 | 2 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 30 | 23 | 20 | 31 | 37 | 35 | 31 | 38 | 0 | 0
2022-02-18 22:00 | 2 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 30 | 25 | 20 | 29 | 38 | 35 | 30 | 38 | 0 | 0
2022-02-18 23:00 | 2 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 29 | 22 | 20 | 28 | 35 | 35 | 28 | 37 | 0 | 0
2022-02-19 | 2 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 28 | 24 | 20 | 28 | 34 | 35 | 27 | 37 | 0 | 0
2022-02-19 01:00 | 2 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 28 | 24 | 19 | 26 | 31 | 35 | 27 | 37 | 0 | 0
2022-02-19 02:00 | 2 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 27 | 25 | 20 | 27 | 30 | 35 | 27 | 36 | 0 | 0
2022-02-19 03:00 | 2 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 26 | 25 | 19 | 28 | 32 | 35 | 25 | 36 | 0 | 0
2022-02-19 04:00 | 2 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 26 | 27 | 19 | 29 | 30 | 35 | 26 | 36 | 0 | 0
2022-02-19 05:00 | 2 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 27 | 28 | 19 | 31 | 30 | 35 | 24 | 37 | 0 | 0
2022-02-19 06:00 | 2 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 27 | 30 | 18 | 32 | 30 | 36 | 24 | 39 | 0 | 0
2022-02-19 07:00 | 2 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 28 | 31 | 18 | 33 | 33 | 37 | 25 | 38 | 0 | 0
2022-02-19 08:00 | 2 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 29 | 32 | 24 | 34 | 38 | 36 | 29 | 40 | 0 | 0
2022-02-19 09:00 | 2 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 30 | 32 | 26 | 34 | 45 | 35 | 34 | 40 | 0 | 0
2022-02-19 10:00 | 2 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 30 | 31 | 28 | 36 | 49 | 34 | 35 | 40 | 0 | 0
2022-02-19 11:00 | 2 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 31 | 34 | 29 | 40 | 51 | 33 | 38 | 41 | 0 | 0
2022-02-19 12:00 | 2 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 31 | 33 | 31 | 41 | 54 | 34 | 37 | 41 | 0 | 0
2022-02-19 13:00 | 2 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 31 | 32 | 33 | 40 | 56 | 34 | 38 | 42 | 0 | 0
2022-02-19 14:00 | 2 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 31 | 32 | 31 | 34 | 57 | 34 | 39 | 42 | 0 | 0
2022-02-19 15:00 | 2 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 31 | 32 | 30 | 34 | 57 | 34 | 37 | 41 | 0 | 0
2022-02-19 16:00 | 2 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 31 | 31 | 29 | 34 | 57 | 33 | 33 | 39 | 0 | 0
2022-02-19 17:00 | 2 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 31 | 31 | 29 | 34 | 54 | 32 | 33 | 34 | 0 | 0
2022-02-19 18:00 | 2 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 32 | 32 | 29 | 35 | 52 | 32 | 35 | 32 | 0 | 0
2022-02-19 19:00 | 2 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 31 | 32 | 32 | 36 | 48 | 32 | 36 | 31 | 0 | 0
2022-02-19 20:00 | 2 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 31 | 33 | 33 | 37 | 47 | 32 | 37 | 29 | 0 | 0
2022-02-19 21:00 | 2 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 31 | 33 | 34 | 35 | 45 | 32 | 38 | 29 | 0 | 0
2022-02-19 22:00 | 2 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 31 | 33 | 35 | 35 | 44 | 32 | 38 | 25 | 0 | 0
2022-02-19 23:00 | 2 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 30 | 34 | 35 | 35 | 44 | 32 | 37 | 27 | 0 | 0
2022-02-20 | 2 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 35 | 35 | 35 | 42 | 32 | 36 | 22 | 0 | 0
2022-02-20 01:00 | 2 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 36 | 35 | 35 | 42 | 32 | 36 | 22 | 0 | 0
2022-02-20 02:00 | 2 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 37 | 35 | 35 | 38 | 32 | 36 | 19 | 0 | 0
2022-02-20 03:00 | 2 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 29 | 36 | 35 | 34 | 36 | 32 | 38 | 20 | 0 | 0
2022-02-20 04:00 | 2 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 29 | 34 | 35 | 34 | 36 | 32 | 39 | 21 | 0 | 0
2022-02-20 05:00 | 2 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 29 | 33 | 35 | 35 | 35 | 32 | 38 | 21 | 0 | 0
2022-02-20 06:00 | 2 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 32 | 32 | 35 | 35 | 32 | 38 | 21 | 0 | 0
2022-02-20 07:00 | 2 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 29 | 31 | 33 | 35 | 39 | 32 | 37 | 22 | 0 | 0
2022-02-20 08:00 | 2 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 30 | 31 | 34 | 35 | 43 | 32 | 37 | 27 | 0 | 0
2022-02-20 09:00 | 2 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 32 | 32 | 35 | 36 | 49 | 33 | 37 | 30 | 0 | 0
2022-02-20 10:00 | 2 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 32 | 34 | 37 | 39 | 53 | 34 | 38 | 33 | 0 | 0
2022-02-20 11:00 | 2 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 33 | 35 | 38 | 43 | 54 | 36 | 41 | 37 | 0 | 0
2022-02-20 12:00 | 2 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 34 | 34 | 39 | 45 | 58 | 37 | 42 | 39 | 0 | 0
2022-02-20 13:00 | 2 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 35 | 34 | 39 | 47 | 59 | 38 | 42 | 40 | 0 | 0
2022-02-20 14:00 | 2 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 34 | 33 | 42 | 49 | 58 | 39 | 42 | 41 | 0 | 0
2022-02-20 15:00 | 2 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 34 | 32 | 39 | 50 | 60 | 40 | 43 | 43 | 0 | 0
2022-02-20 16:00 | 2 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 33 | 32 | 37 | 49 | 60 | 40 | 43 | 42 | 0 | 0
2022-02-20 17:00 | 2 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 32 | 29 | 36 | 46 | 56 | 40 | 41 | 37 | 0 | 0
2022-02-20 18:00 | 2 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 32 | 31 | 36 | 45 | 54 | 41 | 41 | 33 | 0 | 0
2022-02-20 19:00 | 2 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 32 | 26 | 36 | 42 | 53 | 41 | 38 | 28 | 0 | 0
2022-02-20 20:00 | 2 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 31 | 24 | 37 | 40 | 50 | 42 | 37 | 27 | 0 | 0
2022-02-20 21:00 | 2 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 31 | 22 | 37 | 40 | 49 | 42 | 37 | 27 | 0 | 0
2022-02-20 22:00 | 2 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 31 | 18 | 38 | 37 | 50 | 38 | 36 | 25 | 0 | 0
2022-02-20 23:00 | 2 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 30 | 16 | 38 | 37 | 46 | 37 | 34 | 23 | 0 | 0
2022-02-21 | 2 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 30 | 14 | 39 | 36 | 44 | 37 | 33 | 23 | 0 | 0
2022-02-21 01:00 | 2 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 30 | 10 | 40 | 33 | 45 | 35 | 31 | 22 | 0 | 0
2022-02-21 02:00 | 2 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 30 | 7 | 40 | 32 | 43 | 35 | 29 | 19 | 0 | 0
2022-02-21 03:00 | 2 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 30 | 5 | 37 | 29 | 42 | 34 | 27 | 20 | 0 | 0
2022-02-21 04:00 | 2 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 29 | 3 | 36 | 28 | 42 | 33 | 24 | 18 | 0 | 0
2022-02-21 05:00 | 2 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 30 | 1 | 36 | 26 | 41 | 33 | 22 | 19 | 0 | 0
2022-02-21 06:00 | 2 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 30 | 0 | 36 | 22 | 42 | 33 | 19 | 18 | 0 | 0
2022-02-21 07:00 | 2 | 1 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 30 | 1 | 36 | 21 | 43 | 32 | 18 | 20 | 0 | 0
2022-02-21 08:00 | 2 | 1 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 30 | 3 | 38 | 21 | 44 | 32 | 15 | 24 | 0 | 0
2022-02-21 09:00 | 2 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 31 | 5 | 39 | 21 | 46 | 32 | 15 | 29 | 0 | 0
2022-02-21 10:00 | 2 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 32 | 5 | 41 | 22 | 48 | 32 | 16 | 32 | 0 | 0
2022-02-21 11:00 | 2 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 33 | 7 | 40 | 23 | 50 | 32 | 16 | 41 | 0 | 0
2022-02-21 12:00 | 2 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 34 | 9 | 37 | 24 | 52 | 33 | 18 | 43 | 0 | 0
2022-02-21 13:00 | 2 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 35 | 9 | 34 | 25 | 52 | 34 | 19 | 44 | 0 | 0
2022-02-21 14:00 | 2 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 34 | 12 | 34 | 25 | 51 | 33 | 19 | 45 | 0 | 0
2022-02-21 15:00 | 2 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 33 | 13 | 34 | 26 | 51 | 35 | 20 | 46 | 0 | 0
2022-02-21 16:00 | 2 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 33 | 12 | 33 | 25 | 51 | 35 | 20 | 45 | 0 | 0
2022-02-21 17:00 | 2 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 32 | 11 | 33 | 24 | 50 | 34 | 18 | 45 | 0 | 0
2022-02-21 18:00 | 2 | 1 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 33 | 10 | 33 | 22 | 49 | 33 | 17 | 45 | 0 | 0
2022-02-21 19:00 | 2 | 1 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 32 | 8 | 33 | 21 | 48 | 33 | 16 | 45 | 0 | 0
2022-02-21 20:00 | 2 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 32 | 8 | 33 | 20 | 48 | 32 | 18 | 44 | 0 | 0
2022-02-21 21:00 | 2 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 31 | 8 | 32 | 19 | 46 | 32 | 17 | 42 | 0 | 0
2022-02-21 22:00 | 2 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 31 | 10 | 32 | 17 | 47 | 32 | 17 | 43 | 0 | 0
2022-02-21 23:00 | 2 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 30 | 11 | 32 | 15 | 45 | 32 | 16 | 42 | 0 | 0
2022-02-22 | 2 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 30 | 11 | 32 | 15 | 43 | 32 | 16 | 42 | 0 | 0
2022-02-22 01:00 | 2 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 29 | 12 | 31 | 15 | 40 | 32 | 15 | 41 | 0 | 0
2022-02-22 02:00 | 2 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 27 | 12 | 31 | 15 | 39 | 32 | 13 | 42 | 0 | 0
2022-02-22 03:00 | 2 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 28 | 13 | 31 | 15 | 42 | 32 | 13 | 40 | 0 | 0
2022-02-22 04:00 | 2 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 26 | 14 | 31 | 14 | 41 | 32 | 13 | 41 | 0 | 0
2022-02-22 05:00 | 2 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 25 | 17 | 31 | 20 | 40 | 32 | 14 | 42 | 0 | 0
2022-02-22 06:00 | 2 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 25 | 19 | 31 | 24 | 38 | 32 | 17 | 41 | 0 | 0
2022-02-22 07:00 | 2 | 2 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 25 | 21 | 30 | 25 | 39 | 32 | 20 | 42 | 0 | 0
2022-02-22 08:00 | 2 | 2 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 27 | 24 | 30 | 29 | 40 | 33 | 24 | 40 | 0 | 0
2022-02-22 09:00 | 2 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 28 | 29 | 30 | 33 | 42 | 33 | 30 | 41 | 0 | 0
2022-02-22 10:00 | 2 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 29 | 32 | 30 | 38 | 44 | 34 | 34 | 43 | 0 | 0
2022-02-22 11:00 | 2 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 31 | 38 | 30 | 41 | 45 | 35 | 36 | 44 | 0 | 0
2022-02-22 12:00 | 2 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 31 | 42 | 32 | 44 | 47 | 36 | 39 | 44 | 0 | 0
2022-02-22 13:00 | 2 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 31 | 45 | 33 | 46 | 48 | 35 | 41 | 45 | 0 | 0
2022-02-22 14:00 | 2 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 31 | 46 | 32 | 47 | 49 | 35 | 41 | 46 | 0 | 0
2022-02-22 15:00 | 2 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 30 | 49 | 30 | 49 | 48 | 35 | 40 | 45 | 0 | 0
2022-02-22 16:00 | 2 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 29 | 48 | 30 | 48 | 47 | 35 | 40 | 45 | 0 | 0
2022-02-22 17:00 | 2 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 29 | 45 | 28 | 47 | 44 | 34 | 39 | 43 | 0 | 0
2022-02-22 18:00 | 2 | 2 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 28 | 47 | 27 | 46 | 44 | 34 | 38 | 42 | 0 | 0
2022-02-22 19:00 | 2 | 2 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 28 | 47 | 25 | 45 | 42 | 34 | 38 | 41 | 0 | 0
2022-02-22 20:00 | 2 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 28 | 44 | 24 | 45 | 40 | 33 | 39 | 42 | 0 | 0
2022-02-22 21:00 | 2 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 27 | 44 | 22 | 47 | 40 | 33 | 40 | 41 | 0 | 0
2022-02-22 22:00 | 2 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 27 | 46 | 21 | 47 | 38 | 33 | 40 | 40 | 0 | 0
2022-02-22 23:00 | 2 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 27 | 47 | 19 | 47 | 38 | 32 | 40 | 40 | 0 | 0
2022-02-23 | 2 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 27 | 47 | 17 | 47 | 37 | 31 | 40 | 39 | 0 | 0
2022-02-23 01:00 | 2 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 27 | 43 | 17 | 46 | 37 | 31 | 41 | 39 | 0 | 0
2022-02-23 02:00 | 2 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 28 | 35 | 16 | 45 | 37 | 30 | 41 | 38 | 0 | 0
2022-02-23 03:00 | 2 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 27 | 33 | 15 | 45 | 36 | 29 | 41 | 40 | 0 | 0
2022-02-23 04:00 | 2 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 27 | 33 | 15 | 45 | 33 | 29 | 42 | 39 | 0 | 0
2022-02-23 05:00 | 2 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 27 | 32 | 14 | 45 | 32 | 29 | 41 | 40 | 0 | 0
2022-02-23 06:00 | 2 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 28 | 32 | 13 | 44 | 32 | 30 | 39 | 38 | 0 | 0
2022-02-23 07:00 | 2 | 3 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 28 | 32 | 13 | 45 | 33 | 32 | 42 | 42 | 0 | 0
2022-02-23 08:00 | 2 | 3 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 31 | 32 | 13 | 47 | 35 | 35 | 45 | 45 | 0 | 0
2022-02-23 09:00 | 2 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 32 | 32 | 14 | 49 | 34 | 39 | 47 | 46 | 0 | 0
2022-02-23 10:00 | 2 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 33 | 33 | 14 | 50 | 34 | 43 | 45 | 54 | 0 | 0
2022-02-23 11:00 | 2 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 37 | 32 | 15 | 47 | 35 | 45 | 43 | 58 | 0 | 0
2022-02-23 12:00 | 2 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 39 | 33 | 14 | 43 | 36 | 49 | 40 | 63 | 0 | 0
2022-02-23 13:00 | 2 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 38 | 34 | 15 | 40 | 36 | 50 | 38 | 69 | 0 | 0
2022-02-23 14:00 | 2 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 38 | 31 | 16 | 40 | 37 | 53 | 37 | 70 | 0 | 0
2022-02-23 15:00 | 2 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 38 | 32 | 17 | 40 | 37 | 53 | 37 | 70 | 0 | 0
2022-02-23 16:00 | 2 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 36 | 30 | 15 | 40 | 37 | 52 | 37 | 68 | 0 | 0
2022-02-23 17:00 | 2 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 34 | 29 | 13 | 40 | 37 | 49 | 37 | 58 | 0 | 0
2022-02-23 18:00 | 2 | 3 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 33 | 26 | 12 | 39 | 36 | 40 | 36 | 58 | 0 | 0
2022-02-23 19:00 | 2 | 3 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 33 | 25 | 12 | 40 | 35 | 38 | 36 | 56 | 0 | 0
2022-02-23 20:00 | 2 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 33 | 24 | 12 | 39 | 35 | 36 | 35 | 53 | 0 | 0
2022-02-23 21:00 | 2 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 32 | 24 | 12 | 38 | 34 | 35 | 34 | 50 | 0 | 0
2022-02-23 22:00 | 2 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 31 | 23 | 12 | 37 | 34 | 35 | 34 | 47 | 0 | 0
2022-02-23 23:00 | 2 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 30 | 22 | 11 | 37 | 34 | 34 | 34 | 45 | 0 | 0
2022-02-24 | 2 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 28 | 19 | 11 | 37 | 34 | 34 | 31 | 44 | 0 | 0
2022-02-24 01:00 | 2 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 24 | 17 | 12 | 36 | 34 | 34 | 30 | 42 | 0 | 0
2022-02-24 02:00 | 2 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 20 | 14 | 12 | 33 | 34 | 34 | 30 | 40 | 0 | 0
2022-02-24 03:00 | 2 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 18 | 10 | 11 | 32 | 34 | 34 | 28 | 39 | 0 | 0
2022-02-24 04:00 | 2 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 17 | 8 | 10 | 31 | 34 | 34 | 27 | 39 | 0 | 0
2022-02-24 05:00 | 2 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 17 | 10 | 10 | 30 | 34 | 33 | 26 | 33 | 0 | 0
2022-02-24 06:00 | 2 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 16 | 15 | 12 | 29 | 34 | 32 | 25 | 33 | 0 | 0
2022-02-24 07:00 | 2 | 4 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 15 | 15 | 13 | 28 | 34 | 32 | 25 | 36 | 0 | 0
2022-02-24 08:00 | 2 | 4 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 15 | 17 | 14 | 29 | 36 | 32 | 24 | 39 | 0 | 0
2022-02-24 09:00 | 2 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 16 | 19 | 15 | 32 | 36 | 33 | 27 | 45 | 0 | 0
2022-02-24 10:00 | 2 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 18 | 21 | 15 | 33 | 36 | 34 | 28 | 52 | 0 | 0
2022-02-24 11:00 | 2 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 19 | 22 | 16 | 35 | 38 | 35 | 28 | 56 | 0 | 0
2022-02-24 12:00 | 2 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 18 | 22 | 18 | 33 | 42 | 35 | 30 | 64 | 0 | 0
2022-02-24 13:00 | 2 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 19 | 23 | 18 | 36 | 45 | 36 | 31 | 70 | 0 | 0
2022-02-24 14:00 | 2 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 19 | 22 | 18 | 35 | 45 | 35 | 31 | 68 | 0 | 0
2022-02-24 15:00 | 2 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 18 | 21 | 18 | 34 | 43 | 35 | 30 | 68 | 0 | 0
2022-02-24 16:00 | 2 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 18 | 21 | 16 | 33 | 42 | 34 | 30 | 67 | 0 | 0
2022-02-24 17:00 | 2 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 16 | 19 | 15 | 33 | 40 | 31 | 29 | 67 | 0 | 0
2022-02-24 18:00 | 2 | 4 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 16 | 18 | 14 | 31 | 39 | 30 | 28 | 64 | 0 | 0
2022-02-24 19:00 | 2 | 4 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 15 | 18 | 13 | 30 | 38 | 28 | 27 | 65 | 0 | 0
2022-02-24 20:00 | 2 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 15 | 17 | 11 | 28 | 36 | 26 | 26 | 65 | 0 | 0
2022-02-24 21:00 | 2 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 14 | 17 | 9 | 28 | 35 | 22 | 25 | 64 | 0 | 0
2022-02-24 22:00 | 2 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 14 | 17 | 9 | 26 | 33 | 21 | 25 | 58 | 0 | 0
2022-02-24 23:00 | 2 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 12 | 17 | 9 | 28 | 32 | 19 | 24 | 56 | 0 | 0
2022-02-25 | 2 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 11 | 16 | 9 | 27 | 31 | 18 | 22 | 55 | 0 | 0
2022-02-25 01:00 | 2 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 9 | 15 | 10 | 24 | 30 | 17 | 23 | 51 | 0 | 0
2022-02-25 02:00 | 2 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 8 | 15 | 11 | 24 | 30 | 17 | 23 | 45 | 0 | 0
2022-02-25 03:00 | 2 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 7 | 13 | 10 | 24 | 29 | 18 | 22 | 43 | 0 | 0
2022-02-25 04:00 | 2 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 6 | 12 | 9 | 25 | 29 | 17 | 21 | 39 | 0 | 0
2022-02-25 05:00 | 2 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 4 | 12 | 9 | 24 | 29 | 17 | 21 | 39 | 0 | 0
2022-02-25 06:00 | 2 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 3 | 11 | 9 | 24 | 29 | 17 | 21 | 39 | 0 | 0
2022-02-25 07:00 | 2 | 5 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 4 | 10 | 11 | 26 | 28 | 16 | 21 | 40 | 0 | 0
2022-02-25 08:00 | 2 | 5 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 6 | 13 | 16 | 28 | 32 | 16 | 23 | 41 | 0 | 0
2022-02-25 09:00 | 2 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 8 | 15 | 21 | 29 | 33 | 17 | 20 | 41 | 0 | 0
2022-02-25 10:00 | 2 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 11 | 16 | 24 | 29 | 34 | 20 | 21 | 44 | 0 | 0
2022-02-25 11:00 | 2 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 15 | 19 | 24 | 29 | 36 | 23 | 23 | 47 | 0 | 0
2022-02-25 12:00 | 2 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 15 | 20 | 26 | 30 | 37 | 26 | 24 | 49 | 0 | 0
2022-02-25 13:00 | 2 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 15 | 21 | 27 | 32 | 39 | 26 | 26 | 50 | 0 | 0
2022-02-25 14:00 | 2 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 16 | 19 | 29 | 32 | 39 | 26 | 26 | 50 | 0 | 0
2022-02-25 15:00 | 2 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 16 | 19 | 27 | 31 | 38 | 25 | 26 | 49 | 0 | 0
2022-02-25 16:00 | 2 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 14 | 18 | 27 | 30 | 37 | 25 | 25 | 48 | 0 | 0
2022-02-25 17:00 | 2 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 11 | 16 | 27 | 29 | 35 | 23 | 24 | 44 | 0 | 0
2022-02-25 18:00 | 2 | 5 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 10 | 13 | 27 | 28 | 37 | 20 | 23 | 41 | 0 | 0
2022-02-25 19:00 | 2 | 5 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 9 | 11 | 28 | 26 | 35 | 19 | 22 | 39 | 0 | 0
2022-02-25 20:00 | 2 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 9 | 10 | 29 | 26 | 35 | 17 | 20 | 37 | 0 | 0
2022-02-25 21:00 | 2 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 8 | 13 | 29 | 24 | 35 | 16 | 20 | 35 | 0 | 0
2022-02-25 22:00 | 2 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 7 | 13 | 29 | 23 | 35 | 15 | 18 | 33 | 0 | 0
2022-02-25 23:00 | 2 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 8 | 13 | 30 | 24 | 34 | 14 | 15 | 35 | 0 | 0
2022-02-26 | 2 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 7 | 13 | 30 | 26 | 33 | 11 | 14 | 35 | 0 | 0
2022-02-26 01:00 | 2 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 9 | 10 | 31 | 26 | 34 | 11 | 19 | 38 | 0 | 0
2022-02-26 02:00 | 2 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 8 | 10 | 31 | 26 | 34 | 11 | 19 | 41 | 0 | 0
2022-02-26 03:00 | 2 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 8 | 12 | 33 | 25 | 35 | 10 | 17 | 41 | 0 | 0
2022-02-26 04:00 | 2 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 7 | 12 | 33 | 25 | 33 | 9 | 15 | 40 | 0 | 0
2022-02-26 05:00 | 2 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 6 | 10 | 33 | 25 | 33 | 8 | 14 | 41 | 0 | 0
2022-02-26 06:00 | 2 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 3 | 11 | 33 | 23 | 34 | 9 | 14 | 41 | 0 | 0
2022-02-26 07:00 | 2 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 6 | 14 | 33 | 25 | 33 | 10 | 17 | 42 | 0 | 0
2022-02-26 08:00 | 2 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 11 | 15 | 33 | 27 | 34 | 14 | 20 | 43 | 0 | 0
2022-02-26 09:00 | 2 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 15 | 18 | 34 | 28 | 34 | 19 | 22 | 43 | 0 | 0
2022-02-26 10:00 | 2 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 19 | 20 | 34 | 28 | 34 | 22 | 24 | 44 | 0 | 0
2022-02-26 11:00 | 2 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 22 | 21 | 33 | 31 | 34 | 26 | 27 | 45 | 0 | 0
2022-02-26 12:00 | 2 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 24 | 21 | 33 | 34 | 35 | 29 | 28 | 47 | 0 | 0
2022-02-26 13:00 | 2 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 25 | 22 | 33 | 36 | 35 | 32 | 28 | 47 | 0 | 0
2022-02-26 14:00 | 2 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 26 | 23 | 33 | 35 | 34 | 32 | 28 | 49 | 0 | 0
2022-02-26 15:00 | 2 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 26 | 21 | 32 | 34 | 33 | 34 | 29 | 49 | 0 | 0
2022-02-26 16:00 | 2 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 26 | 20 | 32 | 35 | 31 | 33 | 29 | 48 | 0 | 0
2022-02-26 17:00 | 2 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 23 | 19 | 31 | 33 | 29 | 32 | 28 | 47 | 0 | 0
2022-02-26 18:00 | 2 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 22 | 21 | 30 | 33 | 29 | 29 | 26 | 48 | 0 | 0
2022-02-26 19:00 | 2 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 20 | 21 | 31 | 33 | 28 | 28 | 25 | 48 | 0 | 0
2022-02-26 20:00 | 2 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 20 | 21 | 30 | 33 | 26 | 26 | 25 | 47 | 0 | 0
2022-02-26 21:00 | 2 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 19 | 22 | 30 | 32 | 24 | 22 | 24 | 47 | 0 | 0
2022-02-26 22:00 | 2 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 17 | 23 | 30 | 32 | 25 | 24 | 25 | 46 | 0 | 0
2022-02-26 23:00 | 2 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 16 | 25 | 29 | 31 | 24 | 24 | 25 | 44 | 0 | 0
2022-02-27 | 2 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 15 | 26 | 29 | 31 | 21 | 21 | 25 | 43 | 0 | 0
2022-02-27 01:00 | 2 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 15 | 27 | 29 | 32 | 19 | 19 | 26 | 43 | 0 | 0
2022-02-27 02:00 | 2 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 15 | 27 | 28 | 31 | 18 | 22 | 26 | 44 | 0 | 0
2022-02-27 03:00 | 2 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 16 | 25 | 27 | 31 | 18 | 22 | 26 | 40 | 0 | 0
2022-02-27 04:00 | 2 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 16 | 24 | 26 | 31 | 16 | 20 | 26 | 35 | 0 | 0
2022-02-27 05:00 | 2 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 13 | 26 | 26 | 31 | 15 | 19 | 26 | 33 | 0 | 0
2022-02-27 06:00 | 2 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 13 | 26 | 25 | 31 | 14 | 20 | 26 | 35 | 0 | 0
2022-02-27 07:00 | 2 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 17 | 26 | 25 | 31 | 15 | 21 | 27 | 36 | 0 | 0
2022-02-27 08:00 | 2 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 20 | 29 | 25 | 32 | 17 | 23 | 28 | 41 | 0 | 0
2022-02-27 09:00 | 2 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 22 | 31 | 26 | 33 | 19 | 26 | 29 | 45 | 0 | 0
2022-02-27 10:00 | 2 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 25 | 32 | 27 | 34 | 22 | 33 | 29 | 45 | 0 | 0
2022-02-27 11:00 | 2 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 28 | 32 | 29 | 35 | 24 | 36 | 30 | 44 | 0 | 0
2022-02-27 12:00 | 2 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 30 | 28 | 30 | 34 | 26 | 39 | 31 | 43 | 0 | 0
2022-02-27 13:00 | 2 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 31 | 29 | 30 | 33 | 27 | 39 | 32 | 42 | 0 | 0
2022-02-27 14:00 | 2 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 32 | 27 | 29 | 33 | 28 | 40 | 32 | 39 | 0 | 0
2022-02-27 15:00 | 2 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 32 | 26 | 29 | 33 | 29 | 40 | 31 | 37 | 0 | 0
2022-02-27 16:00 | 2 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 31 | 24 | 29 | 33 | 28 | 41 | 31 | 35 | 0 | 0
2022-02-27 17:00 | 2 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 29 | 23 | 26 | 33 | 26 | 38 | 30 | 32 | 0 | 0
2022-02-27 18:00 | 2 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 26 | 22 | 26 | 33 | 25 | 35 | 29 | 30 | 0 | 0
2022-02-27 19:00 | 2 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 24 | 21 | 26 | 33 | 25 | 32 | 29 | 28 | 0 | 0
2022-02-27 20:00 | 2 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 24 | 21 | 26 | 34 | 25 | 32 | 28 | 25 | 0 | 0
2022-02-27 21:00 | 2 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 22 | 20 | 26 | 34 | 24 | 28 | 28 | 24 | 0 | 0
2022-02-27 22:00 | 2 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 21 | 20 | 25 | 34 | 23 | 28 | 27 | 23 | 0 | 0
2022-02-27 23:00 | 2 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 20 | 18 | 24 | 33 | 22 | 28 | 26 | 23 | 0 | 0
2022-02-28 | 2 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 21 | 16 | 24 | 32 | 21 | 29 | 26 | 21 | 0 | 0
2022-02-28 01:00 | 2 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 18 | 12 | 24 | 32 | 19 | 28 | 26 | 20 | 0 | 0
2022-02-28 02:00 | 2 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 18 | 7 | 24 | 31 | 19 | 26 | 26 | 20 | 0 | 0
2022-02-28 03:00 | 2 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 19 | 8 | 23 | 31 | 18 | 25 | 27 | 19 | 0 | 0
2022-02-28 04:00 | 2 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 20 | 8 | 22 | 31 | 17 | 25 | 26 | 18 | 0 | 0
2022-02-28 05:00 | 2 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 18 | 3 | 22 | 30 | 17 | 24 | 25 | 17 | 0 | 0
2022-02-28 06:00 | 2 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 18 | 2 | 23 | 30 | 16 | 23 | 24 | 17 | 0 | 0
2022-02-28 07:00 | 2 | 1 | 8 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 19 | 4 | 23 | 29 | 18 | 25 | 25 | 19 | 0 | 0
2022-02-28 08:00 | 2 | 1 | 9 | 1 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 24 | 14 | 26 | 31 | 21 | 30 | 25 | 21 | 0 | 0
2022-02-28 09:00 | 2 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 25 | 22 | 29 | 32 | 23 | 33 | 25 | 23 | 0 | 0
2022-02-28 10:00 | 2 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 25 | 28 | 33 | 33 | 26 | 38 | 29 | 27 | 0 | 0
2022-02-28 11:00 | 2 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 27 | 29 | 33 | 35 | 29 | 42 | 30 | 31 | 0 | 0
2022-02-28 12:00 | 2 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 28 | 34 | 33 | 37 | 31 | 45 | 31 | 33 | 0 | 0
2022-02-28 13:00 | 2 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 29 | 32 | 33 | 38 | 32 | 45 | 33 | 37 | 0 | 0
2022-02-28 14:00 | 2 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 28 | 34 | 32 | 37 | 34 | 46 | 32 | 40 | 0 | 0
2022-02-28 15:00 | 2 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 29 | 33 | 31 | 40 | 34 | 46 | 34 | 42 | 0 | 0
2022-02-28 16:00 | 2 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 26 | 33 | 31 | 39 | 32 | 44 | 34 | 41 | 0 | 0
2022-02-28 17:00 | 2 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 22 | 31 | 29 | 37 | 30 | 42 | 32 | 37 | 0 | 0
2022-02-28 18:00 | 2 | 1 | 19 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 20 | 28 | 29 | 34 | 30 | 38 | 28 | 35 | 0 | 0
2022-02-28 19:00 | 2 | 1 | 20 | 1 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 18 | 28 | 29 | 33 | 29 | 37 | 28 | 32 | 0 | 0
2022-02-28 20:00 | 2 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 17 | 27 | 29 | 33 | 29 | 36 | 28 | 28 | 0 | 0
2022-02-28 21:00 | 2 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 17 | 25 | 29 | 32 | 31 | 33 | 25 | 27 | 0 | 0
2022-02-28 22:00 | 2 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 17 | 23 | 30 | 31 | 32 | 30 | 21 | 25 | 0 | 0
2022-02-28 23:00 | 2 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 17 | 20 | 30 | 31 | 33 | 27 | 17 | 24 | 0 | 0
2022-03-01 | 3 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 17 | 18 | 30 | 30 | 35 | 24 | 14 | 22 | 0 | 0
2022-03-01 01:00 | 3 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 17 | 16 | 31 | 29 | 36 | 21 | 10 | 21 | 0 | 0
2022-03-01 02:00 | 3 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 17 | 13 | 31 | 28 | 38 | 18 | 7 | 20 | 0 | 0
2022-03-01 03:00 | 3 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 17 | 11 | 31 | 27 | 39 | 15 | 3 | 18 | 0 | 0
2022-03-01 04:00 | 3 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 17 | 7 | 32 | 27 | 36 | 15 | 2 | 17 | 0 | 0
2022-03-01 05:00 | 3 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 17 | 8 | 33 | 24 | 36 | 16 | 2 | 15 | 0 | 0
2022-03-01 06:00 | 3 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 18 | 7 | 34 | 24 | 37 | 13 | 2 | 14 | 0 | 0
2022-03-01 07:00 | 3 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 21 | 8 | 37 | 28 | 41 | 17 | 3 | 18 | 0 | 0
2022-03-01 08:00 | 3 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 23 | 14 | 38 | 34 | 49 | 19 | 6 | 24 | 0 | 0
2022-03-01 09:00 | 3 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 27 | 18 | 38 | 37 | 54 | 21 | 9 | 27 | 0 | 0
2022-03-01 10:00 | 3 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 29 | 19 | 39 | 41 | 60 | 24 | 10 | 31 | 0 | 0
2022-03-01 11:00 | 3 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 32 | 22 | 41 | 49 | 63 | 26 | 15 | 35 | 0 | 0
2022-03-01 12:00 | 3 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 33 | 23 | 43 | 50 | 65 | 28 | 16 | 38 | 0 | 0
2022-03-01 13:00 | 3 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 34 | 25 | 44 | 53 | 66 | 32 | 16 | 40 | 0 | 0
2022-03-01 14:00 | 3 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 34 | 26 | 41 | 53 | 64 | 31 | 17 | 42 | 0 | 0
2022-03-01 15:00 | 3 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 36 | 27 | 40 | 53 | 63 | 31 | 16 | 43 | 0 | 0
2022-03-01 16:00 | 3 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 36 | 24 | 39 | 53 | 61 | 32 | 16 | 43 | 0 | 0
2022-03-01 17:00 | 3 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 33 | 21 | 38 | 51 | 57 | 30 | 15 | 40 | 0 | 0
2022-03-01 18:00 | 3 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 32 | 19 | 36 | 45 | 54 | 28 | 13 | 37 | 0 | 0
2022-03-01 19:00 | 3 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 33 | 18 | 36 | 46 | 49 | 27 | 12 | 33 | 0 | 0
2022-03-01 20:00 | 3 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 33 | 16 | 34 | 46 | 49 | 26 | 12 | 30 | 0 | 0
2022-03-01 21:00 | 3 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 27 | 15 | 33 | 45 | 47 | 24 | 11 | 27 | 0 | 0
2022-03-01 22:00 | 3 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 26 | 13 | 31 | 42 | 47 | 23 | 9 | 25 | 0 | 0
2022-03-01 23:00 | 3 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 26 | 13 | 30 | 42 | 48 | 21 | 8 | 24 | 0 | 0
2022-03-02 | 3 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 25 | 14 | 30 | 38 | 46 | 23 | 7 | 23 | 0 | 0
2022-03-02 01:00 | 3 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 24 | 15 | 30 | 36 | 45 | 25 | 6 | 22 | 0 | 0
2022-03-02 02:00 | 3 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 23 | 16 | 30 | 33 | 47 | 24 | 6 | 21 | 0 | 0
2022-03-02 03:00 | 3 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 22 | 16 | 30 | 34 | 48 | 24 | 5 | 21 | 0 | 0
2022-03-02 04:00 | 3 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 21 | 17 | 30 | 34 | 47 | 24 | 5 | 20 | 0 | 0
2022-03-02 05:00 | 3 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 21 | 17 | 30 | 31 | 49 | 24 | 4 | 19 | 0 | 0
2022-03-02 06:00 | 3 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 22 | 18 | 30 | 32 | 50 | 24 | 4 | 18 | 0 | 0
2022-03-02 07:00 | 3 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 25 | 18 | 29 | 36 | 53 | 25 | 4 | 23 | 0 | 0
2022-03-02 08:00 | 3 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 28 | 19 | 29 | 41 | 55 | 26 | 7 | 28 | 0 | 0
2022-03-02 09:00 | 3 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 34 | 20 | 28 | 52 | 58 | 30 | 10 | 35 | 0 | 0
2022-03-02 10:00 | 3 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 36 | 23 | 29 | 53 | 60 | 31 | 13 | 42 | 0 | 0
2022-03-02 11:00 | 3 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 38 | 24 | 29 | 54 | 62 | 35 | 15 | 49 | 0 | 0
2022-03-02 12:00 | 3 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 39 | 26 | 29 | 54 | 63 | 36 | 18 | 56 | 0 | 0
2022-03-02 13:00 | 3 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 39 | 27 | 26 | 54 | 64 | 36 | 19 | 57 | 0 | 0
2022-03-02 14:00 | 3 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 40 | 29 | 26 | 54 | 65 | 38 | 19 | 57 | 0 | 0
2022-03-02 15:00 | 3 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 40 | 29 | 26 | 53 | 65 | 39 | 20 | 56 | 0 | 0
2022-03-02 16:00 | 3 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 39 | 29 | 25 | 51 | 66 | 40 | 18 | 54 | 0 | 0
2022-03-02 17:00 | 3 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 38 | 29 | 24 | 49 | 62 | 37 | 16 | 51 | 0 | 0
2022-03-02 18:00 | 3 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 39 | 29 | 23 | 46 | 66 | 35 | 14 | 50 | 0 | 0
2022-03-02 19:00 | 3 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 37 | 28 | 23 | 45 | 64 | 33 | 12 | 48 | 0 | 0
2022-03-02 20:00 | 3 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 37 | 27 | 21 | 43 | 61 | 32 | 10 | 41 | 0 | 0
2022-03-02 21:00 | 3 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 38 | 25 | 20 | 41 | 58 | 32 | 9 | 36 | 0 | 0
2022-03-02 22:00 | 3 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 40 | 22 | 18 | 39 | 56 | 32 | 9 | 32 | 0 | 0
2022-03-02 23:00 | 3 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 41 | 21 | 17 | 38 | 54 | 33 | 9 | 31 | 0 | 0
2022-03-03 | 3 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 41 | 22 | 15 | 36 | 52 | 33 | 8 | 31 | 0 | 0
2022-03-03 01:00 | 3 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 42 | 23 | 14 | 35 | 50 | 32 | 8 | 29 | 0 | 0
2022-03-03 02:00 | 3 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 43 | 27 | 13 | 32 | 50 | 33 | 9 | 28 | 0 | 0
2022-03-03 03:00 | 3 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 44 | 23 | 11 | 32 | 45 | 32 | 9 | 28 | 0 | 0
2022-03-03 04:00 | 3 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 46 | 22 | 10 | 32 | 41 | 32 | 9 | 27 | 0 | 0
2022-03-03 05:00 | 3 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 47 | 19 | 10 | 31 | 42 | 32 | 9 | 25 | 0 | 0
2022-03-03 06:00 | 3 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 48 | 18 | 8 | 31 | 42 | 32 | 10 | 25 | 0 | 0
2022-03-03 07:00 | 3 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 49 | 20 | 10 | 32 | 46 | 33 | 11 | 27 | 0 | 0
2022-03-03 08:00 | 3 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 50 | 26 | 11 | 35 | 52 | 34 | 14 | 35 | 0 | 0
2022-03-03 09:00 | 3 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 50 | 32 | 12 | 36 | 56 | 34 | 19 | 42 | 0 | 0
2022-03-03 10:00 | 3 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 52 | 34 | 15 | 37 | 58 | 38 | 22 | 47 | 0 | 0
2022-03-03 11:00 | 3 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 54 | 35 | 16 | 39 | 60 | 40 | 26 | 50 | 0 | 0
2022-03-03 12:00 | 3 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 54 | 37 | 17 | 41 | 61 | 40 | 29 | 52 | 0 | 0
2022-03-03 13:00 | 3 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 55 | 38 | 19 | 44 | 61 | 41 | 32 | 52 | 0 | 0
2022-03-03 14:00 | 3 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 45 | 41 | 19 | 46 | 61 | 42 | 34 | 50 | 0 | 0
2022-03-03 15:00 | 3 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 40 | 39 | 19 | 46 | 60 | 40 | 35 | 47 | 0 | 0
2022-03-03 16:00 | 3 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 40 | 39 | 18 | 46 | 59 | 39 | 35 | 42 | 0 | 0
2022-03-03 17:00 | 3 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 38 | 36 | 16 | 42 | 58 | 38 | 33 | 40 | 0 | 0
2022-03-03 18:00 | 3 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 34 | 34 | 14 | 38 | 56 | 37 | 30 | 37 | 0 | 0
2022-03-03 19:00 | 3 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 32 | 34 | 13 | 37 | 56 | 36 | 27 | 34 | 0 | 0
2022-03-03 20:00 | 3 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 30 | 33 | 13 | 36 | 55 | 36 | 29 | 32 | 0 | 0
2022-03-03 21:00 | 3 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 28 | 31 | 12 | 35 | 53 | 36 | 27 | 29 | 0 | 0
2022-03-03 22:00 | 3 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 27 | 30 | 12 | 33 | 53 | 35 | 28 | 26 | 0 | 0
2022-03-03 23:00 | 3 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 26 | 29 | 9 | 33 | 51 | 35 | 29 | 24 | 0 | 0
2022-03-04 | 3 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 24 | 28 | 9 | 33 | 50 | 35 | 28 | 23 | 0 | 0
2022-03-04 01:00 | 3 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 22 | 26 | 8 | 33 | 50 | 34 | 27 | 22 | 0 | 0
2022-03-04 02:00 | 3 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 20 | 27 | 8 | 33 | 50 | 34 | 26 | 21 | 0 | 0
2022-03-04 03:00 | 3 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 18 | 27 | 10 | 33 | 49 | 32 | 24 | 20 | 0 | 0
2022-03-04 04:00 | 3 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 18 | 26 | 17 | 33 | 47 | 33 | 22 | 18 | 0 | 0
2022-03-04 05:00 | 3 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 17 | 26 | 19 | 33 | 46 | 33 | 23 | 18 | 0 | 0
2022-03-04 06:00 | 3 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 17 | 27 | 24 | 33 | 46 | 33 | 26 | 17 | 0 | 0
2022-03-04 07:00 | 3 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 17 | 28 | 26 | 33 | 45 | 32 | 27 | 20 | 0 | 0
2022-03-04 08:00 | 3 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 17 | 30 | 28 | 33 | 47 | 33 | 31 | 22 | 0 | 0
2022-03-04 09:00 | 3 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 18 | 31 | 30 | 33 | 47 | 34 | 35 | 24 | 0 | 0
2022-03-04 10:00 | 3 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 19 | 32 | 33 | 34 | 48 | 34 | 38 | 28 | 0 | 0
2022-03-04 11:00 | 3 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 19 | 33 | 34 | 34 | 49 | 35 | 40 | 31 | 0 | 0
2022-03-04 12:00 | 3 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 19 | 32 | 36 | 32 | 50 | 36 | 40 | 32 | 0 | 0
2022-03-04 13:00 | 3 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 20 | 33 | 37 | 32 | 50 | 37 | 42 | 35 | 0 | 0
2022-03-04 14:00 | 3 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 18 | 33 | 38 | 33 | 52 | 37 | 43 | 36 | 0 | 0
2022-03-04 15:00 | 3 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 18 | 33 | 39 | 34 | 52 | 36 | 44 | 37 | 0 | 0
2022-03-04 16:00 | 3 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 18 | 32 | 40 | 34 | 52 | 35 | 43 | 37 | 0 | 0
2022-03-04 17:00 | 3 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 16 | 31 | 39 | 35 | 51 | 34 | 41 | 34 | 0 | 0
2022-03-04 18:00 | 3 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 15 | 31 | 40 | 36 | 49 | 34 | 39 | 31 | 0 | 0
2022-03-04 19:00 | 3 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 14 | 30 | 42 | 36 | 49 | 34 | 39 | 30 | 0 | 0
2022-03-04 20:00 | 3 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 13 | 30 | 42 | 36 | 48 | 32 | 37 | 30 | 0 | 0
2022-03-04 21:00 | 3 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 13 | 29 | 40 | 36 | 48 | 32 | 37 | 30 | 0 | 0
2022-03-04 22:00 | 3 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 12 | 29 | 38 | 37 | 49 | 30 | 36 | 28 | 0 | 0
2022-03-04 23:00 | 3 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 11 | 29 | 35 | 43 | 48 | 29 | 36 | 28 | 0 | 0
2022-03-05 | 3 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 11 | 29 | 33 | 44 | 48 | 28 | 37 | 27 | 0 | 0
2022-03-05 01:00 | 3 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 10 | 28 | 30 | 44 | 48 | 28 | 36 | 27 | 0 | 0
2022-03-05 02:00 | 3 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 9 | 28 | 28 | 42 | 47 | 28 | 40 | 26 | 0 | 0
2022-03-05 03:00 | 3 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 8 | 27 | 26 | 41 | 46 | 28 | 35 | 26 | 0 | 0
2022-03-05 04:00 | 3 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 8 | 26 | 25 | 40 | 47 | 26 | 35 | 25 | 0 | 0
2022-03-05 05:00 | 3 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 8 | 25 | 24 | 42 | 47 | 27 | 35 | 24 | 0 | 0
2022-03-05 06:00 | 3 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 9 | 25 | 24 | 50 | 47 | 28 | 34 | 23 | 0 | 0
2022-03-05 07:00 | 3 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 9 | 26 | 23 | 45 | 47 | 28 | 37 | 24 | 0 | 0
2022-03-05 08:00 | 3 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 12 | 27 | 23 | 53 | 47 | 30 | 38 | 25 | 0 | 0
2022-03-05 09:00 | 3 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 14 | 30 | 23 | 54 | 48 | 32 | 38 | 27 | 0 | 0
2022-03-05 10:00 | 3 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 17 | 31 | 24 | 54 | 48 | 33 | 38 | 28 | 0 | 0
2022-03-05 11:00 | 3 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 19 | 32 | 25 | 54 | 49 | 36 | 38 | 30 | 0 | 0
2022-03-05 12:00 | 3 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 21 | 32 | 28 | 53 | 50 | 38 | 39 | 34 | 0 | 0
2022-03-05 13:00 | 3 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 22 | 31 | 28 | 51 | 52 | 38 | 40 | 36 | 0 | 0
2022-03-05 14:00 | 3 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 23 | 33 | 29 | 41 | 54 | 38 | 42 | 36 | 0 | 0
2022-03-05 15:00 | 3 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 24 | 32 | 29 | 46 | 54 | 38 | 43 | 37 | 0 | 0
2022-03-05 16:00 | 3 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 23 | 31 | 29 | 43 | 55 | 38 | 42 | 37 | 0 | 0
2022-03-05 17:00 | 3 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 23 | 29 | 28 | 39 | 51 | 36 | 42 | 35 | 0 | 0
2022-03-05 18:00 | 3 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 22 | 27 | 26 | 37 | 52 | 36 | 43 | 33 | 0 | 0
2022-03-05 19:00 | 3 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 23 | 27 | 26 | 36 | 53 | 35 | 44 | 32 | 0 | 0
2022-03-05 20:00 | 3 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 23 | 27 | 24 | 35 | 55 | 34 | 44 | 32 | 0 | 0
2022-03-05 21:00 | 3 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 23 | 28 | 22 | 35 | 57 | 33 | 44 | 32 | 0 | 0
2022-03-05 22:00 | 3 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 23 | 29 | 22 | 34 | 56 | 32 | 40 | 31 | 0 | 0
2022-03-05 23:00 | 3 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 24 | 30 | 22 | 33 | 62 | 32 | 39 | 32 | 0 | 0
2022-03-06 | 3 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 25 | 30 | 21 | 32 | 58 | 32 | 38 | 31 | 0 | 0
2022-03-06 01:00 | 3 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 25 | 29 | 20 | 31 | 62 | 33 | 36 | 31 | 0 | 0
2022-03-06 02:00 | 3 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 26 | 29 | 19 | 30 | 58 | 33 | 33 | 31 | 0 | 0
2022-03-06 03:00 | 3 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 25 | 29 | 18 | 29 | 58 | 33 | 29 | 30 | 0 | 0
2022-03-06 04:00 | 3 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 25 | 29 | 19 | 28 | 58 | 32 | 28 | 29 | 0 | 0
2022-03-06 05:00 | 3 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 27 | 29 | 19 | 26 | 57 | 32 | 27 | 27 | 0 | 0
2022-03-06 06:00 | 3 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 28 | 22 | 25 | 57 | 32 | 27 | 25 | 0 | 0
2022-03-06 07:00 | 3 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 31 | 28 | 23 | 26 | 57 | 33 | 27 | 24 | 0 | 0
2022-03-06 08:00 | 3 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 33 | 28 | 26 | 27 | 59 | 34 | 29 | 23 | 0 | 0
2022-03-06 09:00 | 3 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 37 | 28 | 32 | 28 | 60 | 33 | 31 | 24 | 0 | 0
2022-03-06 10:00 | 3 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 41 | 29 | 36 | 30 | 63 | 34 | 33 | 26 | 0 | 0
2022-03-06 11:00 | 3 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 45 | 29 | 32 | 32 | 60 | 34 | 34 | 28 | 0 | 0
2022-03-06 12:00 | 3 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 48 | 31 | 32 | 34 | 60 | 33 | 36 | 30 | 0 | 0
2022-03-06 13:00 | 3 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 51 | 31 | 32 | 35 | 60 | 33 | 36 | 30 | 0 | 0
2022-03-06 14:00 | 3 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 53 | 30 | 32 | 36 | 66 | 33 | 39 | 31 | 0 | 0
2022-03-06 15:00 | 3 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 54 | 28 | 30 | 36 | 64 | 32 | 39 | 31 | 0 | 0
2022-03-06 16:00 | 3 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 53 | 27 | 30 | 35 | 61 | 31 | 39 | 29 | 0 | 0
2022-03-06 17:00 | 3 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 47 | 25 | 30 | 33 | 60 | 31 | 37 | 27 | 0 | 0
2022-03-06 18:00 | 3 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 39 | 23 | 31 | 31 | 58 | 30 | 34 | 24 | 0 | 0
2022-03-06 19:00 | 3 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 36 | 23 | 31 | 30 | 55 | 29 | 33 | 21 | 0 | 0
2022-03-06 20:00 | 3 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 37 | 22 | 31 | 29 | 51 | 28 | 33 | 19 | 0 | 0
2022-03-06 21:00 | 3 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 36 | 21 | 30 | 27 | 50 | 28 | 34 | 16 | 0 | 0
2022-03-06 22:00 | 3 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 36 | 20 | 30 | 28 | 48 | 28 | 34 | 15 | 0 | 0
2022-03-06 23:00 | 3 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 35 | 18 | 30 | 26 | 47 | 24 | 35 | 14 | 0 | 0
2022-03-07 | 3 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 35 | 17 | 29 | 23 | 47 | 24 | 36 | 13 | 0 | 0
2022-03-07 01:00 | 3 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 32 | 15 | 28 | 20 | 47 | 23 | 35 | 12 | 0 | 0
2022-03-07 02:00 | 3 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 30 | 13 | 28 | 20 | 47 | 22 | 34 | 10 | 0 | 0
2022-03-07 03:00 | 3 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 29 | 8 | 27 | 19 | 47 | 21 | 34 | 10 | 0 | 0
2022-03-07 04:00 | 3 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 28 | 7 | 26 | 21 | 46 | 19 | 34 | 9 | 0 | 0
2022-03-07 05:00 | 3 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 27 | 7 | 26 | 23 | 45 | 17 | 34 | 7 | 0 | 0
2022-03-07 06:00 | 3 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 27 | 4 | 26 | 22 | 45 | 18 | 34 | 6 | 0 | 0
2022-03-07 07:00 | 3 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 27 | 4 | 27 | 25 | 46 | 17 | 36 | 11 | 0 | 0
2022-03-07 08:00 | 3 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 28 | 3 | 27 | 29 | 48 | 15 | 39 | 15 | 0 | 0
2022-03-07 09:00 | 3 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 29 | 4 | 27 | 32 | 50 | 13 | 41 | 18 | 0 | 0
2022-03-07 10:00 | 3 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 30 | 3 | 28 | 36 | 50 | 13 | 45 | 24 | 0 | 0
2022-03-07 11:00 | 3 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 34 | 3 | 28 | 37 | 52 | 12 | 48 | 28 | 0 | 0
2022-03-07 12:00 | 3 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 36 | 3 | 28 | 39 | 52 | 14 | 52 | 30 | 0 | 0
2022-03-07 13:00 | 3 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 39 | 4 | 27 | 40 | 54 | 14 | 54 | 32 | 0 | 0
2022-03-07 14:00 | 3 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 39 | 4 | 26 | 43 | 54 | 13 | 54 | 34 | 0 | 0
2022-03-07 15:00 | 3 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 40 | 2 | 26 | 42 | 54 | 14 | 54 | 35 | 0 | 0
2022-03-07 16:00 | 3 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 40 | 2 | 26 | 42 | 54 | 13 | 53 | 34 | 0 | 0
2022-03-07 17:00 | 3 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 39 | 2 | 26 | 40 | 50 | 11 | 52 | 32 | 0 | 0
2022-03-07 18:00 | 3 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 37 | 1 | 25 | 41 | 47 | 12 | 52 | 30 | 0 | 0
2022-03-07 19:00 | 3 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 36 | 1 | 25 | 39 | 47 | 10 | 49 | 26 | 0 | 0
2022-03-07 20:00 | 3 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 35 | 0 | 23 | 38 | 46 | 10 | 48 | 24 | 0 | 0
2022-03-07 21:00 | 3 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 34 | 0 | 21 | 36 | 44 | 8 | 47 | 22 | 0 | 0
2022-03-07 22:00 | 3 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 33 | 0 | 20 | 35 | 43 | 8 | 45 | 19 | 0 | 0
2022-03-07 23:00 | 3 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 34 | 1 | 18 | 35 | 43 | 8 | 44 | 19 | 0 | 0
2022-03-08 | 3 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 32 | 1 | 18 | 36 | 43 | 6 | 44 | 18 | 0 | 0
2022-03-08 01:00 | 3 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 31 | 1 | 18 | 36 | 41 | 5 | 45 | 17 | 0 | 0
2022-03-08 02:00 | 3 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 33 | 0 | 17 | 36 | 41 | 5 | 46 | 16 | 0 | 0
2022-03-08 03:00 | 3 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 33 | 0 | 17 | 37 | 41 | 5 | 47 | 15 | 0 | 0
2022-03-08 04:00 | 3 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 33 | -1 | 16 | 37 | 42 | 2 | 48 | 14 | 0 | 0
2022-03-08 05:00 | 3 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 34 | -2 | 15 | 36 | 42 | 1 | 48 | 14 | 0 | 0
2022-03-08 06:00 | 3 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 35 | -3 | 15 | 37 | 42 | 1 | 49 | 14 | 0 | 0
2022-03-08 07:00 | 3 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 38 | -1 | 15 | 38 | 42 | 1 | 48 | 18 | 0 | 0
2022-03-08 08:00 | 3 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 43 | -1 | 14 | 39 | 41 | 6 | 48 | 22 | 0 | 0
2022-03-08 09:00 | 3 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 50 | 2 | 15 | 42 | 43 | 12 | 49 | 27 | 0 | 0
2022-03-08 10:00 | 3 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 56 | 9 | 16 | 43 | 44 | 14 | 50 | 31 | 0 | 0
2022-03-08 11:00 | 3 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 59 | 13 | 18 | 47 | 44 | 17 | 52 | 38 | 0 | 0
2022-03-08 12:00 | 3 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 62 | 18 | 19 | 55 | 45 | 17 | 52 | 41 | 0 | 0
2022-03-08 13:00 | 3 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 63 | 18 | 21 | 60 | 43 | 19 | 53 | 43 | 0 | 0
2022-03-08 14:00 | 3 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 64 | 19 | 23 | 62 | 40 | 22 | 52 | 44 | 0 | 0
2022-03-08 15:00 | 3 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 62 | 20 | 24 | 60 | 40 | 22 | 52 | 44 | 0 | 0
2022-03-08 16:00 | 3 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 60 | 20 | 22 | 59 | 39 | 25 | 52 | 44 | 0 | 0
2022-03-08 17:00 | 3 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 58 | 18 | 20 | 58 | 38 | 25 | 51 | 39 | 0 | 0
2022-03-08 18:00 | 3 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 56 | 17 | 20 | 55 | 38 | 23 | 50 | 31 | 0 | 0
2022-03-08 19:00 | 3 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 54 | 17 | 21 | 53 | 35 | 25 | 51 | 31 | 0 | 0
2022-03-08 20:00 | 3 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 53 | 17 | 23 | 51 | 37 | 24 | 51 | 31 | 0 | 0
2022-03-08 21:00 | 3 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 52 | 17 | 26 | 49 | 38 | 25 | 49 | 29 | 0 | 0
2022-03-08 22:00 | 3 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 51 | 18 | 27 | 46 | 36 | 25 | 48 | 29 | 0 | 0
2022-03-08 23:00 | 3 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 51 | 19 | 26 | 46 | 37 | 26 | 42 | 28 | 0 | 0
2022-03-09 | 3 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 49 | 20 | 27 | 49 | 38 | 26 | 39 | 28 | 0 | 0
2022-03-09 01:00 | 3 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 48 | 22 | 28 | 47 | 37 | 28 | 37 | 26 | 0 | 0
2022-03-09 02:00 | 3 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 47 | 23 | 29 | 46 | 37 | 30 | 35 | 26 | 0 | 0
2022-03-09 03:00 | 3 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 46 | 25 | 29 | 43 | 37 | 38 | 34 | 27 | 0 | 0
2022-03-09 04:00 | 3 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 46 | 26 | 31 | 43 | 36 | 39 | 34 | 28 | 0 | 0
2022-03-09 05:00 | 3 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 46 | 27 | 30 | 40 | 35 | 42 | 34 | 28 | 0 | 0
2022-03-09 06:00 | 3 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 47 | 29 | 25 | 38 | 35 | 42 | 34 | 29 | 0 | 0
2022-03-09 07:00 | 3 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 50 | 31 | 25 | 42 | 35 | 44 | 34 | 30 | 0 | 0
2022-03-09 08:00 | 3 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 52 | 32 | 23 | 44 | 35 | 45 | 35 | 31 | 0 | 0
2022-03-09 09:00 | 3 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 56 | 34 | 23 | 45 | 36 | 46 | 37 | 33 | 0 | 0
2022-03-09 10:00 | 3 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 55 | 37 | 24 | 48 | 38 | 48 | 39 | 36 | 0 | 0
2022-03-09 11:00 | 3 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 56 | 38 | 25 | 50 | 38 | 47 | 40 | 38 | 0 | 0
2022-03-09 12:00 | 3 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 59 | 40 | 25 | 53 | 40 | 53 | 41 | 39 | 0 | 0
2022-03-09 13:00 | 3 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 60 | 41 | 25 | 54 | 41 | 59 | 42 | 40 | 0 | 0
2022-03-09 14:00 | 3 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 58 | 42 | 26 | 55 | 42 | 61 | 43 | 39 | 0 | 0
2022-03-09 15:00 | 3 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 56 | 44 | 25 | 56 | 43 | 63 | 42 | 37 | 0 | 0
2022-03-09 16:00 | 3 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 57 | 44 | 25 | 55 | 42 | 63 | 42 | 37 | 0 | 0
2022-03-09 17:00 | 3 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 58 | 44 | 25 | 52 | 40 | 62 | 39 | 37 | 0 | 0
2022-03-09 18:00 | 3 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 56 | 43 | 25 | 48 | 39 | 57 | 38 | 36 | 0 | 0
2022-03-09 19:00 | 3 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 56 | 41 | 24 | 44 | 39 | 54 | 34 | 36 | 0 | 0
2022-03-09 20:00 | 3 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 58 | 44 | 22 | 40 | 38 | 54 | 33 | 36 | 0 | 0
2022-03-09 21:00 | 3 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 59 | 47 | 20 | 37 | 38 | 54 | 31 | 36 | 0 | 0
2022-03-09 22:00 | 3 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 59 | 48 | 18 | 37 | 37 | 56 | 30 | 36 | 0 | 0
2022-03-09 23:00 | 3 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 48 | 48 | 17 | 35 | 35 | 57 | 30 | 36 | 0 | 0
2022-03-10 | 3 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 39 | 50 | 17 | 35 | 34 | 57 | 30 | 36 | 0 | 0
2022-03-10 01:00 | 3 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 35 | 50 | 18 | 34 | 36 | 58 | 27 | 36 | 0 | 0
2022-03-10 02:00 | 3 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 32 | 50 | 18 | 35 | 37 | 57 | 26 | 36 | 0 | 0
2022-03-10 03:00 | 3 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 30 | 50 | 19 | 36 | 37 | 56 | 29 | 36 | 0 | 0
2022-03-10 04:00 | 3 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 29 | 50 | 21 | 36 | 37 | 56 | 28 | 37 | 0 | 0
2022-03-10 05:00 | 3 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 27 | 50 | 24 | 33 | 37 | 53 | 27 | 37 | 0 | 0
2022-03-10 06:00 | 3 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 26 | 50 | 26 | 32 | 38 | 53 | 29 | 37 | 0 | 0
2022-03-10 07:00 | 3 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 27 | 50 | 28 | 40 | 38 | 56 | 35 | 38 | 0 | 0
2022-03-10 08:00 | 3 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 27 | 54 | 31 | 45 | 39 | 60 | 37 | 39 | 0 | 0
2022-03-10 09:00 | 3 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 27 | 56 | 33 | 49 | 41 | 63 | 41 | 40 | 0 | 0
2022-03-10 10:00 | 3 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 28 | 56 | 39 | 51 | 42 | 67 | 46 | 43 | 0 | 0
2022-03-10 11:00 | 3 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 27 | 58 | 42 | 54 | 42 | 68 | 48 | 48 | 0 | 0
2022-03-10 12:00 | 3 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 27 | 62 | 45 | 55 | 44 | 71 | 51 | 52 | 0 | 0
2022-03-10 13:00 | 3 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 27 | 63 | 47 | 56 | 44 | 72 | 50 | 54 | 0 | 0
2022-03-10 14:00 | 3 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 23 | 64 | 49 | 57 | 44 | 70 | 49 | 58 | 0 | 0
2022-03-10 15:00 | 3 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 22 | 65 | 48 | 58 | 44 | 71 | 46 | 58 | 0 | 0
2022-03-10 16:00 | 3 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 22 | 65 | 46 | 58 | 44 | 70 | 48 | 57 | 0 | 0
2022-03-10 17:00 | 3 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 21 | 63 | 45 | 55 | 43 | 68 | 49 | 54 | 0 | 0
2022-03-10 18:00 | 3 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 20 | 62 | 44 | 51 | 43 | 60 | 48 | 51 | 0 | 0
2022-03-10 19:00 | 3 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 19 | 57 | 41 | 44 | 41 | 57 | 48 | 51 | 0 | 0
2022-03-10 20:00 | 3 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 19 | 54 | 40 | 42 | 40 | 55 | 47 | 49 | 0 | 0
2022-03-10 21:00 | 3 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 18 | 52 | 41 | 39 | 40 | 57 | 45 | 48 | 0 | 0
2022-03-10 22:00 | 3 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 18 | 51 | 42 | 37 | 39 | 56 | 43 | 47 | 0 | 0
2022-03-10 23:00 | 3 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 17 | 50 | 41 | 35 | 38 | 57 | 43 | 47 | 0 | 0
2022-03-11 | 3 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 17 | 50 | 40 | 34 | 37 | 56 | 42 | 47 | 0 | 0
2022-03-11 01:00 | 3 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 17 | 50 | 40 | 34 | 36 | 56 | 42 | 47 | 0 | 0
2022-03-11 02:00 | 3 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 16 | 49 | 40 | 31 | 36 | 48 | 42 | 47 | 0 | 0
2022-03-11 03:00 | 3 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 16 | 46 | 42 | 32 | 36 | 46 | 40 | 47 | 0 | 0
2022-03-11 04:00 | 3 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 16 | 41 | 42 | 31 | 35 | 42 | 32 | 47 | 0 | 0
2022-03-11 05:00 | 3 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 16 | 34 | 43 | 31 | 34 | 37 | 29 | 46 | 0 | 0
2022-03-11 06:00 | 3 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 16 | 32 | 44 | 31 | 35 | 38 | 26 | 45 | 0 | 0
2022-03-11 07:00 | 3 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 18 | 30 | 47 | 35 | 38 | 37 | 25 | 46 | 0 | 0
2022-03-11 08:00 | 3 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 21 | 29 | 48 | 39 | 40 | 36 | 26 | 48 | 0 | 0
2022-03-11 09:00 | 3 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 23 | 28 | 50 | 42 | 43 | 36 | 27 | 51 | 0 | 0
2022-03-11 10:00 | 3 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 25 | 28 | 47 | 45 | 46 | 36 | 28 | 54 | 0 | 0
2022-03-11 11:00 | 3 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 26 | 29 | 47 | 47 | 47 | 37 | 30 | 55 | 0 | 0
2022-03-11 12:00 | 3 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 29 | 29 | 46 | 53 | 52 | 36 | 30 | 57 | 0 | 0
2022-03-11 13:00 | 3 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 30 | 29 | 45 | 56 | 53 | 38 | 32 | 60 | 0 | 0
2022-03-11 14:00 | 3 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 31 | 28 | 46 | 50 | 53 | 38 | 34 | 65 | 0 | 0
2022-03-11 15:00 | 3 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 31 | 28 | 47 | 46 | 54 | 38 | 31 | 64 | 0 | 0
2022-03-11 16:00 | 3 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 31 | 28 | 46 | 46 | 53 | 38 | 30 | 63 | 0 | 0
2022-03-11 17:00 | 3 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 30 | 28 | 46 | 44 | 51 | 38 | 29 | 60 | 0 | 0
2022-03-11 18:00 | 3 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 28 | 43 | 44 | 50 | 38 | 29 | 57 | 0 | 0
2022-03-11 19:00 | 3 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 29 | 28 | 41 | 45 | 50 | 38 | 25 | 56 | 0 | 0
2022-03-11 20:00 | 3 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 29 | 27 | 40 | 45 | 48 | 38 | 25 | 56 | 0 | 0
2022-03-11 21:00 | 3 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 29 | 26 | 39 | 45 | 46 | 38 | 26 | 55 | 0 | 0
2022-03-11 22:00 | 3 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 28 | 25 | 37 | 45 | 45 | 36 | 20 | 54 | 0 | 0
2022-03-11 23:00 | 3 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 29 | 25 | 36 | 46 | 45 | 37 | 20 | 54 | 0 | 0
2022-03-12 | 3 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 30 | 23 | 35 | 46 | 43 | 36 | 19 | 54 | 0 | 0
2022-03-12 01:00 | 3 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 31 | 22 | 34 | 48 | 40 | 34 | 18 | 53 | 0 | 0
2022-03-12 02:00 | 3 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 32 | 20 | 33 | 46 | 39 | 32 | 18 | 50 | 0 | 0
2022-03-12 03:00 | 3 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 32 | 22 | 33 | 47 | 40 | 32 | 17 | 48 | 0 | 0
2022-03-12 04:00 | 3 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 32 | 22 | 33 | 47 | 41 | 31 | 17 | 48 | 0 | 0
2022-03-12 05:00 | 3 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 33 | 21 | 33 | 46 | 43 | 32 | 17 | 47 | 0 | 0
2022-03-12 06:00 | 3 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 33 | 21 | 33 | 47 | 43 | 32 | 17 | 46 | 0 | 0
2022-03-12 07:00 | 3 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 29 | 24 | 33 | 45 | 43 | 33 | 17 | 49 | 0 | 0
2022-03-12 08:00 | 3 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 29 | 27 | 33 | 49 | 39 | 34 | 20 | 51 | 0 | 0
2022-03-12 09:00 | 3 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 30 | 30 | 34 | 49 | 39 | 36 | 22 | 54 | 0 | 0
2022-03-12 10:00 | 3 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 30 | 33 | 35 | 49 | 40 | 39 | 24 | 58 | 0 | 0
2022-03-12 11:00 | 3 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 31 | 33 | 34 | 49 | 41 | 40 | 26 | 65 | 0 | 0
2022-03-12 12:00 | 3 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 34 | 30 | 36 | 46 | 41 | 37 | 27 | 68 | 0 | 0
2022-03-12 13:00 | 3 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 37 | 30 | 37 | 47 | 43 | 36 | 28 | 69 | 0 | 0
2022-03-12 14:00 | 3 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 40 | 30 | 38 | 48 | 44 | 36 | 29 | 74 | 0 | 0
2022-03-12 15:00 | 3 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 40 | 31 | 40 | 45 | 44 | 37 | 30 | 72 | 0 | 0
2022-03-12 16:00 | 3 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 39 | 31 | 38 | 45 | 43 | 37 | 29 | 70 | 0 | 0
2022-03-12 17:00 | 3 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 38 | 31 | 35 | 44 | 42 | 38 | 27 | 70 | 0 | 0
2022-03-12 18:00 | 3 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 38 | 31 | 34 | 43 | 40 | 38 | 25 | 66 | 0 | 0
2022-03-12 19:00 | 3 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 36 | 31 | 34 | 43 | 39 | 38 | 24 | 60 | 0 | 0
2022-03-12 20:00 | 3 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 35 | 31 | 45 | 43 | 37 | 39 | 23 | 58 | 0 | 0
2022-03-12 21:00 | 3 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 34 | 31 | 46 | 42 | 35 | 40 | 23 | 56 | 0 | 0
2022-03-12 22:00 | 3 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 33 | 31 | 49 | 42 | 35 | 40 | 22 | 53 | 0 | 0
2022-03-12 23:00 | 3 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 33 | 31 | 52 | 41 | 34 | 40 | 21 | 51 | 0 | 0
2022-03-13 | 3 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 31 | 31 | 53 | 41 | 33 | 39 | 19 | 50 | 0 | 0
2022-03-13 01:00 | 3 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 31 | 31 | 55 | 40 | 32 | 42 | 18 | 52 | 0 | 0
2022-03-13 02:00 | 3 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 30 | 32 | 54 | 40 | 32 | 42 | 17 | 50 | 0 | 0
2022-03-13 03:00 | 3 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 30 | 32 | 51 | 39 | 32 | 41 | 17 | 50 | 0 | 0
2022-03-13 04:00 | 3 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 32 | 33 | 54 | 38 | 31 | 41 | 19 | 48 | 0 | 0
2022-03-13 05:00 | 3 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 32 | 33 | 55 | 38 | 31 | 42 | 20 | 46 | 0 | 0
2022-03-13 06:00 | 3 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 33 | 34 | 53 | 39 | 32 | 44 | 21 | 47 | 0 | 0
2022-03-13 07:00 | 3 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 35 | 35 | 55 | 41 | 32 | 46 | 21 | 48 | 0 | 0
2022-03-13 08:00 | 3 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 36 | 36 | 40 | 45 | 33 | 48 | 21 | 52 | 0 | 0
2022-03-13 09:00 | 3 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 37 | 36 | 42 | 47 | 35 | 48 | 20 | 63 | 0 | 0
2022-03-13 10:00 | 3 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 37 | 37 | 43 | 49 | 36 | 50 | 20 | 74 | 0 | 0
2022-03-13 11:00 | 3 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 39 | 38 | 45 | 54 | 38 | 52 | 21 | 76 | 0 | 0
2022-03-13 12:00 | 3 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 40 | 39 | 48 | 54 | 41 | 56 | 22 | 79 | 0 | 0
2022-03-13 13:00 | 3 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 40 | 39 | 49 | 56 | 42 | 57 | 24 | 82 | 0 | 0
2022-03-13 14:00 | 3 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 40 | 40 | 49 | 58 | 45 | 58 | 24 | 81 | 0 | 0
2022-03-13 15:00 | 3 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 39 | 40 | 46 | 54 | 45 | 57 | 24 | 80 | 0 | 0
2022-03-13 16:00 | 3 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 39 | 41 | 48 | 52 | 45 | 58 | 24 | 77 | 0 | 0
2022-03-13 17:00 | 3 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 39 | 41 | 46 | 50 | 43 | 55 | 25 | 75 | 0 | 0
2022-03-13 18:00 | 3 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 38 | 40 | 45 | 49 | 42 | 56 | 26 | 72 | 0 | 0
2022-03-13 19:00 | 3 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 39 | 40 | 44 | 48 | 41 | 56 | 27 | 70 | 0 | 0
2022-03-13 20:00 | 3 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 39 | 40 | 43 | 48 | 41 | 56 | 28 | 68 | 0 | 0
2022-03-13 21:00 | 3 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 39 | 40 | 42 | 46 | 40 | 56 | 29 | 61 | 0 | 0
2022-03-13 22:00 | 3 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 39 | 41 | 40 | 45 | 37 | 56 | 29 | 59 | 0 | 0
2022-03-13 23:00 | 3 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 39 | 42 | 39 | 45 | 36 | 58 | 31 | 57 | 0 | 0
2022-03-14 | 3 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 39 | 41 | 39 | 45 | 34 | 56 | 31 | 54 | 0 | 0
2022-03-14 01:00 | 3 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 40 | 40 | 38 | 44 | 33 | 54 | 29 | 52 | 0 | 0
2022-03-14 02:00 | 3 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 38 | 40 | 37 | 42 | 32 | 55 | 29 | 52 | 0 | 0
2022-03-14 03:00 | 3 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 38 | 40 | 35 | 42 | 32 | 54 | 29 | 49 | 0 | 0
2022-03-14 04:00 | 3 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 39 | 40 | 35 | 42 | 32 | 53 | 29 | 47 | 0 | 0
2022-03-14 05:00 | 3 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 37 | 39 | 35 | 42 | 30 | 48 | 30 | 46 | 0 | 0
2022-03-14 06:00 | 3 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 36 | 40 | 35 | 41 | 31 | 48 | 31 | 49 | 0 | 0
2022-03-14 07:00 | 3 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 36 | 40 | 36 | 42 | 33 | 51 | 32 | 51 | 0 | 0
2022-03-14 08:00 | 3 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 37 | 40 | 37 | 44 | 35 | 53 | 32 | 53 | 0 | 0
2022-03-14 09:00 | 3 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 39 | 42 | 39 | 44 | 38 | 53 | 33 | 56 | 0 | 0
2022-03-14 10:00 | 3 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 40 | 44 | 39 | 44 | 40 | 54 | 33 | 67 | 0 | 0
2022-03-14 11:00 | 3 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 45 | 46 | 40 | 45 | 43 | 57 | 33 | 76 | 0 | 0
2022-03-14 12:00 | 3 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 47 | 48 | 40 | 47 | 44 | 54 | 34 | 78 | 0 | 0
2022-03-14 13:00 | 3 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 51 | 49 | 40 | 49 | 45 | 54 | 35 | 81 | 0 | 0
2022-03-14 14:00 | 3 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 51 | 49 | 39 | 50 | 46 | 53 | 34 | 81 | 0 | 0
2022-03-14 15:00 | 3 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 51 | 47 | 39 | 49 | 46 | 52 | 35 | 81 | 0 | 0
2022-03-14 16:00 | 3 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 51 | 46 | 37 | 49 | 45 | 51 | 34 | 79 | 0 | 0
2022-03-14 17:00 | 3 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 48 | 45 | 35 | 48 | 44 | 51 | 33 | 78 | 0 | 0
2022-03-14 18:00 | 3 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 46 | 45 | 34 | 44 | 43 | 50 | 32 | 77 | 0 | 0
2022-03-14 19:00 | 3 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 46 | 44 | 33 | 37 | 42 | 49 | 31 | 72 | 0 | 0
2022-03-14 20:00 | 3 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 45 | 44 | 30 | 36 | 42 | 49 | 31 | 72 | 0 | 0
2022-03-14 21:00 | 3 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 43 | 43 | 30 | 38 | 43 | 49 | 31 | 65 | 0 | 0
2022-03-14 22:00 | 3 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 41 | 43 | 30 | 39 | 44 | 48 | 30 | 62 | 0 | 0
2022-03-14 23:00 | 3 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 41 | 43 | 30 | 40 | 45 | 49 | 30 | 59 | 0 | 0
2022-03-15 | 3 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 46 | 43 | 29 | 39 | 46 | 49 | 31 | 56 | 0 | 0
2022-03-15 01:00 | 3 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 47 | 43 | 29 | 37 | 45 | 48 | 31 | 53 | 0 | 0
2022-03-15 02:00 | 3 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 49 | 43 | 30 | 36 | 44 | 47 | 31 | 52 | 0 | 0
2022-03-15 03:00 | 3 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 50 | 39 | 30 | 34 | 45 | 47 | 31 | 51 | 0 | 0
2022-03-15 04:00 | 3 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 50 | 35 | 31 | 34 | 44 | 46 | 30 | 49 | 0 | 0
2022-03-15 05:00 | 3 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 50 | 35 | 32 | 37 | 43 | 45 | 28 | 50 | 0 | 0
2022-03-15 06:00 | 3 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 50 | 34 | 32 | 38 | 43 | 44 | 27 | 49 | 0 | 0
2022-03-15 07:00 | 3 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 51 | 36 | 32 | 39 | 49 | 42 | 28 | 53 | 0 | 0
2022-03-15 08:00 | 3 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 52 | 37 | 34 | 40 | 52 | 42 | 28 | 59 | 0 | 0
2022-03-15 09:00 | 3 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 52 | 40 | 36 | 40 | 53 | 44 | 29 | 69 | 0 | 0
2022-03-15 10:00 | 3 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 54 | 43 | 42 | 42 | 55 | 47 | 31 | 71 | 0 | 0
2022-03-15 11:00 | 3 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 54 | 44 | 44 | 42 | 56 | 49 | 33 | 74 | 0 | 0
2022-03-15 12:00 | 3 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 56 | 48 | 42 | 44 | 58 | 51 | 34 | 77 | 0 | 0
2022-03-15 13:00 | 3 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 56 | 47 | 42 | 44 | 59 | 54 | 34 | 80 | 0 | 0
2022-03-15 14:00 | 3 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 59 | 47 | 45 | 43 | 59 | 53 | 35 | 78 | 0 | 0
2022-03-15 15:00 | 3 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 60 | 46 | 42 | 44 | 58 | 53 | 36 | 79 | 0 | 0
2022-03-15 16:00 | 3 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 61 | 45 | 40 | 41 | 58 | 53 | 36 | 78 | 0 | 0
2022-03-15 17:00 | 3 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 61 | 43 | 39 | 39 | 57 | 51 | 35 | 76 | 0 | 0
2022-03-15 18:00 | 3 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 59 | 41 | 39 | 37 | 56 | 49 | 33 | 73 | 0 | 0
2022-03-15 19:00 | 3 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 57 | 34 | 39 | 37 | 55 | 46 | 31 | 69 | 0 | 0
2022-03-15 20:00 | 3 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 57 | 34 | 39 | 35 | 52 | 45 | 30 | 74 | 0 | 0
2022-03-15 21:00 | 3 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 58 | 34 | 41 | 35 | 50 | 44 | 30 | 72 | 0 | 0
2022-03-15 22:00 | 3 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 57 | 33 | 41 | 34 | 47 | 43 | 28 | 71 | 0 | 0
2022-03-15 23:00 | 3 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 57 | 33 | 41 | 32 | 48 | 42 | 26 | 69 | 0 | 0
2022-03-16 | 3 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 54 | 31 | 42 | 31 | 45 | 40 | 24 | 67 | 0 | 0
2022-03-16 01:00 | 3 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 51 | 31 | 42 | 28 | 42 | 39 | 23 | 67 | 0 | 0
2022-03-16 02:00 | 3 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 50 | 31 | 42 | 28 | 39 | 39 | 22 | 64 | 0 | 0
2022-03-16 03:00 | 3 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 48 | 31 | 41 | 29 | 38 | 38 | 20 | 61 | 0 | 0
2022-03-16 04:00 | 3 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 43 | 32 | 41 | 27 | 38 | 38 | 20 | 59 | 0 | 0
2022-03-16 05:00 | 3 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 41 | 32 | 41 | 28 | 38 | 38 | 20 | 59 | 0 | 0
2022-03-16 06:00 | 3 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 39 | 30 | 41 | 29 | 37 | 38 | 17 | 63 | 0 | 0
2022-03-16 07:00 | 3 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 36 | 30 | 41 | 34 | 32 | 38 | 20 | 67 | 0 | 0
2022-03-16 08:00 | 3 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 36 | 30 | 42 | 37 | 32 | 37 | 24 | 70 | 0 | 0
2022-03-16 09:00 | 3 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 33 | 29 | 42 | 39 | 32 | 38 | 27 | 73 | 0 | 0
2022-03-16 10:00 | 3 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 31 | 30 | 40 | 39 | 32 | 38 | 30 | 73 | 0 | 0
2022-03-16 11:00 | 3 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 31 | 31 | 41 | 44 | 32 | 38 | 34 | 74 | 0 | 0
2022-03-16 12:00 | 3 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 31 | 31 | 42 | 47 | 33 | 39 | 36 | 72 | 0 | 0
2022-03-16 13:00 | 3 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 31 | 31 | 42 | 49 | 33 | 39 | 41 | 72 | 0 | 0
2022-03-16 14:00 | 3 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 30 | 32 | 43 | 51 | 33 | 38 | 44 | 72 | 0 | 0
2022-03-16 15:00 | 3 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 29 | 32 | 43 | 52 | 34 | 36 | 41 | 72 | 0 | 0
2022-03-16 16:00 | 3 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 29 | 32 | 44 | 50 | 33 | 37 | 46 | 70 | 0 | 0
2022-03-16 17:00 | 3 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 28 | 31 | 43 | 49 | 34 | 37 | 43 | 70 | 0 | 0
2022-03-16 18:00 | 3 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 27 | 31 | 43 | 45 | 34 | 37 | 41 | 70 | 0 | 0
2022-03-16 19:00 | 3 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 25 | 31 | 43 | 41 | 34 | 37 | 39 | 70 | 0 | 0
2022-03-16 20:00 | 3 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 24 | 30 | 43 | 40 | 34 | 36 | 40 | 69 | 0 | 0
2022-03-16 21:00 | 3 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 23 | 30 | 46 | 41 | 34 | 36 | 40 | 66 | 0 | 0
2022-03-16 22:00 | 3 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 22 | 30 | 46 | 40 | 33 | 36 | 40 | 65 | 0 | 0
2022-03-16 23:00 | 3 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 22 | 31 | 49 | 38 | 33 | 36 | 39 | 65 | 0 | 0
2022-03-17 | 3 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 21 | 29 | 47 | 37 | 32 | 36 | 39 | 65 | 0 | 0
2022-03-17 01:00 | 3 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 20 | 28 | 47 | 36 | 32 | 34 | 39 | 65 | 0 | 0
2022-03-17 02:00 | 3 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 19 | 28 | 47 | 36 | 32 | 34 | 38 | 64 | 0 | 0
2022-03-17 03:00 | 3 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 19 | 28 | 41 | 35 | 31 | 34 | 40 | 65 | 0 | 0
2022-03-17 04:00 | 3 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 19 | 28 | 39 | 33 | 31 | 35 | 40 | 64 | 0 | 0
2022-03-17 05:00 | 3 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 20 | 29 | 37 | 34 | 31 | 35 | 40 | 64 | 0 | 0
2022-03-17 06:00 | 3 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 20 | 29 | 35 | 33 | 31 | 35 | 40 | 66 | 0 | 0
2022-03-17 07:00 | 3 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 22 | 30 | 35 | 39 | 31 | 34 | 42 | 66 | 0 | 0
2022-03-17 08:00 | 3 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 25 | 30 | 34 | 42 | 31 | 36 | 46 | 67 | 0 | 0
2022-03-17 09:00 | 3 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 28 | 30 | 34 | 45 | 32 | 37 | 49 | 63 | 0 | 0
2022-03-17 10:00 | 3 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 31 | 31 | 34 | 47 | 33 | 36 | 51 | 60 | 0 | 0
2022-03-17 11:00 | 3 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 33 | 32 | 34 | 44 | 34 | 38 | 48 | 57 | 0 | 0
2022-03-17 12:00 | 3 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 36 | 33 | 34 | 46 | 34 | 38 | 49 | 56 | 0 | 0
2022-03-17 13:00 | 3 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 37 | 33 | 34 | 48 | 33 | 39 | 50 | 58 | 0 | 0
2022-03-17 14:00 | 3 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 37 | 33 | 34 | 45 | 34 | 38 | 51 | 56 | 0 | 0
2022-03-17 15:00 | 3 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 37 | 33 | 34 | 42 | 34 | 40 | 52 | 55 | 0 | 0
2022-03-17 16:00 | 3 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 37 | 32 | 34 | 42 | 34 | 40 | 52 | 54 | 0 | 0
2022-03-17 17:00 | 3 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 36 | 32 | 34 | 40 | 34 | 40 | 53 | 54 | 0 | 0
2022-03-17 18:00 | 3 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 35 | 31 | 34 | 37 | 34 | 39 | 52 | 54 | 0 | 0
2022-03-17 19:00 | 3 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 34 | 31 | 34 | 36 | 34 | 38 | 54 | 53 | 0 | 0
2022-03-17 20:00 | 3 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 33 | 31 | 34 | 34 | 33 | 38 | 54 | 54 | 0 | 0
2022-03-17 21:00 | 3 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 33 | 31 | 33 | 32 | 32 | 35 | 55 | 53 | 0 | 0
2022-03-17 22:00 | 3 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 29 | 30 | 34 | 31 | 32 | 35 | 55 | 53 | 0 | 0
2022-03-17 23:00 | 3 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 27 | 30 | 33 | 31 | 32 | 32 | 55 | 52 | 0 | 0
2022-03-18 | 3 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 27 | 29 | 33 | 29 | 31 | 30 | 56 | 51 | 0 | 0
2022-03-18 01:00 | 3 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 27 | 28 | 34 | 27 | 31 | 32 | 54 | 50 | 0 | 0
2022-03-18 02:00 | 3 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 27 | 27 | 34 | 27 | 31 | 31 | 56 | 47 | 0 | 0
2022-03-18 03:00 | 3 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 28 | 27 | 34 | 27 | 32 | 29 | 56 | 49 | 0 | 0
2022-03-18 04:00 | 3 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 29 | 27 | 34 | 27 | 30 | 29 | 48 | 47 | 0 | 0
2022-03-18 05:00 | 3 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 30 | 25 | 35 | 26 | 32 | 29 | 37 | 46 | 0 | 0
2022-03-18 06:00 | 3 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 30 | 26 | 35 | 27 | 32 | 29 | 35 | 45 | 0 | 0
2022-03-18 07:00 | 3 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 30 | 27 | 36 | 29 | 33 | 32 | 35 | 45 | 0 | 0
2022-03-18 08:00 | 3 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 30 | 32 | 38 | 30 | 35 | 37 | 35 | 47 | 0 | 0
2022-03-18 09:00 | 3 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 30 | 37 | 40 | 31 | 38 | 43 | 38 | 48 | 0 | 0
2022-03-18 10:00 | 3 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 30 | 41 | 42 | 33 | 39 | 45 | 40 | 51 | 0 | 0
2022-03-18 11:00 | 3 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 31 | 43 | 43 | 35 | 40 | 49 | 40 | 50 | 0 | 0
2022-03-18 12:00 | 3 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 31 | 46 | 45 | 36 | 43 | 53 | 42 | 48 | 0 | 0
2022-03-18 13:00 | 3 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 31 | 49 | 46 | 37 | 43 | 56 | 42 | 49 | 0 | 0
2022-03-18 14:00 | 3 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 32 | 50 | 40 | 38 | 44 | 58 | 43 | 49 | 0 | 0
2022-03-18 15:00 | 3 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 32 | 50 | 37 | 39 | 45 | 59 | 42 | 48 | 0 | 0
2022-03-18 16:00 | 3 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 32 | 44 | 38 | 38 | 44 | 59 | 42 | 47 | 0 | 0
2022-03-18 17:00 | 3 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 32 | 47 | 38 | 36 | 43 | 57 | 39 | 46 | 0 | 0
2022-03-18 18:00 | 3 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 33 | 45 | 37 | 33 | 42 | 57 | 36 | 44 | 0 | 0
2022-03-18 19:00 | 3 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 33 | 44 | 37 | 33 | 42 | 56 | 34 | 43 | 0 | 0
2022-03-18 20:00 | 3 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 33 | 44 | 36 | 31 | 41 | 56 | 33 | 42 | 0 | 0
2022-03-18 21:00 | 3 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 33 | 45 | 36 | 30 | 40 | 54 | 32 | 41 | 0 | 0
2022-03-18 22:00 | 3 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 33 | 45 | 35 | 29 | 38 | 52 | 31 | 39 | 0 | 0
2022-03-18 23:00 | 3 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 33 | 50 | 35 | 28 | 37 | 51 | 30 | 33 | 0 | 0
2022-03-19 | 3 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 32 | 43 | 35 | 26 | 36 | 51 | 29 | 31 | 0 | 0
2022-03-19 01:00 | 3 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 32 | 43 | 34 | 25 | 34 | 52 | 28 | 31 | 0 | 0
2022-03-19 02:00 | 3 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 31 | 44 | 34 | 24 | 33 | 55 | 28 | 30 | 0 | 0
2022-03-19 03:00 | 3 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 31 | 44 | 34 | 21 | 34 | 61 | 28 | 31 | 0 | 0
2022-03-19 04:00 | 3 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 30 | 45 | 34 | 20 | 33 | 63 | 29 | 31 | 0 | 0
2022-03-19 05:00 | 3 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 30 | 49 | 34 | 20 | 33 | 63 | 28 | 32 | 0 | 0
2022-03-19 06:00 | 3 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 29 | 51 | 34 | 21 | 33 | 58 | 29 | 33 | 0 | 0
2022-03-19 07:00 | 3 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 30 | 52 | 33 | 28 | 33 | 58 | 31 | 35 | 0 | 0
2022-03-19 08:00 | 3 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 30 | 52 | 36 | 32 | 35 | 59 | 31 | 41 | 0 | 0
2022-03-19 09:00 | 3 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 30 | 54 | 36 | 35 | 36 | 61 | 38 | 42 | 0 | 0
2022-03-19 10:00 | 3 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 30 | 59 | 37 | 38 | 37 | 63 | 41 | 44 | 0 | 0
2022-03-19 11:00 | 3 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 31 | 57 | 37 | 41 | 40 | 65 | 44 | 45 | 0 | 0
2022-03-19 12:00 | 3 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 32 | 57 | 37 | 44 | 42 | 59 | 47 | 47 | 0 | 0
2022-03-19 13:00 | 3 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 33 | 56 | 37 | 46 | 42 | 62 | 49 | 46 | 0 | 0
2022-03-19 14:00 | 3 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 33 | 56 | 37 | 50 | 43 | 61 | 50 | 45 | 0 | 0
2022-03-19 15:00 | 3 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 34 | 53 | 36 | 49 | 42 | 60 | 52 | 45 | 0 | 0
2022-03-19 16:00 | 3 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 33 | 50 | 36 | 48 | 43 | 57 | 51 | 44 | 0 | 0
2022-03-19 17:00 | 3 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 34 | 44 | 36 | 42 | 42 | 52 | 50 | 43 | 0 | 0
2022-03-19 18:00 | 3 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 32 | 38 | 35 | 38 | 40 | 46 | 47 | 43 | 0 | 0
2022-03-19 19:00 | 3 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 32 | 35 | 35 | 37 | 39 | 46 | 46 | 41 | 0 | 0
2022-03-19 20:00 | 3 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 31 | 34 | 35 | 37 | 38 | 43 | 45 | 39 | 0 | 0
2022-03-19 21:00 | 3 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 31 | 31 | 34 | 37 | 36 | 41 | 44 | 39 | 0 | 0
2022-03-19 22:00 | 3 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 30 | 28 | 34 | 36 | 36 | 40 | 44 | 38 | 0 | 0
2022-03-19 23:00 | 3 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 30 | 26 | 32 | 34 | 35 | 37 | 43 | 36 | 0 | 0
2022-03-20 | 3 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 32 | 22 | 33 | 34 | 32 | 36 | 42 | 35 | 0 | 0
2022-03-20 01:00 | 3 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 33 | 20 | 33 | 33 | 29 | 35 | 41 | 34 | 0 | 0
2022-03-20 02:00 | 3 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 32 | 19 | 33 | 31 | 30 | 34 | 41 | 34 | 0 | 0
2022-03-20 03:00 | 3 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 32 | 18 | 33 | 31 | 30 | 34 | 42 | 33 | 0 | 0
2022-03-20 04:00 | 3 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 32 | 19 | 33 | 32 | 30 | 32 | 42 | 33 | 0 | 0
2022-03-20 05:00 | 3 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 31 | 20 | 34 | 33 | 29 | 31 | 39 | 32 | 0 | 0
2022-03-20 06:00 | 3 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 31 | 19 | 34 | 34 | 32 | 32 | 40 | 32 | 0 | 0
2022-03-20 07:00 | 3 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 31 | 19 | 36 | 37 | 35 | 29 | 43 | 31 | 0 | 0
2022-03-20 08:00 | 3 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 31 | 19 | 38 | 39 | 38 | 29 | 47 | 31 | 0 | 0
2022-03-20 09:00 | 3 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 32 | 18 | 41 | 44 | 42 | 30 | 49 | 31 | 0 | 0
2022-03-20 10:00 | 3 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 32 | 18 | 43 | 50 | 45 | 28 | 53 | 31 | 0 | 0
2022-03-20 11:00 | 3 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 69 | 32 | 18 | 45 | 50 | 48 | 28 | 55 | 32 | 0 | 0
2022-03-20 12:00 | 3 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 74 | 32 | 16 | 49 | 56 | 49 | 26 | 57 | 31 | 0 | 0
2022-03-20 13:00 | 3 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 74 | 32 | 15 | 52 | 62 | 51 | 25 | 57 | 31 | 0 | 0
2022-03-20 14:00 | 3 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 73 | 32 | 14 | 47 | 58 | 53 | 25 | 58 | 31 | 0 | 0
2022-03-20 15:00 | 3 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 73 | 32 | 15 | 45 | 60 | 53 | 25 | 57 | 32 | 0 | 0
2022-03-20 16:00 | 3 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 71 | 32 | 13 | 44 | 57 | 51 | 25 | 54 | 32 | 0 | 0
2022-03-20 17:00 | 3 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 32 | 10 | 42 | 55 | 51 | 21 | 51 | 32 | 0 | 0
2022-03-20 18:00 | 3 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 32 | 9 | 47 | 51 | 50 | 19 | 50 | 32 | 0 | 0
2022-03-20 19:00 | 3 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 32 | 8 | 45 | 51 | 47 | 19 | 50 | 31 | 0 | 0
2022-03-20 20:00 | 3 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 33 | 7 | 43 | 48 | 46 | 17 | 48 | 31 | 0 | 0
2022-03-20 21:00 | 3 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 33 | 6 | 43 | 45 | 47 | 15 | 49 | 31 | 0 | 0
2022-03-20 22:00 | 3 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 33 | 6 | 42 | 42 | 48 | 14 | 47 | 32 | 0 | 0
2022-03-20 23:00 | 3 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 32 | 6 | 42 | 40 | 51 | 13 | 49 | 33 | 0 | 0
2022-03-21 | 3 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 31 | 5 | 41 | 37 | 50 | 13 | 50 | 34 | 0 | 0
2022-03-21 01:00 | 3 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 31 | 5 | 42 | 35 | 49 | 14 | 50 | 33 | 0 | 0
2022-03-21 02:00 | 3 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 31 | 4 | 41 | 34 | 52 | 12 | 50 | 32 | 0 | 0
2022-03-21 03:00 | 3 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 30 | 3 | 41 | 34 | 51 | 13 | 50 | 31 | 0 | 0
2022-03-21 04:00 | 3 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 29 | 2 | 43 | 31 | 50 | 13 | 50 | 29 | 0 | 0
2022-03-21 05:00 | 3 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 29 | 0 | 36 | 30 | 50 | 12 | 50 | 28 | 0 | 0
2022-03-21 06:00 | 3 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 29 | 0 | 38 | 30 | 50 | 12 | 50 | 28 | 0 | 0
2022-03-21 07:00 | 3 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 29 | 4 | 37 | 32 | 50 | 14 | 51 | 31 | 0 | 0
2022-03-21 08:00 | 3 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 30 | 8 | 40 | 35 | 48 | 14 | 53 | 33 | 0 | 0
2022-03-21 09:00 | 3 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 31 | 12 | 41 | 36 | 47 | 16 | 55 | 37 | 0 | 0
2022-03-21 10:00 | 3 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 33 | 13 | 40 | 37 | 47 | 19 | 58 | 41 | 0 | 0
2022-03-21 11:00 | 3 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 69 | 36 | 16 | 40 | 38 | 47 | 22 | 56 | 44 | 0 | 0
2022-03-21 12:00 | 3 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 72 | 39 | 19 | 40 | 41 | 47 | 24 | 55 | 47 | 0 | 0
2022-03-21 13:00 | 3 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 41 | 21 | 42 | 43 | 48 | 27 | 54 | 50 | 0 | 0
2022-03-21 14:00 | 3 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 44 | 21 | 41 | 43 | 48 | 28 | 54 | 51 | 0 | 0
2022-03-21 15:00 | 3 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 42 | 23 | 38 | 44 | 47 | 29 | 53 | 51 | 0 | 0
2022-03-21 16:00 | 3 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 32 | 22 | 35 | 43 | 45 | 30 | 54 | 52 | 0 | 0
2022-03-21 17:00 | 3 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 28 | 21 | 35 | 41 | 43 | 29 | 47 | 49 | 0 | 0
2022-03-21 18:00 | 3 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 24 | 19 | 34 | 39 | 42 | 27 | 42 | 41 | 0 | 0
2022-03-21 19:00 | 3 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 20 | 17 | 34 | 36 | 40 | 26 | 39 | 38 | 0 | 0
2022-03-21 20:00 | 3 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 18 | 16 | 34 | 35 | 39 | 25 | 35 | 35 | 0 | 0
2022-03-21 21:00 | 3 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 17 | 15 | 34 | 36 | 37 | 24 | 35 | 33 | 0 | 0
2022-03-21 22:00 | 3 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 15 | 13 | 34 | 33 | 35 | 25 | 35 | 32 | 0 | 0
2022-03-21 23:00 | 3 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 14 | 13 | 34 | 34 | 34 | 20 | 34 | 31 | 0 | 0
2022-03-22 | 3 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 13 | 12 | 33 | 35 | 33 | 20 | 34 | 33 | 0 | 0
2022-03-22 01:00 | 3 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 12 | 12 | 34 | 33 | 32 | 19 | 34 | 34 | 0 | 0
2022-03-22 02:00 | 3 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 12 | 13 | 34 | 31 | 31 | 18 | 33 | 34 | 0 | 0
2022-03-22 03:00 | 3 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 11 | 13 | 33 | 32 | 30 | 19 | 33 | 34 | 0 | 0
2022-03-22 04:00 | 3 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 11 | 9 | 33 | 31 | 28 | 17 | 33 | 34 | 0 | 0
2022-03-22 05:00 | 3 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 10 | 11 | 32 | 29 | 28 | 18 | 33 | 34 | 0 | 0
2022-03-22 06:00 | 3 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 11 | 12 | 33 | 29 | 28 | 17 | 33 | 34 | 0 | 0
2022-03-22 07:00 | 3 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 12 | 16 | 33 | 32 | 28 | 21 | 32 | 41 | 0 | 0
2022-03-22 08:00 | 3 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 15 | 21 | 34 | 35 | 30 | 27 | 32 | 46 | 0 | 0
2022-03-22 09:00 | 3 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 17 | 29 | 35 | 38 | 31 | 32 | 32 | 50 | 0 | 0
2022-03-22 10:00 | 3 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 19 | 30 | 36 | 40 | 33 | 36 | 32 | 54 | 0 | 0
2022-03-22 11:00 | 3 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 19 | 33 | 38 | 44 | 36 | 36 | 33 | 57 | 0 | 0
2022-03-22 12:00 | 3 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 21 | 35 | 38 | 44 | 36 | 39 | 33 | 59 | 0 | 0
2022-03-22 13:00 | 3 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 20 | 36 | 37 | 43 | 38 | 39 | 33 | 62 | 0 | 0
2022-03-22 14:00 | 3 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 20 | 38 | 38 | 43 | 37 | 42 | 34 | 63 | 0 | 0
2022-03-22 15:00 | 3 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 21 | 39 | 37 | 39 | 37 | 43 | 34 | 65 | 0 | 0
2022-03-22 16:00 | 3 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 21 | 39 | 36 | 39 | 37 | 43 | 34 | 64 | 0 | 0
2022-03-22 17:00 | 3 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 19 | 38 | 36 | 38 | 36 | 44 | 34 | 64 | 0 | 0
2022-03-22 18:00 | 3 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 18 | 34 | 37 | 39 | 35 | 39 | 33 | 62 | 0 | 0
2022-03-22 19:00 | 3 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 18 | 33 | 38 | 39 | 34 | 36 | 33 | 58 | 0 | 0
2022-03-22 20:00 | 3 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 17 | 32 | 35 | 38 | 34 | 36 | 32 | 58 | 0 | 0
2022-03-22 21:00 | 3 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 17 | 32 | 35 | 38 | 34 | 34 | 32 | 57 | 0 | 0
2022-03-22 22:00 | 3 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 16 | 31 | 36 | 37 | 33 | 32 | 32 | 56 | 0 | 0
2022-03-22 23:00 | 3 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 17 | 31 | 35 | 36 | 32 | 31 | 31 | 56 | 0 | 0
2022-03-23 | 3 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 16 | 30 | 35 | 35 | 30 | 31 | 31 | 57 | 0 | 0
2022-03-23 01:00 | 3 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 17 | 29 | 35 | 34 | 28 | 33 | 31 | 58 | 0 | 0
2022-03-23 02:00 | 3 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 17 | 30 | 34 | 34 | 27 | 32 | 31 | 59 | 0 | 0
2022-03-23 03:00 | 3 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 17 | 30 | 34 | 33 | 28 | 30 | 31 | 56 | 0 | 0
2022-03-23 04:00 | 3 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 17 | 29 | 33 | 33 | 27 | 28 | 31 | 54 | 0 | 0
2022-03-23 05:00 | 3 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 18 | 29 | 30 | 33 | 27 | 30 | 32 | 53 | 0 | 0
2022-03-23 06:00 | 3 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 19 | 29 | 29 | 33 | 29 | 31 | 31 | 52 | 0 | 0
2022-03-23 07:00 | 3 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 21 | 32 | 34 | 34 | 32 | 38 | 32 | 50 | 0 | 0
2022-03-23 08:00 | 3 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 24 | 36 | 37 | 35 | 35 | 44 | 32 | 53 | 0 | 0
2022-03-23 09:00 | 3 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 26 | 40 | 38 | 36 | 37 | 48 | 33 | 55 | 0 | 0
2022-03-23 10:00 | 3 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 29 | 42 | 39 | 37 | 38 | 50 | 34 | 52 | 0 | 0
2022-03-23 11:00 | 3 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 33 | 42 | 40 | 38 | 41 | 50 | 35 | 50 | 0 | 0
2022-03-23 12:00 | 3 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 35 | 42 | 41 | 38 | 42 | 52 | 36 | 48 | 0 | 0
2022-03-23 13:00 | 3 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 37 | 42 | 42 | 38 | 44 | 54 | 38 | 41 | 0 | 0
2022-03-23 14:00 | 3 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 38 | 40 | 44 | 39 | 45 | 55 | 41 | 42 | 0 | 0
2022-03-23 15:00 | 3 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 40 | 39 | 45 | 39 | 46 | 55 | 42 | 43 | 0 | 0
2022-03-23 16:00 | 3 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 39 | 44 | 43 | 40 | 46 | 55 | 42 | 44 | 0 | 0
2022-03-23 17:00 | 3 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 38 | 45 | 40 | 40 | 44 | 54 | 40 | 40 | 0 | 0
2022-03-23 18:00 | 3 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 36 | 42 | 39 | 40 | 43 | 51 | 39 | 37 | 0 | 0
2022-03-23 19:00 | 3 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 36 | 41 | 39 | 40 | 42 | 46 | 37 | 35 | 0 | 0
2022-03-23 20:00 | 3 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 35 | 40 | 40 | 40 | 41 | 46 | 36 | 34 | 0 | 0
2022-03-23 21:00 | 3 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 36 | 41 | 37 | 40 | 39 | 43 | 34 | 32 | 0 | 0
2022-03-23 22:00 | 3 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 30 | 39 | 36 | 40 | 38 | 43 | 34 | 31 | 0 | 0
2022-03-23 23:00 | 3 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 28 | 38 | 35 | 40 | 37 | 41 | 32 | 30 | 0 | 0
2022-03-24 | 3 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 28 | 37 | 33 | 39 | 34 | 42 | 32 | 29 | 0 | 0
2022-03-24 01:00 | 3 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 26 | 36 | 33 | 38 | 34 | 45 | 31 | 29 | 0 | 0
2022-03-24 02:00 | 3 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 25 | 34 | 34 | 38 | 33 | 42 | 31 | 29 | 0 | 0
2022-03-24 03:00 | 3 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 24 | 31 | 34 | 38 | 34 | 38 | 30 | 29 | 0 | 0
2022-03-24 04:00 | 3 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 24 | 29 | 33 | 38 | 33 | 35 | 31 | 29 | 0 | 0
2022-03-24 05:00 | 3 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 24 | 24 | 32 | 38 | 33 | 33 | 32 | 29 | 0 | 0
2022-03-24 06:00 | 3 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 25 | 23 | 31 | 38 | 35 | 33 | 32 | 29 | 0 | 0
2022-03-24 07:00 | 3 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 28 | 24 | 37 | 40 | 39 | 33 | 35 | 30 | 0 | 0
2022-03-24 08:00 | 3 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 29 | 25 | 43 | 40 | 44 | 32 | 37 | 31 | 0 | 0
2022-03-24 09:00 | 3 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 30 | 27 | 48 | 42 | 50 | 34 | 42 | 32 | 0 | 0
2022-03-24 10:00 | 3 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 34 | 30 | 50 | 41 | 54 | 36 | 45 | 33 | 0 | 0
2022-03-24 11:00 | 3 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 36 | 34 | 52 | 41 | 57 | 39 | 47 | 34 | 0 | 0
2022-03-24 12:00 | 3 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 38 | 37 | 54 | 39 | 59 | 43 | 48 | 34 | 0 | 0
2022-03-24 13:00 | 3 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 39 | 39 | 54 | 38 | 59 | 45 | 48 | 34 | 0 | 0
2022-03-24 14:00 | 3 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 37 | 42 | 48 | 37 | 60 | 47 | 48 | 36 | 0 | 0
2022-03-24 15:00 | 3 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 35 | 42 | 50 | 36 | 59 | 48 | 47 | 34 | 0 | 0
2022-03-24 16:00 | 3 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 35 | 43 | 49 | 36 | 57 | 50 | 45 | 33 | 0 | 0
2022-03-24 17:00 | 3 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 33 | 42 | 47 | 36 | 55 | 49 | 42 | 32 | 0 | 0
2022-03-24 18:00 | 3 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 30 | 38 | 44 | 36 | 54 | 46 | 41 | 32 | 0 | 0
2022-03-24 19:00 | 3 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 30 | 34 | 38 | 36 | 52 | 44 | 41 | 32 | 0 | 0
2022-03-24 20:00 | 3 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 30 | 36 | 38 | 36 | 50 | 42 | 40 | 32 | 0 | 0
2022-03-24 21:00 | 3 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 30 | 33 | 36 | 36 | 49 | 39 | 38 | 31 | 0 | 0
2022-03-24 22:00 | 3 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 29 | 33 | 36 | 36 | 48 | 38 | 38 | 29 | 0 | 0
2022-03-24 23:00 | 3 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 27 | 34 | 36 | 36 | 46 | 37 | 38 | 28 | 0 | 0
2022-03-25 | 3 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 26 | 35 | 37 | 37 | 44 | 36 | 38 | 26 | 0 | 0
2022-03-25 01:00 | 3 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 25 | 35 | 36 | 37 | 43 | 33 | 37 | 27 | 0 | 0
2022-03-25 02:00 | 3 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 24 | 36 | 35 | 36 | 44 | 36 | 37 | 27 | 0 | 0
2022-03-25 03:00 | 3 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 25 | 36 | 33 | 37 | 45 | 37 | 37 | 28 | 0 | 0
2022-03-25 04:00 | 3 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 25 | 38 | 30 | 36 | 47 | 36 | 37 | 27 | 0 | 0
2022-03-25 05:00 | 3 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 25 | 38 | 32 | 35 | 47 | 36 | 36 | 25 | 0 | 0
2022-03-25 06:00 | 3 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 25 | 39 | 33 | 34 | 47 | 36 | 35 | 25 | 0 | 0
2022-03-25 07:00 | 3 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 25 | 43 | 38 | 36 | 48 | 41 | 36 | 28 | 0 | 0
2022-03-25 08:00 | 3 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 26 | 47 | 44 | 38 | 50 | 53 | 36 | 32 | 0 | 0
2022-03-25 09:00 | 3 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 27 | 52 | 47 | 38 | 51 | 61 | 37 | 38 | 0 | 0
2022-03-25 10:00 | 3 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 28 | 58 | 39 | 40 | 52 | 67 | 38 | 41 | 0 | 0
2022-03-25 11:00 | 3 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 30 | 62 | 40 | 42 | 54 | 69 | 39 | 43 | 0 | 0
2022-03-25 12:00 | 3 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 31 | 63 | 45 | 44 | 53 | 71 | 40 | 43 | 0 | 0
2022-03-25 13:00 | 3 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 31 | 65 | 45 | 45 | 55 | 73 | 40 | 45 | 0 | 0
2022-03-25 14:00 | 3 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 31 | 66 | 39 | 46 | 56 | 73 | 39 | 47 | 0 | 0
2022-03-25 15:00 | 3 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 27 | 66 | 37 | 47 | 58 | 74 | 40 | 48 | 0 | 0
2022-03-25 16:00 | 3 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 26 | 66 | 35 | 46 | 58 | 73 | 40 | 47 | 0 | 0
2022-03-25 17:00 | 3 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 26 | 65 | 34 | 44 | 57 | 72 | 40 | 45 | 0 | 0
2022-03-25 18:00 | 3 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 27 | 62 | 32 | 41 | 57 | 66 | 39 | 43 | 0 | 0
2022-03-25 19:00 | 3 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 26 | 61 | 32 | 39 | 54 | 64 | 38 | 40 | 0 | 0
2022-03-25 20:00 | 3 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 26 | 60 | 32 | 38 | 53 | 63 | 37 | 35 | 0 | 0
2022-03-25 21:00 | 3 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 26 | 57 | 32 | 37 | 51 | 58 | 36 | 31 | 0 | 0
2022-03-25 22:00 | 3 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 26 | 55 | 32 | 37 | 52 | 56 | 35 | 30 | 0 | 0
2022-03-25 23:00 | 3 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 26 | 54 | 31 | 37 | 53 | 56 | 35 | 28 | 0 | 0
2022-03-26 | 3 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 27 | 54 | 31 | 37 | 52 | 56 | 35 | 27 | 0 | 0
2022-03-26 01:00 | 3 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 27 | 54 | 31 | 32 | 51 | 56 | 35 | 26 | 0 | 0
2022-03-26 02:00 | 3 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 28 | 54 | 31 | 32 | 52 | 55 | 35 | 25 | 0 | 0
2022-03-26 03:00 | 3 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 54 | 31 | 31 | 51 | 52 | 34 | 24 | 0 | 0
2022-03-26 04:00 | 3 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 53 | 30 | 29 | 51 | 55 | 34 | 23 | 0 | 0
2022-03-26 05:00 | 3 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 52 | 30 | 29 | 50 | 54 | 34 | 22 | 0 | 0
2022-03-26 06:00 | 3 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 29 | 53 | 30 | 32 | 50 | 56 | 34 | 24 | 0 | 0
2022-03-26 07:00 | 3 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 30 | 55 | 30 | 37 | 55 | 60 | 34 | 30 | 0 | 0
2022-03-26 08:00 | 3 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 30 | 59 | 29 | 40 | 59 | 64 | 35 | 38 | 0 | 0
2022-03-26 09:00 | 3 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 30 | 61 | 30 | 42 | 61 | 67 | 36 | 43 | 0 | 0
2022-03-26 10:00 | 3 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 30 | 64 | 31 | 45 | 60 | 70 | 36 | 45 | 0 | 0
2022-03-26 11:00 | 3 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 30 | 67 | 30 | 48 | 64 | 72 | 36 | 48 | 0 | 0
2022-03-26 12:00 | 3 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 31 | 67 | 30 | 51 | 68 | 73 | 38 | 48 | 0 | 0
2022-03-26 13:00 | 3 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 31 | 66 | 30 | 52 | 70 | 72 | 39 | 43 | 0 | 0
2022-03-26 14:00 | 3 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 31 | 67 | 29 | 54 | 75 | 72 | 39 | 42 | 0 | 0
2022-03-26 15:00 | 3 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 32 | 67 | 29 | 55 | 73 | 71 | 39 | 46 | 0 | 0
2022-03-26 16:00 | 3 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 31 | 66 | 28 | 55 | 71 | 71 | 38 | 42 | 0 | 0
2022-03-26 17:00 | 3 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 32 | 64 | 26 | 54 | 69 | 70 | 38 | 39 | 0 | 0
2022-03-26 18:00 | 3 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 32 | 57 | 25 | 48 | 66 | 68 | 38 | 36 | 0 | 0
2022-03-26 19:00 | 3 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 32 | 49 | 25 | 43 | 64 | 60 | 38 | 34 | 0 | 0
2022-03-26 20:00 | 3 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 32 | 49 | 23 | 39 | 61 | 56 | 38 | 32 | 0 | 0
2022-03-26 21:00 | 3 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 33 | 48 | 22 | 38 | 60 | 55 | 37 | 30 | 0 | 0
2022-03-26 22:00 | 3 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 34 | 46 | 23 | 38 | 58 | 52 | 36 | 30 | 0 | 0
2022-03-26 23:00 | 3 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 35 | 44 | 23 | 35 | 56 | 51 | 36 | 28 | 0 | 0
2022-03-27 | 3 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 36 | 42 | 24 | 34 | 55 | 49 | 35 | 27 | 0 | 0
2022-03-27 01:00 | 3 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 36 | 40 | 22 | 34 | 54 | 49 | 34 | 25 | 0 | 0
2022-03-27 02:00 | 3 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 36 | 41 | 22 | 32 | 56 | 47 | 35 | 24 | 0 | 0
2022-03-27 03:00 | 3 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 35 | 41 | 20 | 31 | 56 | 49 | 33 | 23 | 0 | 0
2022-03-27 04:00 | 3 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 33 | 42 | 20 | 30 | 54 | 48 | 30 | 21 | 0 | 0
2022-03-27 05:00 | 3 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 31 | 42 | 19 | 29 | 52 | 46 | 31 | 21 | 0 | 0
2022-03-27 06:00 | 3 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 30 | 42 | 19 | 31 | 55 | 43 | 32 | 24 | 0 | 0
2022-03-27 07:00 | 3 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 30 | 41 | 20 | 37 | 56 | 41 | 35 | 26 | 0 | 0
2022-03-27 08:00 | 3 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 30 | 35 | 20 | 44 | 59 | 42 | 38 | 28 | 0 | 0
2022-03-27 09:00 | 3 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 29 | 33 | 21 | 51 | 58 | 40 | 41 | 29 | 0 | 0
2022-03-27 10:00 | 3 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 30 | 33 | 22 | 57 | 60 | 40 | 45 | 33 | 0 | 0
2022-03-27 11:00 | 3 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 30 | 33 | 24 | 67 | 64 | 43 | 47 | 34 | 0 | 0
2022-03-27 12:00 | 3 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 31 | 34 | 24 | 68 | 66 | 46 | 49 | 38 | 0 | 0
2022-03-27 13:00 | 3 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 69 | 32 | 34 | 24 | 72 | 67 | 46 | 50 | 38 | 0 | 0
2022-03-27 14:00 | 3 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 32 | 34 | 24 | 73 | 68 | 49 | 51 | 39 | 0 | 0
2022-03-27 15:00 | 3 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 31 | 33 | 24 | 69 | 69 | 47 | 52 | 41 | 0 | 0
2022-03-27 16:00 | 3 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 31 | 34 | 23 | 70 | 68 | 47 | 52 | 41 | 0 | 0
2022-03-27 17:00 | 3 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 31 | 33 | 21 | 68 | 66 | 43 | 51 | 39 | 0 | 0
2022-03-27 18:00 | 3 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 30 | 31 | 20 | 66 | 64 | 42 | 47 | 35 | 0 | 0
2022-03-27 19:00 | 3 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 30 | 31 | 20 | 65 | 62 | 40 | 44 | 33 | 0 | 0
2022-03-27 20:00 | 3 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 30 | 31 | 20 | 61 | 61 | 39 | 41 | 29 | 0 | 0
2022-03-27 21:00 | 3 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 29 | 30 | 19 | 58 | 59 | 37 | 38 | 28 | 0 | 0
2022-03-27 22:00 | 3 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 28 | 30 | 18 | 56 | 59 | 37 | 39 | 27 | 0 | 0
2022-03-27 23:00 | 3 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 27 | 30 | 13 | 60 | 57 | 31 | 37 | 24 | 0 | 0
2022-03-28 | 3 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 27 | 30 | 12 | 60 | 55 | 32 | 38 | 23 | 0 | 0
2022-03-28 01:00 | 3 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 26 | 30 | 12 | 60 | 53 | 29 | 38 | 22 | 0 | 0
2022-03-28 02:00 | 3 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 26 | 30 | 11 | 56 | 51 | 29 | 37 | 21 | 0 | 0
2022-03-28 03:00 | 3 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 25 | 30 | 13 | 54 | 51 | 28 | 38 | 19 | 0 | 0
2022-03-28 04:00 | 3 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 25 | 28 | 14 | 56 | 51 | 29 | 37 | 19 | 0 | 0
2022-03-28 05:00 | 3 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 24 | 27 | 15 | 52 | 50 | 28 | 34 | 19 | 0 | 0
2022-03-28 06:00 | 3 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 25 | 27 | 14 | 55 | 51 | 27 | 38 | 21 | 0 | 0
2022-03-28 07:00 | 3 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 28 | 31 | 20 | 56 | 52 | 33 | 40 | 26 | 0 | 0
2022-03-28 08:00 | 3 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 30 | 34 | 24 | 63 | 52 | 40 | 42 | 31 | 0 | 0
2022-03-28 09:00 | 3 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 33 | 40 | 27 | 64 | 52 | 47 | 45 | 36 | 0 | 0
2022-03-28 10:00 | 3 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 36 | 44 | 28 | 60 | 55 | 48 | 48 | 41 | 0 | 0
2022-03-28 11:00 | 3 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 39 | 47 | 30 | 61 | 55 | 51 | 52 | 47 | 0 | 0
2022-03-28 12:00 | 3 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 40 | 50 | 30 | 68 | 58 | 55 | 54 | 49 | 0 | 0
2022-03-28 13:00 | 3 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 42 | 52 | 31 | 70 | 60 | 57 | 53 | 51 | 0 | 0
2022-03-28 14:00 | 3 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 44 | 54 | 32 | 70 | 63 | 60 | 52 | 51 | 0 | 0
2022-03-28 15:00 | 3 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 45 | 56 | 33 | 64 | 60 | 61 | 52 | 53 | 0 | 0
2022-03-28 16:00 | 3 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 44 | 53 | 32 | 65 | 57 | 62 | 51 | 53 | 0 | 0
2022-03-28 17:00 | 3 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 42 | 51 | 31 | 65 | 53 | 61 | 49 | 50 | 0 | 0
2022-03-28 18:00 | 3 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 42 | 50 | 28 | 60 | 49 | 58 | 48 | 47 | 0 | 0
2022-03-28 19:00 | 3 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 41 | 47 | 27 | 57 | 46 | 55 | 48 | 44 | 0 | 0
2022-03-28 20:00 | 3 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 38 | 47 | 24 | 56 | 47 | 54 | 47 | 39 | 0 | 0
2022-03-28 21:00 | 3 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 39 | 47 | 23 | 55 | 46 | 52 | 45 | 38 | 0 | 0
2022-03-28 22:00 | 3 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 38 | 48 | 25 | 56 | 46 | 53 | 42 | 37 | 0 | 0
2022-03-28 23:00 | 3 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 33 | 50 | 26 | 56 | 46 | 53 | 42 | 33 | 0 | 0
2022-03-29 | 3 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 32 | 50 | 27 | 57 | 45 | 51 | 41 | 31 | 0 | 0
2022-03-29 01:00 | 3 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 32 | 50 | 27 | 55 | 45 | 51 | 40 | 30 | 0 | 0
2022-03-29 02:00 | 3 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 34 | 50 | 27 | 55 | 43 | 52 | 41 | 29 | 0 | 0
2022-03-29 03:00 | 3 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 33 | 48 | 28 | 54 | 42 | 48 | 41 | 27 | 0 | 0
2022-03-29 04:00 | 3 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 33 | 47 | 28 | 55 | 39 | 47 | 41 | 27 | 0 | 0
2022-03-29 05:00 | 3 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 34 | 47 | 28 | 55 | 37 | 45 | 42 | 25 | 0 | 0
2022-03-29 06:00 | 3 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 35 | 48 | 28 | 57 | 39 | 48 | 42 | 29 | 0 | 0
2022-03-29 07:00 | 3 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 39 | 51 | 31 | 58 | 40 | 55 | 43 | 33 | 0 | 0
2022-03-29 08:00 | 3 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 44 | 55 | 34 | 61 | 41 | 61 | 44 | 39 | 0 | 0
2022-03-29 09:00 | 3 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 47 | 60 | 38 | 62 | 44 | 67 | 46 | 44 | 0 | 0
2022-03-29 10:00 | 3 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 51 | 64 | 44 | 67 | 47 | 70 | 48 | 48 | 0 | 0
2022-03-29 11:00 | 3 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 53 | 66 | 45 | 70 | 50 | 72 | 49 | 48 | 0 | 0
2022-03-29 12:00 | 3 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 54 | 70 | 48 | 74 | 53 | 74 | 49 | 50 | 0 | 0
2022-03-29 13:00 | 3 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 57 | 70 | 47 | 71 | 55 | 76 | 50 | 49 | 0 | 0
2022-03-29 14:00 | 3 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 58 | 71 | 47 | 73 | 54 | 77 | 50 | 49 | 0 | 0
2022-03-29 15:00 | 3 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 58 | 72 | 47 | 72 | 53 | 77 | 50 | 47 | 0 | 0
2022-03-29 16:00 | 3 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 57 | 70 | 46 | 71 | 51 | 76 | 51 | 46 | 0 | 0
2022-03-29 17:00 | 3 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 55 | 67 | 45 | 70 | 47 | 74 | 50 | 44 | 0 | 0
2022-03-29 18:00 | 3 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 54 | 64 | 39 | 66 | 43 | 72 | 50 | 44 | 0 | 0
2022-03-29 19:00 | 3 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 52 | 63 | 36 | 62 | 41 | 68 | 49 | 44 | 0 | 0
2022-03-29 20:00 | 3 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 51 | 61 | 37 | 58 | 38 | 65 | 48 | 43 | 0 | 0
2022-03-29 21:00 | 3 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 51 | 60 | 35 | 61 | 37 | 63 | 48 | 41 | 0 | 0
2022-03-29 22:00 | 3 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 51 | 60 | 35 | 63 | 36 | 61 | 47 | 40 | 0 | 0
2022-03-29 23:00 | 3 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 50 | 59 | 41 | 59 | 37 | 60 | 46 | 39 | 0 | 0
2022-03-30 | 3 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 49 | 59 | 42 | 58 | 37 | 58 | 46 | 37 | 0 | 0
2022-03-30 01:00 | 3 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 48 | 58 | 42 | 59 | 37 | 58 | 46 | 35 | 0 | 0
2022-03-30 02:00 | 3 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 49 | 59 | 42 | 56 | 36 | 55 | 46 | 34 | 0 | 0
2022-03-30 03:00 | 3 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 49 | 59 | 45 | 52 | 36 | 57 | 45 | 34 | 0 | 0
2022-03-30 04:00 | 3 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 49 | 58 | 47 | 48 | 36 | 57 | 45 | 33 | 0 | 0
2022-03-30 05:00 | 3 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 45 | 58 | 47 | 46 | 36 | 58 | 45 | 34 | 0 | 0
2022-03-30 06:00 | 3 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 44 | 58 | 47 | 44 | 37 | 56 | 45 | 34 | 0 | 0
2022-03-30 07:00 | 3 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 44 | 60 | 48 | 46 | 37 | 63 | 45 | 35 | 0 | 0
2022-03-30 08:00 | 3 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 46 | 62 | 50 | 46 | 39 | 69 | 45 | 37 | 0 | 0
2022-03-30 09:00 | 3 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 46 | 67 | 46 | 44 | 39 | 73 | 45 | 38 | 0 | 0
2022-03-30 10:00 | 3 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 49 | 71 | 49 | 45 | 41 | 75 | 45 | 38 | 0 | 0
2022-03-30 11:00 | 3 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 52 | 74 | 56 | 42 | 42 | 78 | 45 | 38 | 0 | 0
2022-03-30 12:00 | 3 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 53 | 76 | 61 | 44 | 44 | 80 | 47 | 39 | 0 | 0
2022-03-30 13:00 | 3 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 56 | 77 | 65 | 44 | 45 | 82 | 47 | 39 | 0 | 0
2022-03-30 14:00 | 3 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 56 | 78 | 67 | 47 | 45 | 82 | 47 | 39 | 0 | 0
2022-03-30 15:00 | 3 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 56 | 78 | 68 | 47 | 43 | 82 | 47 | 39 | 0 | 0
2022-03-30 16:00 | 3 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 55 | 73 | 68 | 48 | 43 | 81 | 47 | 39 | 0 | 0
2022-03-30 17:00 | 3 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 54 | 70 | 66 | 47 | 41 | 79 | 46 | 39 | 0 | 0
2022-03-30 18:00 | 3 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 52 | 63 | 64 | 46 | 40 | 76 | 47 | 39 | 0 | 0
2022-03-30 19:00 | 3 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 47 | 62 | 64 | 45 | 40 | 72 | 47 | 39 | 0 | 0
2022-03-30 20:00 | 3 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 46 | 60 | 64 | 43 | 40 | 70 | 46 | 38 | 0 | 0
2022-03-30 21:00 | 3 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 44 | 58 | 63 | 42 | 39 | 70 | 45 | 38 | 0 | 0
2022-03-30 22:00 | 3 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 43 | 53 | 62 | 41 | 40 | 70 | 45 | 38 | 0 | 0
2022-03-30 23:00 | 3 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 44 | 51 | 53 | 41 | 40 | 67 | 45 | 38 | 0 | 0
2022-03-31 | 3 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 44 | 49 | 48 | 41 | 40 | 63 | 44 | 38 | 0 | 0
2022-03-31 01:00 | 3 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 43 | 44 | 50 | 40 | 41 | 59 | 44 | 37 | 0 | 0
2022-03-31 02:00 | 3 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 42 | 42 | 50 | 40 | 41 | 58 | 43 | 38 | 0 | 0
2022-03-31 03:00 | 3 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 42 | 38 | 50 | 40 | 41 | 55 | 42 | 38 | 0 | 0
2022-03-31 04:00 | 3 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 42 | 36 | 52 | 40 | 41 | 52 | 41 | 38 | 0 | 0
2022-03-31 05:00 | 3 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 39 | 33 | 50 | 40 | 41 | 50 | 41 | 38 | 0 | 0
2022-03-31 06:00 | 3 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 42 | 36 | 51 | 40 | 42 | 49 | 41 | 38 | 0 | 0
2022-03-31 07:00 | 3 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 45 | 42 | 54 | 41 | 43 | 50 | 41 | 39 | 0 | 0
2022-03-31 08:00 | 3 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 47 | 47 | 57 | 42 | 44 | 56 | 41 | 40 | 0 | 0
2022-03-31 09:00 | 3 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 49 | 52 | 61 | 42 | 45 | 62 | 41 | 42 | 0 | 0
2022-03-31 10:00 | 3 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 52 | 57 | 64 | 42 | 46 | 65 | 41 | 42 | 0 | 0
2022-03-31 11:00 | 3 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 52 | 60 | 66 | 41 | 47 | 68 | 40 | 41 | 0 | 0
2022-03-31 12:00 | 3 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 54 | 64 | 70 | 40 | 48 | 72 | 39 | 42 | 0 | 0
2022-03-31 13:00 | 3 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 55 | 66 | 66 | 39 | 49 | 72 | 38 | 43 | 0 | 0
2022-03-31 14:00 | 3 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 55 | 69 | 44 | 39 | 49 | 76 | 38 | 43 | 0 | 0
2022-03-31 15:00 | 3 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 54 | 70 | 53 | 39 | 49 | 77 | 37 | 43 | 0 | 0
2022-03-31 16:00 | 3 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 54 | 70 | 48 | 39 | 49 | 75 | 37 | 43 | 0 | 0
2022-03-31 17:00 | 3 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 52 | 68 | 46 | 38 | 48 | 76 | 34 | 44 | 0 | 0
2022-03-31 18:00 | 3 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 48 | 62 | 43 | 38 | 49 | 73 | 34 | 43 | 0 | 0
2022-03-31 19:00 | 3 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 46 | 58 | 43 | 38 | 49 | 68 | 34 | 43 | 0 | 0
2022-03-31 20:00 | 3 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 43 | 57 | 45 | 38 | 48 | 67 | 34 | 43 | 0 | 0
2022-03-31 21:00 | 3 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 41 | 54 | 43 | 39 | 47 | 67 | 34 | 43 | 0 | 0
2022-03-31 22:00 | 3 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 40 | 50 | 41 | 40 | 45 | 66 | 33 | 43 | 0 | 0
2022-03-31 23:00 | 3 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 38 | 47 | 39 | 41 | 44 | 66 | 33 | 43 | 0 | 0
2022-04-01 | 4 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 37 | 43 | 37 | 42 | 42 | 66 | 32 | 43 | 0 | 0
2022-04-01 01:00 | 4 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 35 | 40 | 35 | 43 | 41 | 65 | 32 | 43 | 0 | 0
2022-04-01 02:00 | 4 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 34 | 37 | 33 | 44 | 39 | 65 | 31 | 43 | 0 | 0
2022-04-01 03:00 | 4 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 32 | 33 | 31 | 45 | 38 | 65 | 31 | 43 | 0 | 0
2022-04-01 04:00 | 4 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 31 | 33 | 29 | 43 | 37 | 65 | 29 | 43 | 0 | 0
2022-04-01 05:00 | 4 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 31 | 32 | 28 | 45 | 36 | 64 | 28 | 43 | 0 | 0
2022-04-01 06:00 | 4 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 33 | 32 | 28 | 45 | 38 | 65 | 30 | 43 | 0 | 0
2022-04-01 07:00 | 4 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 35 | 34 | 34 | 48 | 43 | 68 | 32 | 43 | 0 | 0
2022-04-01 08:00 | 4 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 38 | 36 | 36 | 50 | 45 | 70 | 33 | 44 | 0 | 0
2022-04-01 09:00 | 4 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 42 | 38 | 37 | 52 | 46 | 72 | 34 | 45 | 0 | 0
2022-04-01 10:00 | 4 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 44 | 39 | 37 | 52 | 46 | 73 | 36 | 45 | 0 | 0
2022-04-01 11:00 | 4 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 44 | 39 | 38 | 54 | 51 | 71 | 42 | 45 | 0 | 0
2022-04-01 12:00 | 4 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 47 | 40 | 39 | 52 | 50 | 76 | 46 | 45 | 0 | 0
2022-04-01 13:00 | 4 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 48 | 40 | 40 | 54 | 52 | 77 | 49 | 46 | 0 | 0
2022-04-01 14:00 | 4 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 49 | 41 | 41 | 54 | 52 | 76 | 51 | 46 | 0 | 0
2022-04-01 15:00 | 4 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 50 | 41 | 41 | 52 | 51 | 77 | 52 | 46 | 0 | 0
2022-04-01 16:00 | 4 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 50 | 41 | 40 | 52 | 50 | 75 | 52 | 46 | 0 | 0
2022-04-01 17:00 | 4 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 47 | 41 | 38 | 52 | 50 | 73 | 51 | 46 | 0 | 0
2022-04-01 18:00 | 4 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 44 | 41 | 37 | 50 | 48 | 68 | 47 | 46 | 0 | 0
2022-04-01 19:00 | 4 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 41 | 41 | 39 | 46 | 47 | 60 | 45 | 46 | 0 | 0
2022-04-01 20:00 | 4 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 40 | 40 | 38 | 43 | 47 | 53 | 44 | 46 | 0 | 0
2022-04-01 21:00 | 4 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 42 | 40 | 38 | 39 | 46 | 49 | 43 | 45 | 0 | 0
2022-04-01 22:00 | 4 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 42 | 40 | 35 | 41 | 44 | 46 | 40 | 46 | 0 | 0
2022-04-01 23:00 | 4 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 42 | 39 | 33 | 43 | 44 | 44 | 43 | 45 | 0 | 0
2022-04-02 | 4 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 41 | 39 | 39 | 41 | 43 | 42 | 44 | 46 | 0 | 0
2022-04-02 01:00 | 4 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 40 | 38 | 45 | 41 | 43 | 39 | 43 | 46 | 0 | 0
2022-04-02 02:00 | 4 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 41 | 38 | 48 | 39 | 42 | 37 | 43 | 46 | 0 | 0
2022-04-02 03:00 | 4 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 41 | 37 | 50 | 43 | 41 | 35 | 43 | 46 | 0 | 0
2022-04-02 04:00 | 4 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 40 | 37 | 50 | 41 | 42 | 33 | 42 | 47 | 0 | 0
2022-04-02 05:00 | 4 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 40 | 37 | 47 | 43 | 40 | 33 | 42 | 48 | 0 | 0
2022-04-02 06:00 | 4 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 40 | 37 | 46 | 43 | 42 | 32 | 42 | 48 | 0 | 0
2022-04-02 07:00 | 4 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 39 | 39 | 47 | 48 | 46 | 34 | 42 | 50 | 0 | 0
2022-04-02 08:00 | 4 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 39 | 40 | 47 | 52 | 49 | 37 | 43 | 55 | 0 | 0
2022-04-02 09:00 | 4 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 40 | 42 | 48 | 52 | 47 | 38 | 46 | 54 | 0 | 0
2022-04-02 10:00 | 4 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 42 | 42 | 50 | 55 | 45 | 39 | 46 | 57 | 0 | 0
2022-04-02 11:00 | 4 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 46 | 43 | 52 | 61 | 49 | 43 | 48 | 58 | 0 | 0
2022-04-02 12:00 | 4 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 45 | 43 | 54 | 63 | 48 | 46 | 51 | 57 | 0 | 0
2022-04-02 13:00 | 4 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 43 | 43 | 57 | 64 | 49 | 47 | 51 | 60 | 0 | 0
2022-04-02 14:00 | 4 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 45 | 44 | 58 | 66 | 50 | 47 | 50 | 56 | 0 | 0
2022-04-02 15:00 | 4 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 44 | 44 | 58 | 66 | 49 | 48 | 49 | 54 | 0 | 0
2022-04-02 16:00 | 4 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 44 | 43 | 60 | 64 | 49 | 45 | 48 | 53 | 0 | 0
2022-04-02 17:00 | 4 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 44 | 43 | 62 | 63 | 48 | 42 | 48 | 52 | 0 | 0
2022-04-02 18:00 | 4 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 42 | 42 | 62 | 61 | 47 | 41 | 48 | 51 | 0 | 0
2022-04-02 19:00 | 4 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 41 | 40 | 62 | 61 | 45 | 40 | 46 | 50 | 0 | 0
2022-04-02 20:00 | 4 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 39 | 39 | 63 | 59 | 43 | 39 | 45 | 49 | 0 | 0
2022-04-02 21:00 | 4 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 39 | 37 | 64 | 61 | 42 | 39 | 44 | 50 | 0 | 0
2022-04-02 22:00 | 4 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 37 | 35 | 55 | 61 | 40 | 40 | 44 | 49 | 0 | 0
2022-04-02 23:00 | 4 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 38 | 32 | 60 | 64 | 39 | 41 | 42 | 47 | 0 | 0
2022-04-03 | 4 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 38 | 30 | 54 | 64 | 39 | 42 | 41 | 46 | 0 | 0
2022-04-03 01:00 | 4 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 37 | 29 | 50 | 64 | 39 | 40 | 38 | 45 | 0 | 0
2022-04-03 02:00 | 4 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 35 | 27 | 49 | 63 | 38 | 40 | 37 | 45 | 0 | 0
2022-04-03 03:00 | 4 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 34 | 26 | 43 | 63 | 36 | 40 | 40 | 44 | 0 | 0
2022-04-03 04:00 | 4 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 34 | 27 | 38 | 63 | 35 | 40 | 39 | 44 | 0 | 0
2022-04-03 05:00 | 4 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 33 | 28 | 37 | 61 | 36 | 40 | 36 | 43 | 0 | 0
2022-04-03 06:00 | 4 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 35 | 29 | 37 | 57 | 41 | 40 | 38 | 43 | 0 | 0
2022-04-03 07:00 | 4 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 37 | 30 | 37 | 63 | 46 | 41 | 41 | 44 | 0 | 0
2022-04-03 08:00 | 4 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 39 | 32 | 37 | 64 | 50 | 42 | 42 | 45 | 0 | 0
2022-04-03 09:00 | 4 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 43 | 33 | 39 | 64 | 52 | 43 | 45 | 45 | 0 | 0
2022-04-03 10:00 | 4 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 46 | 40 | 41 | 63 | 54 | 44 | 48 | 45 | 0 | 0
2022-04-03 11:00 | 4 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 49 | 46 | 41 | 57 | 56 | 46 | 52 | 46 | 0 | 0
2022-04-03 12:00 | 4 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 51 | 53 | 42 | 48 | 57 | 47 | 56 | 47 | 0 | 0
2022-04-03 13:00 | 4 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 53 | 54 | 43 | 46 | 57 | 48 | 57 | 47 | 0 | 0
2022-04-03 14:00 | 4 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 55 | 56 | 43 | 46 | 58 | 50 | 59 | 47 | 0 | 0
2022-04-03 15:00 | 4 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 55 | 57 | 44 | 46 | 58 | 55 | 60 | 47 | 0 | 0
2022-04-03 16:00 | 4 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 53 | 56 | 40 | 48 | 57 | 56 | 60 | 46 | 0 | 0
2022-04-03 17:00 | 4 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 51 | 54 | 38 | 46 | 54 | 56 | 59 | 45 | 0 | 0
2022-04-03 18:00 | 4 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 49 | 53 | 36 | 45 | 51 | 55 | 57 | 43 | 0 | 0
2022-04-03 19:00 | 4 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 48 | 52 | 35 | 43 | 50 | 54 | 57 | 43 | 0 | 0
2022-04-03 20:00 | 4 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 47 | 50 | 35 | 43 | 50 | 53 | 55 | 42 | 0 | 0
2022-04-03 21:00 | 4 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 48 | 49 | 33 | 39 | 50 | 52 | 54 | 42 | 0 | 0
2022-04-03 22:00 | 4 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 49 | 49 | 34 | 39 | 50 | 52 | 53 | 40 | 0 | 0
2022-04-03 23:00 | 4 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 50 | 48 | 34 | 39 | 49 | 53 | 51 | 40 | 0 | 0
2022-04-04 | 4 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 49 | 48 | 34 | 37 | 49 | 52 | 50 | 40 | 0 | 0
2022-04-04 01:00 | 4 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 47 | 48 | 32 | 36 | 48 | 52 | 50 | 39 | 0 | 0
2022-04-04 02:00 | 4 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 43 | 48 | 34 | 32 | 47 | 52 | 48 | 39 | 0 | 0
2022-04-04 03:00 | 4 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 41 | 48 | 35 | 30 | 51 | 53 | 45 | 39 | 0 | 0
2022-04-04 04:00 | 4 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 40 | 49 | 36 | 32 | 52 | 53 | 45 | 39 | 0 | 0
2022-04-04 05:00 | 4 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 41 | 49 | 38 | 32 | 55 | 54 | 44 | 39 | 0 | 0
2022-04-04 06:00 | 4 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 42 | 50 | 41 | 36 | 55 | 56 | 45 | 39 | 0 | 0
2022-04-04 07:00 | 4 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 43 | 50 | 42 | 37 | 56 | 61 | 46 | 40 | 0 | 0
2022-04-04 08:00 | 4 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 45 | 50 | 41 | 39 | 58 | 67 | 46 | 39 | 0 | 0
2022-04-04 09:00 | 4 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 46 | 50 | 42 | 43 | 60 | 72 | 50 | 40 | 0 | 0
2022-04-04 10:00 | 4 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 48 | 48 | 42 | 43 | 66 | 75 | 50 | 39 | 0 | 0
2022-04-04 11:00 | 4 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 51 | 46 | 45 | 45 | 65 | 75 | 51 | 37 | 0 | 0
2022-04-04 12:00 | 4 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 52 | 44 | 47 | 47 | 65 | 71 | 53 | 36 | 0 | 0
2022-04-04 13:00 | 4 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 54 | 43 | 44 | 48 | 66 | 65 | 54 | 36 | 0 | 0
2022-04-04 14:00 | 4 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 55 | 41 | 44 | 48 | 66 | 64 | 58 | 37 | 0 | 0
2022-04-04 15:00 | 4 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 46 | 40 | 44 | 50 | 65 | 62 | 54 | 36 | 0 | 0
2022-04-04 16:00 | 4 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 46 | 38 | 45 | 48 | 62 | 64 | 57 | 37 | 0 | 0
2022-04-04 17:00 | 4 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 47 | 36 | 45 | 46 | 55 | 63 | 53 | 37 | 0 | 0
2022-04-04 18:00 | 4 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 44 | 34 | 47 | 45 | 49 | 62 | 51 | 38 | 0 | 0
2022-04-04 19:00 | 4 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 44 | 33 | 48 | 43 | 44 | 61 | 50 | 40 | 0 | 0
2022-04-04 20:00 | 4 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 42 | 33 | 49 | 39 | 42 | 59 | 48 | 42 | 0 | 0
2022-04-04 21:00 | 4 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 39 | 32 | 46 | 37 | 38 | 61 | 47 | 43 | 0 | 0
2022-04-04 22:00 | 4 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 37 | 32 | 46 | 39 | 36 | 60 | 45 | 41 | 0 | 0
2022-04-04 23:00 | 4 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 35 | 31 | 47 | 37 | 33 | 60 | 44 | 37 | 0 | 0
2022-04-05 | 4 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 35 | 31 | 48 | 37 | 32 | 57 | 42 | 37 | 0 | 0
2022-04-05 01:00 | 4 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 34 | 31 | 50 | 36 | 31 | 53 | 40 | 36 | 0 | 0
2022-04-05 02:00 | 4 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 34 | 32 | 47 | 36 | 29 | 49 | 40 | 34 | 0 | 0
2022-04-05 03:00 | 4 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 32 | 32 | 42 | 30 | 28 | 46 | 39 | 33 | 0 | 0
2022-04-05 04:00 | 4 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 33 | 32 | 40 | 28 | 28 | 44 | 39 | 33 | 0 | 0
2022-04-05 05:00 | 4 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 33 | 32 | 41 | 27 | 27 | 42 | 38 | 35 | 0 | 0
2022-04-05 06:00 | 4 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 33 | 32 | 41 | 30 | 28 | 41 | 38 | 40 | 0 | 0
2022-04-05 07:00 | 4 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 33 | 34 | 41 | 34 | 32 | 40 | 38 | 43 | 0 | 0
2022-04-05 08:00 | 4 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 34 | 36 | 43 | 36 | 34 | 40 | 39 | 46 | 0 | 0
2022-04-05 09:00 | 4 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 39 | 38 | 41 | 36 | 34 | 41 | 42 | 45 | 0 | 0
2022-04-05 10:00 | 4 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 43 | 41 | 43 | 39 | 37 | 44 | 47 | 46 | 0 | 0
2022-04-05 11:00 | 4 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 72 | 46 | 43 | 42 | 39 | 39 | 46 | 51 | 49 | 0 | 0
2022-04-05 12:00 | 4 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 77 | 46 | 46 | 43 | 43 | 42 | 47 | 53 | 51 | 0 | 0
2022-04-05 13:00 | 4 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 80 | 47 | 47 | 42 | 45 | 41 | 52 | 53 | 53 | 0 | 0
2022-04-05 14:00 | 4 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 81 | 50 | 47 | 39 | 45 | 42 | 53 | 53 | 52 | 0 | 0
2022-04-05 15:00 | 4 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 79 | 51 | 48 | 33 | 45 | 43 | 55 | 54 | 52 | 0 | 0
2022-04-05 16:00 | 4 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 78 | 50 | 47 | 34 | 45 | 43 | 57 | 54 | 52 | 0 | 0
2022-04-05 17:00 | 4 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 76 | 48 | 45 | 33 | 43 | 42 | 55 | 53 | 51 | 0 | 0
2022-04-05 18:00 | 4 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 73 | 46 | 44 | 34 | 43 | 40 | 54 | 51 | 51 | 0 | 0
2022-04-05 19:00 | 4 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 71 | 44 | 43 | 33 | 41 | 37 | 50 | 49 | 44 | 0 | 0
2022-04-05 20:00 | 4 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 43 | 41 | 33 | 37 | 37 | 48 | 48 | 42 | 0 | 0
2022-04-05 21:00 | 4 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 43 | 40 | 32 | 36 | 37 | 46 | 47 | 40 | 0 | 0
2022-04-05 22:00 | 4 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 42 | 39 | 32 | 36 | 35 | 44 | 47 | 41 | 0 | 0
2022-04-05 23:00 | 4 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 41 | 39 | 32 | 36 | 35 | 45 | 46 | 41 | 0 | 0
2022-04-06 | 4 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 39 | 38 | 31 | 34 | 36 | 44 | 45 | 41 | 0 | 0
2022-04-06 01:00 | 4 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 69 | 38 | 37 | 31 | 34 | 36 | 44 | 43 | 40 | 0 | 0
2022-04-06 02:00 | 4 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 36 | 37 | 31 | 34 | 35 | 44 | 40 | 39 | 0 | 0
2022-04-06 03:00 | 4 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 35 | 36 | 31 | 30 | 35 | 44 | 40 | 39 | 0 | 0
2022-04-06 04:00 | 4 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 36 | 35 | 30 | 30 | 34 | 44 | 39 | 38 | 0 | 0
2022-04-06 05:00 | 4 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 35 | 33 | 29 | 30 | 33 | 44 | 40 | 37 | 0 | 0
2022-04-06 06:00 | 4 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 38 | 32 | 29 | 32 | 34 | 45 | 41 | 38 | 0 | 0
2022-04-06 07:00 | 4 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 42 | 38 | 29 | 34 | 36 | 46 | 45 | 41 | 0 | 0
2022-04-06 08:00 | 4 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 45 | 44 | 30 | 36 | 40 | 45 | 48 | 42 | 0 | 0
2022-04-06 09:00 | 4 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 47 | 50 | 29 | 39 | 43 | 44 | 51 | 44 | 0 | 0
2022-04-06 10:00 | 4 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 49 | 52 | 30 | 39 | 47 | 45 | 55 | 46 | 0 | 0
2022-04-06 11:00 | 4 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 51 | 54 | 33 | 39 | 49 | 46 | 57 | 45 | 0 | 0
2022-04-06 12:00 | 4 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 53 | 56 | 34 | 43 | 51 | 47 | 59 | 45 | 0 | 0
2022-04-06 13:00 | 4 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 54 | 57 | 31 | 43 | 52 | 50 | 60 | 45 | 0 | 0
2022-04-06 14:00 | 4 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 54 | 58 | 30 | 45 | 53 | 51 | 60 | 45 | 0 | 0
2022-04-06 15:00 | 4 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 54 | 59 | 29 | 43 | 53 | 52 | 61 | 45 | 0 | 0
2022-04-06 16:00 | 4 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 54 | 58 | 31 | 43 | 54 | 53 | 60 | 45 | 0 | 0
2022-04-06 17:00 | 4 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 52 | 56 | 29 | 41 | 53 | 55 | 58 | 44 | 0 | 0
2022-04-06 18:00 | 4 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 48 | 55 | 28 | 41 | 50 | 53 | 55 | 43 | 0 | 0
2022-04-06 19:00 | 4 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 46 | 51 | 28 | 39 | 49 | 52 | 53 | 40 | 0 | 0
2022-04-06 20:00 | 4 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 45 | 46 | 28 | 37 | 49 | 52 | 50 | 40 | 0 | 0
2022-04-06 21:00 | 4 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 44 | 42 | 28 | 37 | 48 | 53 | 48 | 40 | 0 | 0
2022-04-06 22:00 | 4 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 43 | 44 | 30 | 36 | 49 | 52 | 49 | 39 | 0 | 0
2022-04-06 23:00 | 4 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 40 | 46 | 30 | 36 | 48 | 52 | 48 | 38 | 0 | 0
2022-04-07 | 4 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 41 | 48 | 29 | 27 | 47 | 57 | 48 | 37 | 0 | 0
2022-04-07 01:00 | 4 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 42 | 47 | 28 | 27 | 47 | 57 | 49 | 37 | 0 | 0
2022-04-07 02:00 | 4 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 42 | 47 | 27 | 27 | 46 | 57 | 47 | 35 | 0 | 0
2022-04-07 03:00 | 4 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 41 | 46 | 27 | 27 | 45 | 53 | 45 | 32 | 0 | 0
2022-04-07 04:00 | 4 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 42 | 46 | 23 | 25 | 44 | 51 | 44 | 31 | 0 | 0
2022-04-07 05:00 | 4 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 41 | 47 | 22 | 25 | 43 | 50 | 43 | 31 | 0 | 0
2022-04-07 06:00 | 4 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 45 | 47 | 24 | 28 | 47 | 49 | 48 | 32 | 0 | 0
2022-04-07 07:00 | 4 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 48 | 51 | 31 | 36 | 52 | 51 | 55 | 32 | 0 | 0
2022-04-07 08:00 | 4 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 53 | 54 | 30 | 37 | 58 | 52 | 58 | 32 | 0 | 0
2022-04-07 09:00 | 4 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 58 | 58 | 35 | 39 | 60 | 56 | 60 | 34 | 0 | 0
2022-04-07 10:00 | 4 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 61 | 59 | 39 | 43 | 61 | 60 | 61 | 39 | 0 | 0
2022-04-07 11:00 | 4 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 62 | 59 | 39 | 45 | 62 | 63 | 61 | 41 | 0 | 0
2022-04-07 12:00 | 4 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 61 | 60 | 39 | 46 | 62 | 67 | 65 | 45 | 0 | 0
2022-04-07 13:00 | 4 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 61 | 60 | 37 | 48 | 63 | 68 | 64 | 46 | 0 | 0
2022-04-07 14:00 | 4 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 61 | 60 | 37 | 48 | 63 | 70 | 63 | 47 | 0 | 0
2022-04-07 15:00 | 4 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 60 | 60 | 36 | 52 | 62 | 71 | 62 | 47 | 0 | 0
2022-04-07 16:00 | 4 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 58 | 59 | 37 | 50 | 62 | 71 | 61 | 44 | 0 | 0
2022-04-07 17:00 | 4 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 55 | 57 | 37 | 48 | 60 | 69 | 59 | 41 | 0 | 0
2022-04-07 18:00 | 4 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 53 | 56 | 36 | 48 | 56 | 66 | 56 | 41 | 0 | 0
2022-04-07 19:00 | 4 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 51 | 54 | 35 | 45 | 54 | 63 | 53 | 38 | 0 | 0
2022-04-07 20:00 | 4 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 49 | 53 | 38 | 45 | 52 | 61 | 52 | 36 | 0 | 0
2022-04-07 21:00 | 4 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 48 | 51 | 39 | 45 | 50 | 60 | 51 | 34 | 0 | 0
2022-04-07 22:00 | 4 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 46 | 51 | 33 | 45 | 48 | 58 | 50 | 33 | 0 | 0
2022-04-07 23:00 | 4 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 46 | 51 | 33 | 45 | 47 | 54 | 50 | 31 | 0 | 0
2022-04-08 | 4 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 46 | 51 | 31 | 45 | 43 | 50 | 49 | 31 | 0 | 0
2022-04-08 01:00 | 4 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 46 | 50 | 30 | 41 | 42 | 48 | 49 | 29 | 0 | 0
2022-04-08 02:00 | 4 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 46 | 49 | 28 | 41 | 41 | 46 | 49 | 31 | 0 | 0
2022-04-08 03:00 | 4 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 45 | 48 | 28 | 39 | 41 | 45 | 49 | 31 | 0 | 0
2022-04-08 04:00 | 4 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 45 | 48 | 25 | 39 | 40 | 44 | 50 | 31 | 0 | 0
2022-04-08 05:00 | 4 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 45 | 47 | 24 | 41 | 41 | 44 | 50 | 31 | 0 | 0
2022-04-08 06:00 | 4 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 46 | 47 | 23 | 41 | 44 | 43 | 50 | 33 | 0 | 0
2022-04-08 07:00 | 4 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 49 | 49 | 22 | 43 | 46 | 44 | 50 | 35 | 0 | 0
2022-04-08 08:00 | 4 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 49 | 52 | 24 | 45 | 49 | 45 | 51 | 38 | 0 | 0
2022-04-08 09:00 | 4 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 52 | 54 | 25 | 46 | 52 | 47 | 53 | 39 | 0 | 0
2022-04-08 10:00 | 4 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 56 | 55 | 26 | 50 | 56 | 48 | 57 | 43 | 0 | 0
2022-04-08 11:00 | 4 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 57 | 56 | 27 | 54 | 60 | 51 | 60 | 45 | 0 | 0
2022-04-08 12:00 | 4 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 60 | 57 | 28 | 57 | 64 | 52 | 63 | 47 | 0 | 0
2022-04-08 13:00 | 4 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 59 | 56 | 29 | 61 | 64 | 53 | 64 | 46 | 0 | 0
2022-04-08 14:00 | 4 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 58 | 56 | 28 | 64 | 66 | 54 | 63 | 50 | 0 | 0
2022-04-08 15:00 | 4 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 58 | 55 | 28 | 66 | 66 | 53 | 65 | 50 | 0 | 0
2022-04-08 16:00 | 4 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 59 | 54 | 26 | 66 | 58 | 51 | 62 | 50 | 0 | 0
2022-04-08 17:00 | 4 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 57 | 53 | 26 | 63 | 58 | 50 | 62 | 48 | 0 | 0
2022-04-08 18:00 | 4 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 55 | 52 | 26 | 61 | 52 | 46 | 61 | 46 | 0 | 0
2022-04-08 19:00 | 4 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 54 | 51 | 25 | 61 | 50 | 42 | 59 | 40 | 0 | 0
2022-04-08 20:00 | 4 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 52 | 51 | 25 | 60 | 50 | 39 | 56 | 37 | 0 | 0
2022-04-08 21:00 | 4 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 51 | 50 | 24 | 59 | 48 | 37 | 56 | 33 | 0 | 0
2022-04-08 22:00 | 4 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 51 | 50 | 24 | 59 | 48 | 36 | 56 | 31 | 0 | 0
2022-04-08 23:00 | 4 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 51 | 50 | 20 | 59 | 48 | 34 | 56 | 30 | 0 | 0
2022-04-09 | 4 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 51 | 50 | 18 | 61 | 48 | 33 | 56 | 29 | 0 | 0
2022-04-09 01:00 | 4 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 50 | 49 | 18 | 61 | 48 | 32 | 55 | 27 | 0 | 0
2022-04-09 02:00 | 4 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 49 | 49 | 18 | 61 | 48 | 31 | 55 | 27 | 0 | 0
2022-04-09 03:00 | 4 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 48 | 48 | 17 | 61 | 49 | 31 | 55 | 28 | 0 | 0
2022-04-09 04:00 | 4 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 49 | 48 | 18 | 61 | 49 | 30 | 55 | 28 | 0 | 0
2022-04-09 05:00 | 4 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 49 | 47 | 19 | 63 | 49 | 29 | 56 | 28 | 0 | 0
2022-04-09 06:00 | 4 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 51 | 47 | 22 | 63 | 50 | 31 | 56 | 31 | 0 | 0
2022-04-09 07:00 | 4 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 51 | 49 | 27 | 64 | 52 | 34 | 57 | 35 | 0 | 0
2022-04-09 08:00 | 4 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 52 | 52 | 31 | 66 | 54 | 37 | 58 | 40 | 0 | 0
2022-04-09 09:00 | 4 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 54 | 54 | 34 | 66 | 57 | 42 | 61 | 47 | 0 | 0
2022-04-09 10:00 | 4 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 53 | 55 | 36 | 68 | 64 | 45 | 59 | 55 | 0 | 0
2022-04-09 11:00 | 4 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 54 | 55 | 38 | 68 | 66 | 49 | 59 | 58 | 0 | 0
2022-04-09 12:00 | 4 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 53 | 56 | 38 | 68 | 70 | 52 | 61 | 62 | 0 | 0
2022-04-09 13:00 | 4 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 53 | 58 | 39 | 66 | 71 | 56 | 63 | 63 | 0 | 0
2022-04-09 14:00 | 4 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 54 | 59 | 39 | 64 | 74 | 56 | 60 | 62 | 0 | 0
2022-04-09 15:00 | 4 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 56 | 61 | 39 | 64 | 75 | 56 | 61 | 64 | 0 | 0
2022-04-09 16:00 | 4 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 56 | 58 | 40 | 64 | 76 | 57 | 61 | 63 | 0 | 0
2022-04-09 17:00 | 4 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 56 | 56 | 39 | 63 | 76 | 55 | 60 | 62 | 0 | 0
2022-04-09 18:00 | 4 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 54 | 53 | 34 | 63 | 74 | 53 | 59 | 60 | 0 | 0
2022-04-09 19:00 | 4 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 54 | 51 | 32 | 63 | 73 | 50 | 59 | 58 | 0 | 0
2022-04-09 20:00 | 4 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 54 | 48 | 30 | 61 | 51 | 50 | 58 | 58 | 0 | 0
2022-04-09 21:00 | 4 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 48 | 46 | 28 | 57 | 50 | 48 | 59 | 58 | 0 | 0
2022-04-09 22:00 | 4 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 46 | 46 | 28 | 59 | 47 | 48 | 50 | 56 | 0 | 0
2022-04-09 23:00 | 4 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 45 | 45 | 28 | 55 | 47 | 50 | 49 | 53 | 0 | 0
2022-04-10 | 4 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 45 | 45 | 30 | 54 | 46 | 50 | 48 | 53 | 0 | 0
2022-04-10 01:00 | 4 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 43 | 44 | 30 | 50 | 46 | 50 | 46 | 52 | 0 | 0
2022-04-10 02:00 | 4 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 42 | 43 | 31 | 48 | 44 | 49 | 45 | 51 | 0 | 0
2022-04-10 03:00 | 4 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 41 | 42 | 32 | 48 | 44 | 48 | 44 | 51 | 0 | 0
2022-04-10 04:00 | 4 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 42 | 41 | 31 | 48 | 42 | 46 | 42 | 52 | 0 | 0
2022-04-10 05:00 | 4 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 43 | 40 | 32 | 48 | 41 | 45 | 42 | 52 | 0 | 0
2022-04-10 06:00 | 4 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 44 | 39 | 34 | 48 | 42 | 48 | 41 | 50 | 0 | 0
2022-04-10 07:00 | 4 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 48 | 39 | 38 | 50 | 42 | 51 | 44 | 52 | 0 | 0
2022-04-10 08:00 | 4 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 52 | 40 | 41 | 52 | 46 | 53 | 47 | 51 | 0 | 0
2022-04-10 09:00 | 4 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 53 | 40 | 45 | 54 | 49 | 58 | 51 | 53 | 0 | 0
2022-04-10 10:00 | 4 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 55 | 41 | 46 | 55 | 49 | 67 | 54 | 51 | 0 | 0
2022-04-10 11:00 | 4 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 55 | 42 | 47 | 55 | 50 | 74 | 58 | 54 | 0 | 0
2022-04-10 12:00 | 4 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 54 | 43 | 51 | 57 | 53 | 78 | 59 | 54 | 0 | 0
2022-04-10 13:00 | 4 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 53 | 43 | 56 | 61 | 52 | 80 | 58 | 52 | 0 | 0
2022-04-10 14:00 | 4 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 48 | 42 | 56 | 63 | 53 | 81 | 56 | 51 | 0 | 0
2022-04-10 15:00 | 4 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 50 | 42 | 58 | 63 | 52 | 81 | 56 | 51 | 0 | 0
2022-04-10 16:00 | 4 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 50 | 41 | 60 | 63 | 51 | 81 | 56 | 53 | 0 | 0
2022-04-10 17:00 | 4 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 49 | 40 | 59 | 63 | 50 | 80 | 55 | 53 | 0 | 0
2022-04-10 18:00 | 4 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 47 | 39 | 54 | 59 | 49 | 77 | 54 | 52 | 0 | 0
2022-04-10 19:00 | 4 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 46 | 38 | 53 | 50 | 48 | 74 | 53 | 52 | 0 | 0
2022-04-10 20:00 | 4 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 46 | 38 | 53 | 48 | 47 | 71 | 52 | 56 | 0 | 0
2022-04-10 21:00 | 4 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 46 | 37 | 53 | 46 | 47 | 71 | 50 | 57 | 0 | 0
2022-04-10 22:00 | 4 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 45 | 36 | 53 | 45 | 46 | 69 | 51 | 58 | 0 | 0
2022-04-10 23:00 | 4 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 43 | 34 | 53 | 43 | 46 | 73 | 50 | 60 | 0 | 0
2022-04-11 | 4 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 40 | 33 | 53 | 42 | 46 | 66 | 50 | 58 | 0 | 0
2022-04-11 01:00 | 4 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 39 | 33 | 57 | 41 | 45 | 64 | 49 | 55 | 0 | 0
2022-04-11 02:00 | 4 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 38 | 33 | 59 | 40 | 45 | 63 | 47 | 54 | 0 | 0
2022-04-11 03:00 | 4 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 37 | 33 | 59 | 39 | 46 | 63 | 46 | 51 | 0 | 0
2022-04-11 04:00 | 4 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 35 | 32 | 58 | 38 | 46 | 62 | 43 | 49 | 0 | 0
2022-04-11 05:00 | 4 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 35 | 31 | 58 | 37 | 46 | 63 | 42 | 48 | 0 | 0
2022-04-11 06:00 | 4 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 38 | 30 | 61 | 45 | 47 | 65 | 43 | 47 | 0 | 0
2022-04-11 07:00 | 4 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 41 | 33 | 64 | 48 | 48 | 66 | 46 | 44 | 0 | 0
2022-04-11 08:00 | 4 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 44 | 35 | 68 | 54 | 50 | 72 | 48 | 43 | 0 | 0
2022-04-11 09:00 | 4 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 46 | 38 | 71 | 57 | 53 | 73 | 50 | 44 | 0 | 0
2022-04-11 10:00 | 4 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 47 | 39 | 72 | 63 | 56 | 72 | 52 | 47 | 0 | 0
2022-04-11 11:00 | 4 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 47 | 39 | 74 | 63 | 57 | 70 | 55 | 44 | 0 | 0
2022-04-11 12:00 | 4 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 48 | 40 | 76 | 64 | 59 | 56 | 56 | 43 | 0 | 0
2022-04-11 13:00 | 4 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 47 | 41 | 77 | 64 | 60 | 52 | 56 | 44 | 0 | 0
2022-04-11 14:00 | 4 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 48 | 42 | 76 | 66 | 60 | 53 | 53 | 44 | 0 | 0
2022-04-11 15:00 | 4 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 50 | 43 | 75 | 64 | 59 | 55 | 52 | 45 | 0 | 0
2022-04-11 16:00 | 4 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 49 | 42 | 75 | 64 | 57 | 57 | 52 | 46 | 0 | 0
2022-04-11 17:00 | 4 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 47 | 42 | 74 | 63 | 55 | 58 | 51 | 46 | 0 | 0
2022-04-11 18:00 | 4 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 44 | 41 | 74 | 57 | 54 | 56 | 49 | 42 | 0 | 0
2022-04-11 19:00 | 4 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 42 | 40 | 68 | 55 | 53 | 56 | 47 | 38 | 0 | 0
2022-04-11 20:00 | 4 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 41 | 39 | 69 | 54 | 52 | 55 | 44 | 36 | 0 | 0
2022-04-11 21:00 | 4 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 41 | 38 | 70 | 52 | 51 | 52 | 43 | 37 | 0 | 0
2022-04-11 22:00 | 4 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 41 | 39 | 69 | 50 | 49 | 50 | 43 | 34 | 0 | 0
2022-04-11 23:00 | 4 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 42 | 39 | 68 | 48 | 49 | 49 | 42 | 32 | 0 | 0
2022-04-12 | 4 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 41 | 40 | 70 | 46 | 49 | 48 | 43 | 32 | 0 | 0
2022-04-12 01:00 | 4 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 41 | 41 | 69 | 45 | 49 | 48 | 43 | 34 | 0 | 0
2022-04-12 02:00 | 4 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 40 | 42 | 68 | 45 | 50 | 48 | 43 | 34 | 0 | 0
2022-04-12 03:00 | 4 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 42 | 43 | 66 | 43 | 50 | 48 | 42 | 34 | 0 | 0
2022-04-12 04:00 | 4 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 41 | 43 | 66 | 45 | 50 | 47 | 43 | 34 | 0 | 0
2022-04-12 05:00 | 4 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 42 | 43 | 65 | 43 | 51 | 46 | 43 | 33 | 0 | 0
2022-04-12 06:00 | 4 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 44 | 43 | 64 | 45 | 51 | 47 | 50 | 35 | 0 | 0
2022-04-12 07:00 | 4 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 46 | 43 | 66 | 45 | 51 | 52 | 54 | 37 | 0 | 0
2022-04-12 08:00 | 4 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 49 | 43 | 69 | 46 | 51 | 56 | 56 | 38 | 0 | 0
2022-04-12 09:00 | 4 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 50 | 43 | 70 | 46 | 53 | 60 | 60 | 40 | 0 | 0
2022-04-12 10:00 | 4 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 53 | 45 | 69 | 48 | 56 | 63 | 65 | 41 | 0 | 0
2022-04-12 11:00 | 4 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 57 | 47 | 70 | 50 | 63 | 66 | 69 | 40 | 0 | 0
2022-04-12 12:00 | 4 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 61 | 49 | 69 | 52 | 64 | 68 | 69 | 41 | 0 | 0
2022-04-12 13:00 | 4 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 62 | 49 | 72 | 54 | 69 | 69 | 70 | 43 | 0 | 0
2022-04-12 14:00 | 4 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 68 | 59 | 49 | 72 | 55 | 72 | 70 | 68 | 43 | 0 | 0
2022-04-12 15:00 | 4 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 59 | 49 | 72 | 57 | 72 | 70 | 62 | 42 | 0 | 0
2022-04-12 16:00 | 4 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 59 | 49 | 70 | 59 | 72 | 70 | 59 | 42 | 0 | 0
2022-04-12 17:00 | 4 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 54 | 49 | 71 | 59 | 70 | 69 | 58 | 40 | 0 | 0
2022-04-12 18:00 | 4 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 53 | 49 | 67 | 57 | 69 | 65 | 56 | 38 | 0 | 0
2022-04-12 19:00 | 4 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 53 | 45 | 65 | 57 | 67 | 63 | 56 | 35 | 0 | 0
2022-04-12 20:00 | 4 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 52 | 42 | 63 | 57 | 67 | 61 | 56 | 33 | 0 | 0
2022-04-12 21:00 | 4 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 52 | 38 | 63 | 55 | 57 | 60 | 56 | 31 | 0 | 0
2022-04-12 22:00 | 4 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 52 | 37 | 64 | 55 | 55 | 57 | 55 | 32 | 0 | 0
2022-04-12 23:00 | 4 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 48 | 36 | 62 | 55 | 55 | 55 | 55 | 29 | 0 | 0
2022-04-13 | 4 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 44 | 35 | 62 | 55 | 54 | 54 | 56 | 28 | 0 | 0
2022-04-13 01:00 | 4 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 40 | 34 | 63 | 55 | 53 | 54 | 52 | 28 | 0 | 0
2022-04-13 02:00 | 4 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 38 | 34 | 61 | 55 | 52 | 56 | 50 | 27 | 0 | 0
2022-04-13 03:00 | 4 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 38 | 33 | 60 | 55 | 52 | 55 | 47 | 26 | 0 | 0
2022-04-13 04:00 | 4 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 37 | 33 | 60 | 55 | 52 | 54 | 45 | 24 | 0 | 0
2022-04-13 05:00 | 4 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 38 | 32 | 59 | 54 | 50 | 51 | 44 | 23 | 0 | 0
2022-04-13 06:00 | 4 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 39 | 32 | 62 | 55 | 51 | 53 | 45 | 28 | 0 | 0
2022-04-13 07:00 | 4 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 41 | 33 | 66 | 57 | 52 | 57 | 47 | 33 | 0 | 0
2022-04-13 08:00 | 4 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 43 | 33 | 70 | 61 | 53 | 59 | 50 | 37 | 0 | 0
2022-04-13 09:00 | 4 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 46 | 34 | 72 | 63 | 55 | 61 | 52 | 39 | 0 | 0
2022-04-13 10:00 | 4 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 47 | 37 | 70 | 64 | 57 | 64 | 54 | 44 | 0 | 0
2022-04-13 11:00 | 4 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 49 | 39 | 70 | 66 | 58 | 65 | 56 | 45 | 0 | 0
2022-04-13 12:00 | 4 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 49 | 42 | 71 | 64 | 59 | 64 | 56 | 46 | 0 | 0
2022-04-13 13:00 | 4 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 50 | 42 | 75 | 66 | 59 | 64 | 58 | 49 | 0 | 0
2022-04-13 14:00 | 4 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 50 | 43 | 75 | 66 | 59 | 63 | 57 | 49 | 0 | 0
2022-04-13 15:00 | 4 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 49 | 43 | 75 | 68 | 58 | 60 | 56 | 51 | 0 | 0
2022-04-13 16:00 | 4 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 47 | 42 | 76 | 66 | 57 | 58 | 56 | 50 | 0 | 0
2022-04-13 17:00 | 4 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 44 | 41 | 59 | 66 | 56 | 54 | 54 | 49 | 0 | 0
2022-04-13 18:00 | 4 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 40 | 40 | 58 | 63 | 54 | 50 | 52 | 46 | 0 | 0
2022-04-13 19:00 | 4 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 39 | 39 | 60 | 63 | 52 | 48 | 50 | 45 | 0 | 0
2022-04-13 20:00 | 4 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 39 | 37 | 57 | 61 | 51 | 47 | 49 | 44 | 0 | 0
2022-04-13 21:00 | 4 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 37 | 36 | 55 | 61 | 50 | 46 | 48 | 42 | 0 | 0
2022-04-13 22:00 | 4 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 37 | 36 | 51 | 57 | 49 | 45 | 47 | 38 | 0 | 0
2022-04-13 23:00 | 4 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 37 | 35 | 47 | 57 | 48 | 43 | 46 | 38 | 0 | 0
2022-04-14 | 4 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 37 | 35 | 46 | 57 | 45 | 40 | 44 | 38 | 0 | 0
2022-04-14 01:00 | 4 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 37 | 34 | 47 | 57 | 45 | 37 | 42 | 42 | 0 | 0
2022-04-14 02:00 | 4 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 37 | 33 | 45 | 57 | 41 | 36 | 41 | 38 | 0 | 0
2022-04-14 03:00 | 4 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 36 | 32 | 43 | 57 | 42 | 35 | 40 | 38 | 0 | 0
2022-04-14 04:00 | 4 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 35 | 33 | 42 | 55 | 43 | 34 | 39 | 37 | 0 | 0
2022-04-14 05:00 | 4 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 35 | 33 | 39 | 55 | 45 | 34 | 39 | 37 | 0 | 0
2022-04-14 06:00 | 4 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 35 | 34 | 41 | 55 | 47 | 38 | 39 | 39 | 0 | 0
2022-04-14 07:00 | 4 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 35 | 35 | 45 | 55 | 50 | 45 | 40 | 40 | 0 | 0
2022-04-14 08:00 | 4 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 36 | 37 | 47 | 57 | 51 | 48 | 41 | 42 | 0 | 0
2022-04-14 09:00 | 4 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 37 | 38 | 47 | 61 | 54 | 52 | 44 | 46 | 0 | 0
2022-04-14 10:00 | 4 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 38 | 39 | 53 | 64 | 54 | 52 | 45 | 46 | 0 | 0
2022-04-14 11:00 | 4 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 41 | 40 | 49 | 68 | 55 | 52 | 46 | 49 | 0 | 0
2022-04-14 12:00 | 4 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 41 | 41 | 53 | 72 | 55 | 54 | 45 | 53 | 0 | 0
2022-04-14 13:00 | 4 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 41 | 42 | 54 | 72 | 56 | 55 | 46 | 53 | 0 | 0
2022-04-14 14:00 | 4 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 42 | 44 | 54 | 72 | 55 | 57 | 46 | 56 | 0 | 0
2022-04-14 15:00 | 4 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 42 | 45 | 55 | 72 | 55 | 56 | 45 | 59 | 0 | 0
2022-04-14 16:00 | 4 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 43 | 46 | 56 | 66 | 55 | 55 | 47 | 57 | 0 | 0
2022-04-14 17:00 | 4 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 45 | 48 | 52 | 64 | 51 | 54 | 48 | 58 | 0 | 0
2022-04-14 18:00 | 4 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 45 | 49 | 47 | 63 | 51 | 52 | 51 | 57 | 0 | 0
2022-04-14 19:00 | 4 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 47 | 47 | 45 | 64 | 49 | 49 | 52 | 57 | 0 | 0
2022-04-14 20:00 | 4 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 49 | 45 | 42 | 64 | 49 | 48 | 54 | 53 | 0 | 0
2022-04-14 21:00 | 4 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 51 | 43 | 39 | 63 | 48 | 45 | 55 | 53 | 0 | 0
2022-04-14 22:00 | 4 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 52 | 40 | 36 | 63 | 47 | 43 | 57 | 53 | 0 | 0
2022-04-14 23:00 | 4 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 52 | 38 | 36 | 63 | 46 | 43 | 60 | 49 | 0 | 0
2022-04-15 | 4 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 55 | 35 | 36 | 63 | 44 | 42 | 66 | 48 | 0 | 0
2022-04-15 01:00 | 4 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 51 | 34 | 36 | 63 | 43 | 42 | 57 | 49 | 0 | 0
2022-04-15 02:00 | 4 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 47 | 34 | 35 | 61 | 43 | 39 | 53 | 49 | 0 | 0
2022-04-15 03:00 | 4 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 46 | 33 | 33 | 59 | 42 | 39 | 51 | 48 | 0 | 0
2022-04-15 04:00 | 4 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 44 | 33 | 32 | 59 | 41 | 37 | 49 | 48 | 0 | 0
2022-04-15 05:00 | 4 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 43 | 33 | 32 | 57 | 40 | 34 | 47 | 47 | 0 | 0
2022-04-15 06:00 | 4 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 43 | 33 | 37 | 61 | 44 | 38 | 47 | 47 | 0 | 0
2022-04-15 07:00 | 4 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 44 | 33 | 47 | 64 | 47 | 42 | 49 | 50 | 0 | 0
2022-04-15 08:00 | 4 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 45 | 34 | 53 | 68 | 48 | 45 | 49 | 51 | 0 | 0
2022-04-15 09:00 | 4 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 47 | 34 | 49 | 72 | 52 | 48 | 51 | 56 | 0 | 0
2022-04-15 10:00 | 4 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 49 | 34 | 49 | 73 | 53 | 49 | 51 | 57 | 0 | 0
2022-04-15 11:00 | 4 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 49 | 35 | 52 | 75 | 55 | 49 | 53 | 59 | 0 | 0
2022-04-15 12:00 | 4 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 48 | 35 | 53 | 77 | 56 | 50 | 53 | 62 | 0 | 0
2022-04-15 13:00 | 4 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 47 | 35 | 55 | 79 | 58 | 54 | 53 | 63 | 0 | 0
2022-04-15 14:00 | 4 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 49 | 34 | 56 | 77 | 59 | 53 | 52 | 63 | 0 | 0
2022-04-15 15:00 | 4 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 48 | 34 | 55 | 79 | 59 | 51 | 53 | 63 | 0 | 0
2022-04-15 16:00 | 4 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 46 | 33 | 52 | 79 | 59 | 50 | 50 | 62 | 0 | 0
2022-04-15 17:00 | 4 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 43 | 32 | 52 | 79 | 59 | 48 | 45 | 60 | 0 | 0
2022-04-15 18:00 | 4 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 42 | 31 | 49 | 75 | 57 | 45 | 45 | 56 | 0 | 0
2022-04-15 19:00 | 4 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 40 | 31 | 45 | 74 | 54 | 42 | 44 | 52 | 0 | 0
2022-04-15 20:00 | 4 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 38 | 31 | 43 | 73 | 52 | 41 | 44 | 52 | 0 | 0
2022-04-15 21:00 | 4 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 39 | 31 | 42 | 72 | 52 | 39 | 43 | 48 | 0 | 0
2022-04-15 22:00 | 4 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 39 | 30 | 40 | 72 | 50 | 38 | 43 | 43 | 0 | 0
2022-04-15 23:00 | 4 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 38 | 29 | 39 | 70 | 47 | 37 | 42 | 41 | 0 | 0
2022-04-16 | 4 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 38 | 28 | 37 | 68 | 47 | 34 | 42 | 39 | 0 | 0
2022-04-16 01:00 | 4 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 38 | 27 | 36 | 64 | 46 | 35 | 42 | 37 | 0 | 0
2022-04-16 02:00 | 4 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 37 | 27 | 36 | 64 | 45 | 34 | 42 | 37 | 0 | 0
2022-04-16 03:00 | 4 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 37 | 26 | 37 | 63 | 40 | 34 | 42 | 36 | 0 | 0
2022-04-16 04:00 | 4 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 36 | 25 | 37 | 63 | 38 | 33 | 40 | 35 | 0 | 0
2022-04-16 05:00 | 4 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 33 | 24 | 37 | 63 | 40 | 33 | 39 | 34 | 0 | 0
2022-04-16 06:00 | 4 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 32 | 23 | 37 | 66 | 45 | 34 | 38 | 38 | 0 | 0
2022-04-16 07:00 | 4 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 30 | 23 | 46 | 72 | 49 | 38 | 38 | 45 | 0 | 0
2022-04-16 08:00 | 4 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 28 | 22 | 47 | 75 | 52 | 42 | 36 | 51 | 0 | 0
2022-04-16 09:00 | 4 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 28 | 22 | 49 | 81 | 55 | 44 | 34 | 55 | 0 | 0
2022-04-16 10:00 | 4 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 27 | 23 | 51 | 82 | 57 | 45 | 34 | 57 | 0 | 0
2022-04-16 11:00 | 4 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 28 | 24 | 51 | 84 | 60 | 47 | 34 | 59 | 0 | 0
2022-04-16 12:00 | 4 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 28 | 25 | 51 | 84 | 62 | 51 | 34 | 62 | 0 | 0
2022-04-16 13:00 | 4 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 71 | 27 | 25 | 54 | 86 | 64 | 51 | 33 | 63 | 0 | 0
2022-04-16 14:00 | 4 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 71 | 27 | 26 | 53 | 88 | 66 | 54 | 33 | 65 | 0 | 0
2022-04-16 15:00 | 4 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 73 | 26 | 26 | 57 | 88 | 67 | 54 | 33 | 66 | 0 | 0
2022-04-16 16:00 | 4 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 72 | 26 | 25 | 56 | 86 | 66 | 52 | 33 | 64 | 0 | 0
2022-04-16 17:00 | 4 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 25 | 24 | 54 | 84 | 64 | 51 | 32 | 62 | 0 | 0
2022-04-16 18:00 | 4 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 24 | 23 | 47 | 81 | 59 | 50 | 31 | 61 | 0 | 0
2022-04-16 19:00 | 4 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 24 | 22 | 46 | 77 | 56 | 48 | 31 | 58 | 0 | 0
2022-04-16 20:00 | 4 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 24 | 22 | 44 | 79 | 58 | 46 | 29 | 58 | 0 | 0
2022-04-16 21:00 | 4 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 24 | 21 | 41 | 72 | 59 | 44 | 28 | 57 | 0 | 0
2022-04-16 22:00 | 4 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 25 | 22 | 40 | 66 | 57 | 41 | 28 | 58 | 0 | 0
2022-04-16 23:00 | 4 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 25 | 22 | 38 | 66 | 54 | 38 | 29 | 57 | 0 | 0
2022-04-17 | 4 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 25 | 23 | 35 | 66 | 52 | 37 | 29 | 58 | 0 | 0
2022-04-17 01:00 | 4 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 25 | 23 | 36 | 68 | 49 | 37 | 28 | 57 | 0 | 0
2022-04-17 02:00 | 4 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 24 | 22 | 36 | 64 | 49 | 36 | 28 | 56 | 0 | 0
2022-04-17 03:00 | 4 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 24 | 22 | 36 | 63 | 45 | 34 | 27 | 56 | 0 | 0
2022-04-17 04:00 | 4 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 22 | 22 | 36 | 61 | 47 | 34 | 27 | 56 | 0 | 0
2022-04-17 05:00 | 4 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 23 | 22 | 36 | 61 | 45 | 33 | 27 | 55 | 0 | 0
2022-04-17 06:00 | 4 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 26 | 22 | 40 | 64 | 49 | 35 | 29 | 55 | 0 | 0
2022-04-17 07:00 | 4 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 28 | 25 | 49 | 73 | 52 | 40 | 32 | 57 | 0 | 0
2022-04-17 08:00 | 4 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 31 | 29 | 51 | 79 | 55 | 43 | 35 | 57 | 0 | 0
2022-04-17 09:00 | 4 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 34 | 32 | 55 | 82 | 56 | 47 | 37 | 50 | 0 | 0
2022-04-17 10:00 | 4 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 37 | 36 | 55 | 88 | 59 | 50 | 40 | 45 | 0 | 0
2022-04-17 11:00 | 4 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 41 | 39 | 55 | 88 | 60 | 52 | 43 | 45 | 0 | 0
2022-04-17 12:00 | 4 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 42 | 43 | 57 | 90 | 61 | 55 | 46 | 46 | 0 | 0
2022-04-17 13:00 | 4 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 44 | 44 | 62 | 90 | 62 | 56 | 48 | 47 | 0 | 0
2022-04-17 14:00 | 4 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 46 | 46 | 59 | 91 | 63 | 57 | 49 | 52 | 0 | 0
2022-04-17 15:00 | 4 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 46 | 47 | 62 | 90 | 61 | 59 | 51 | 52 | 0 | 0
2022-04-17 16:00 | 4 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 46 | 45 | 62 | 90 | 60 | 58 | 51 | 48 | 0 | 0
2022-04-17 17:00 | 4 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 44 | 44 | 61 | 86 | 57 | 56 | 50 | 46 | 0 | 0
2022-04-17 18:00 | 4 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 41 | 42 | 57 | 82 | 55 | 53 | 47 | 43 | 0 | 0
2022-04-17 19:00 | 4 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 39 | 39 | 54 | 81 | 53 | 51 | 46 | 42 | 0 | 0
2022-04-17 20:00 | 4 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 38 | 35 | 48 | 79 | 52 | 50 | 41 | 40 | 0 | 0
2022-04-17 21:00 | 4 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 38 | 32 | 46 | 77 | 51 | 47 | 38 | 37 | 0 | 0
2022-04-17 22:00 | 4 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 37 | 32 | 47 | 73 | 51 | 45 | 37 | 36 | 0 | 0
2022-04-17 23:00 | 4 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 36 | 31 | 52 | 72 | 50 | 44 | 35 | 35 | 0 | 0
2022-04-18 | 4 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 35 | 31 | 54 | 73 | 49 | 42 | 35 | 35 | 0 | 0
2022-04-18 01:00 | 4 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 34 | 31 | 52 | 72 | 48 | 43 | 35 | 34 | 0 | 0
2022-04-18 02:00 | 4 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 35 | 30 | 54 | 72 | 48 | 43 | 36 | 32 | 0 | 0
2022-04-18 03:00 | 4 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 33 | 30 | 54 | 72 | 47 | 43 | 34 | 32 | 0 | 0
2022-04-18 04:00 | 4 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 32 | 31 | 54 | 68 | 45 | 43 | 34 | 31 | 0 | 0
2022-04-18 05:00 | 4 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 32 | 32 | 54 | 68 | 46 | 43 | 35 | 31 | 0 | 0
2022-04-18 06:00 | 4 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 35 | 33 | 53 | 72 | 49 | 45 | 38 | 35 | 0 | 0
2022-04-18 07:00 | 4 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 36 | 38 | 56 | 73 | 53 | 46 | 42 | 38 | 0 | 0
2022-04-18 08:00 | 4 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 42 | 42 | 57 | 77 | 59 | 51 | 47 | 40 | 0 | 0
2022-04-18 09:00 | 4 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 44 | 47 | 52 | 82 | 64 | 54 | 48 | 43 | 0 | 0
2022-04-18 10:00 | 4 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 45 | 49 | 51 | 84 | 66 | 56 | 52 | 45 | 0 | 0
2022-04-18 11:00 | 4 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 49 | 50 | 51 | 84 | 66 | 58 | 54 | 48 | 0 | 0
2022-04-18 12:00 | 4 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 70 | 50 | 52 | 52 | 86 | 68 | 59 | 56 | 50 | 0 | 0
2022-04-18 13:00 | 4 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 70 | 51 | 53 | 54 | 82 | 67 | 52 | 61 | 51 | 0 | 0
2022-04-18 14:00 | 4 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 51 | 53 | 59 | 77 | 67 | 52 | 57 | 51 | 0 | 0
2022-04-18 15:00 | 4 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 52 | 54 | 62 | 81 | 67 | 51 | 58 | 53 | 0 | 0
2022-04-18 16:00 | 4 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 71 | 53 | 52 | 65 | 81 | 65 | 51 | 59 | 53 | 0 | 0
2022-04-18 17:00 | 4 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 70 | 51 | 49 | 64 | 79 | 64 | 51 | 57 | 51 | 0 | 0
2022-04-18 18:00 | 4 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 48 | 47 | 61 | 73 | 61 | 51 | 54 | 49 | 0 | 0
2022-04-18 19:00 | 4 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 46 | 44 | 58 | 73 | 59 | 50 | 52 | 44 | 0 | 0
2022-04-18 20:00 | 4 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 46 | 40 | 59 | 73 | 57 | 50 | 48 | 40 | 0 | 0
2022-04-18 21:00 | 4 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 45 | 37 | 57 | 72 | 56 | 51 | 46 | 40 | 0 | 0
2022-04-18 22:00 | 4 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 42 | 34 | 57 | 72 | 55 | 51 | 44 | 36 | 0 | 0
2022-04-18 23:00 | 4 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 41 | 32 | 57 | 70 | 55 | 50 | 42 | 34 | 0 | 0
2022-04-19 | 4 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 40 | 29 | 57 | 64 | 55 | 50 | 40 | 33 | 0 | 0
2022-04-19 01:00 | 4 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 38 | 28 | 57 | 64 | 56 | 49 | 38 | 31 | 0 | 0
2022-04-19 02:00 | 4 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 38 | 27 | 56 | 66 | 56 | 49 | 36 | 30 | 0 | 0
2022-04-19 03:00 | 4 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 38 | 26 | 55 | 64 | 57 | 48 | 37 | 30 | 0 | 0
2022-04-19 04:00 | 4 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 37 | 28 | 54 | 63 | 60 | 46 | 36 | 28 | 0 | 0
2022-04-19 05:00 | 4 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 37 | 29 | 53 | 61 | 64 | 46 | 35 | 29 | 0 | 0
2022-04-19 06:00 | 4 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 74 | 39 | 31 | 55 | 66 | 64 | 47 | 39 | 33 | 0 | 0
2022-04-19 07:00 | 4 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 77 | 44 | 38 | 61 | 72 | 65 | 52 | 43 | 39 | 0 | 0
2022-04-19 08:00 | 4 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 79 | 50 | 44 | 66 | 73 | 66 | 54 | 48 | 45 | 0 | 0
2022-04-19 09:00 | 4 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 81 | 53 | 51 | 70 | 77 | 70 | 58 | 55 | 51 | 0 | 0
2022-04-19 10:00 | 4 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 81 | 56 | 55 | 71 | 81 | 71 | 60 | 58 | 54 | 0 | 0
2022-04-19 11:00 | 4 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 83 | 58 | 58 | 68 | 84 | 74 | 61 | 59 | 57 | 0 | 0
2022-04-19 12:00 | 4 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 85 | 60 | 62 | 71 | 86 | 77 | 62 | 62 | 60 | 0 | 0
2022-04-19 13:00 | 4 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 85 | 62 | 62 | 74 | 84 | 79 | 60 | 64 | 60 | 0 | 0
2022-04-19 14:00 | 4 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 64 | 63 | 74 | 77 | 82 | 61 | 66 | 62 | 0 | 0
2022-04-19 15:00 | 4 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 71 | 65 | 63 | 72 | 81 | 84 | 58 | 67 | 62 | 0 | 0
2022-04-19 16:00 | 4 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 70 | 65 | 62 | 69 | 82 | 84 | 53 | 66 | 61 | 0 | 0
2022-04-19 17:00 | 4 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 69 | 63 | 60 | 66 | 79 | 82 | 53 | 65 | 60 | 0 | 0
2022-04-19 18:00 | 4 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 69 | 60 | 59 | 65 | 77 | 79 | 53 | 62 | 58 | 0 | 0
2022-04-19 19:00 | 4 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 59 | 55 | 62 | 75 | 76 | 52 | 57 | 57 | 0 | 0
2022-04-19 20:00 | 4 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 56 | 50 | 64 | 73 | 75 | 51 | 57 | 56 | 0 | 0
2022-04-19 21:00 | 4 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 55 | 46 | 60 | 72 | 75 | 50 | 56 | 54 | 0 | 0
2022-04-19 22:00 | 4 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 53 | 47 | 62 | 72 | 72 | 50 | 54 | 53 | 0 | 0
2022-04-19 23:00 | 4 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 53 | 48 | 60 | 68 | 70 | 49 | 50 | 52 | 0 | 0
2022-04-20 | 4 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 51 | 49 | 62 | 68 | 67 | 49 | 53 | 51 | 0 | 0
2022-04-20 01:00 | 4 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 52 | 48 | 59 | 66 | 65 | 48 | 48 | 51 | 0 | 0
2022-04-20 02:00 | 4 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 51 | 48 | 57 | 70 | 62 | 48 | 45 | 50 | 0 | 0
2022-04-20 03:00 | 4 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 51 | 47 | 59 | 68 | 60 | 47 | 50 | 49 | 0 | 0
2022-04-20 04:00 | 4 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 50 | 48 | 60 | 66 | 58 | 46 | 45 | 49 | 0 | 0
2022-04-20 05:00 | 4 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 50 | 48 | 60 | 64 | 58 | 46 | 44 | 48 | 0 | 0
2022-04-20 06:00 | 4 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 52 | 49 | 60 | 66 | 59 | 46 | 48 | 49 | 0 | 0
2022-04-20 07:00 | 4 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 67 | 55 | 52 | 61 | 70 | 61 | 46 | 54 | 49 | 0 | 0
2022-04-20 08:00 | 4 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 68 | 60 | 54 | 65 | 70 | 63 | 44 | 59 | 50 | 0 | 0
2022-04-20 09:00 | 4 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 69 | 62 | 57 | 70 | 72 | 65 | 46 | 65 | 51 | 0 | 0
2022-04-20 10:00 | 4 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 62 | 59 | 72 | 70 | 65 | 47 | 70 | 52 | 0 | 0
2022-04-20 11:00 | 4 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 53 | 62 | 74 | 66 | 67 | 46 | 70 | 53 | 0 | 0
2022-04-20 12:00 | 4 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 75 | 57 | 64 | 73 | 66 | 71 | 46 | 73 | 57 | 0 | 0
2022-04-20 13:00 | 4 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 74 | 64 | 64 | 75 | 66 | 71 | 46 | 73 | 59 | 0 | 0
2022-04-20 14:00 | 4 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 74 | 59 | 63 | 73 | 64 | 73 | 47 | 72 | 60 | 0 | 0
2022-04-20 15:00 | 4 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 71 | 62 | 63 | 73 | 57 | 73 | 47 | 71 | 59 | 0 | 0
2022-04-20 16:00 | 4 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 67 | 62 | 60 | 72 | 63 | 70 | 46 | 67 | 59 | 0 | 0
2022-04-20 17:00 | 4 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 58 | 57 | 72 | 63 | 68 | 47 | 66 | 59 | 0 | 0
2022-04-20 18:00 | 4 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 56 | 54 | 73 | 63 | 68 | 45 | 64 | 58 | 0 | 0
2022-04-20 19:00 | 4 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 53 | 52 | 59 | 61 | 65 | 42 | 63 | 57 | 0 | 0
2022-04-20 20:00 | 4 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 51 | 50 | 61 | 61 | 63 | 41 | 61 | 56 | 0 | 0
2022-04-20 21:00 | 4 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 50 | 48 | 62 | 61 | 61 | 41 | 59 | 53 | 0 | 0
2022-04-20 22:00 | 4 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 49 | 46 | 62 | 59 | 59 | 40 | 57 | 53 | 0 | 0
2022-04-20 23:00 | 4 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 47 | 44 | 62 | 57 | 58 | 39 | 56 | 52 | 0 | 0
2022-04-21 | 4 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 46 | 42 | 61 | 57 | 57 | 41 | 54 | 52 | 0 | 0
2022-04-21 01:00 | 4 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 44 | 38 | 61 | 55 | 57 | 41 | 52 | 52 | 0 | 0
2022-04-21 02:00 | 4 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 44 | 35 | 60 | 55 | 57 | 41 | 49 | 52 | 0 | 0
2022-04-21 03:00 | 4 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 43 | 31 | 60 | 54 | 56 | 41 | 47 | 52 | 0 | 0
2022-04-21 04:00 | 4 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 43 | 33 | 61 | 54 | 57 | 40 | 44 | 52 | 0 | 0
2022-04-21 05:00 | 4 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 44 | 36 | 61 | 52 | 57 | 40 | 42 | 52 | 0 | 0
2022-04-21 06:00 | 4 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 46 | 38 | 62 | 50 | 58 | 40 | 49 | 52 | 0 | 0
2022-04-21 07:00 | 4 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 49 | 43 | 64 | 50 | 60 | 40 | 51 | 53 | 0 | 0
2022-04-21 08:00 | 4 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 53 | 49 | 67 | 50 | 58 | 40 | 57 | 55 | 0 | 0
2022-04-21 09:00 | 4 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 68 | 55 | 54 | 72 | 50 | 58 | 41 | 60 | 57 | 0 | 0
2022-04-21 10:00 | 4 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 77 | 57 | 56 | 74 | 50 | 60 | 42 | 62 | 58 | 0 | 0
2022-04-21 11:00 | 4 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 79 | 59 | 59 | 75 | 48 | 60 | 43 | 64 | 60 | 0 | 0
2022-04-21 12:00 | 4 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 83 | 58 | 61 | 78 | 46 | 61 | 43 | 65 | 60 | 0 | 0
2022-04-21 13:00 | 4 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 87 | 60 | 61 | 79 | 43 | 63 | 42 | 67 | 63 | 0 | 0
2022-04-21 14:00 | 4 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 89 | 60 | 60 | 75 | 43 | 63 | 42 | 68 | 63 | 0 | 0
2022-04-21 15:00 | 4 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 87 | 61 | 60 | 72 | 43 | 64 | 41 | 66 | 62 | 0 | 0
2022-04-21 16:00 | 4 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 88 | 59 | 57 | 73 | 43 | 66 | 35 | 65 | 59 | 0 | 0
2022-04-21 17:00 | 4 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 85 | 57 | 55 | 71 | 43 | 66 | 35 | 62 | 57 | 0 | 0
2022-04-21 18:00 | 4 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 81 | 53 | 52 | 64 | 43 | 63 | 34 | 59 | 55 | 0 | 0
2022-04-21 19:00 | 4 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 80 | 49 | 50 | 64 | 43 | 61 | 34 | 56 | 54 | 0 | 0
2022-04-21 20:00 | 4 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 78 | 49 | 48 | 64 | 43 | 58 | 35 | 54 | 53 | 0 | 0
2022-04-21 21:00 | 4 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 73 | 47 | 46 | 64 | 43 | 57 | 33 | 53 | 53 | 0 | 0
2022-04-21 22:00 | 4 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 71 | 46 | 44 | 67 | 43 | 57 | 34 | 51 | 49 | 0 | 0
2022-04-21 23:00 | 4 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 46 | 43 | 65 | 43 | 58 | 34 | 50 | 46 | 0 | 0
2022-04-22 | 4 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 43 | 41 | 64 | 43 | 58 | 35 | 51 | 44 | 0 | 0
2022-04-22 01:00 | 4 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 42 | 40 | 61 | 43 | 58 | 34 | 48 | 42 | 0 | 0
2022-04-22 02:00 | 4 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 40 | 39 | 59 | 43 | 57 | 32 | 47 | 40 | 0 | 0
2022-04-22 03:00 | 4 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 38 | 38 | 61 | 43 | 56 | 31 | 45 | 39 | 0 | 0
2022-04-22 04:00 | 4 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 36 | 38 | 61 | 43 | 55 | 30 | 43 | 38 | 0 | 0
2022-04-22 05:00 | 4 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 37 | 37 | 61 | 43 | 55 | 30 | 43 | 38 | 0 | 0
2022-04-22 06:00 | 4 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 40 | 37 | 60 | 45 | 56 | 30 | 44 | 41 | 0 | 0
2022-04-22 07:00 | 4 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 68 | 42 | 43 | 61 | 45 | 60 | 33 | 47 | 45 | 0 | 0
2022-04-22 08:00 | 4 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 44 | 50 | 61 | 45 | 67 | 37 | 49 | 50 | 0 | 0
2022-04-22 09:00 | 4 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 79 | 46 | 56 | 63 | 46 | 72 | 41 | 52 | 53 | 0 | 0
2022-04-22 10:00 | 4 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 85 | 49 | 58 | 62 | 48 | 75 | 45 | 53 | 56 | 0 | 0
2022-04-22 11:00 | 4 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 87 | 51 | 60 | 64 | 54 | 75 | 50 | 56 | 60 | 0 | 0
2022-04-22 12:00 | 4 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 90 | 52 | 62 | 63 | 55 | 77 | 53 | 58 | 65 | 0 | 0
2022-04-22 13:00 | 4 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 90 | 53 | 62 | 64 | 55 | 72 | 53 | 59 | 67 | 0 | 0
2022-04-22 14:00 | 4 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 91 | 54 | 62 | 63 | 55 | 72 | 55 | 60 | 69 | 0 | 0
2022-04-22 15:00 | 4 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 87 | 54 | 62 | 63 | 54 | 74 | 56 | 60 | 71 | 0 | 0
2022-04-22 16:00 | 4 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 85 | 53 | 60 | 62 | 54 | 73 | 56 | 59 | 73 | 0 | 0
2022-04-22 17:00 | 4 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 84 | 50 | 59 | 62 | 52 | 68 | 54 | 56 | 71 | 0 | 0
2022-04-22 18:00 | 4 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 81 | 47 | 57 | 62 | 50 | 63 | 51 | 53 | 65 | 0 | 0
2022-04-22 19:00 | 4 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 79 | 44 | 54 | 61 | 48 | 61 | 49 | 50 | 60 | 0 | 0
2022-04-22 20:00 | 4 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 71 | 42 | 50 | 61 | 46 | 59 | 46 | 49 | 55 | 0 | 0
2022-04-22 21:00 | 4 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 40 | 47 | 58 | 45 | 57 | 43 | 47 | 52 | 0 | 0
2022-04-22 22:00 | 4 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 39 | 45 | 58 | 45 | 55 | 42 | 44 | 50 | 0 | 0
2022-04-22 23:00 | 4 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 37 | 42 | 59 | 43 | 55 | 41 | 42 | 48 | 0 | 0
2022-04-23 | 4 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 35 | 40 | 59 | 43 | 54 | 39 | 40 | 47 | 0 | 0
2022-04-23 01:00 | 4 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 34 | 38 | 51 | 39 | 51 | 35 | 39 | 45 | 0 | 0
2022-04-23 02:00 | 4 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 33 | 37 | 48 | 37 | 49 | 33 | 37 | 44 | 0 | 0
2022-04-23 03:00 | 4 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 33 | 35 | 47 | 37 | 48 | 34 | 37 | 42 | 0 | 0
2022-04-23 04:00 | 4 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 32 | 36 | 47 | 37 | 44 | 32 | 35 | 42 | 0 | 0
2022-04-23 05:00 | 4 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 33 | 38 | 47 | 36 | 46 | 32 | 34 | 44 | 0 | 0
2022-04-23 06:00 | 4 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 37 | 39 | 47 | 41 | 49 | 34 | 37 | 48 | 0 | 0
2022-04-23 07:00 | 4 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 40 | 44 | 47 | 43 | 51 | 39 | 42 | 55 | 0 | 0
2022-04-23 08:00 | 4 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 46 | 50 | 47 | 45 | 53 | 43 | 45 | 61 | 0 | 0
2022-04-23 09:00 | 4 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 51 | 55 | 47 | 46 | 55 | 48 | 49 | 67 | 0 | 0
2022-04-23 10:00 | 4 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 56 | 59 | 47 | 48 | 56 | 52 | 54 | 71 | 0 | 0
2022-04-23 11:00 | 4 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 60 | 64 | 47 | 50 | 59 | 54 | 60 | 73 | 0 | 0
2022-04-23 12:00 | 4 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 62 | 68 | 46 | 52 | 60 | 56 | 62 | 77 | 0 | 0
2022-04-23 13:00 | 4 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 65 | 66 | 46 | 54 | 60 | 56 | 66 | 79 | 0 | 0
2022-04-23 14:00 | 4 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 66 | 64 | 46 | 54 | 60 | 56 | 68 | 80 | 0 | 0
2022-04-23 15:00 | 4 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 72 | 65 | 62 | 46 | 54 | 61 | 56 | 69 | 80 | 0 | 0
2022-04-23 16:00 | 4 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 66 | 57 | 46 | 54 | 60 | 55 | 70 | 79 | 0 | 0
2022-04-23 17:00 | 4 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 63 | 52 | 46 | 54 | 59 | 55 | 68 | 77 | 0 | 0
2022-04-23 18:00 | 4 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 58 | 47 | 46 | 52 | 58 | 49 | 66 | 72 | 0 | 0
2022-04-23 19:00 | 4 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 54 | 44 | 46 | 48 | 57 | 48 | 60 | 70 | 0 | 0
2022-04-23 20:00 | 4 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 51 | 40 | 45 | 46 | 56 | 48 | 56 | 65 | 0 | 0
2022-04-23 21:00 | 4 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 46 | 37 | 45 | 45 | 56 | 49 | 58 | 59 | 0 | 0
2022-04-23 22:00 | 4 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 43 | 35 | 45 | 45 | 56 | 48 | 55 | 56 | 0 | 0
2022-04-23 23:00 | 4 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 41 | 33 | 45 | 39 | 55 | 48 | 52 | 53 | 0 | 0
2022-04-24 | 4 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 40 | 31 | 45 | 37 | 53 | 48 | 48 | 52 | 0 | 0
2022-04-24 01:00 | 4 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 40 | 29 | 45 | 36 | 48 | 48 | 47 | 50 | 0 | 0
2022-04-24 02:00 | 4 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 39 | 26 | 45 | 34 | 47 | 48 | 45 | 48 | 0 | 0
2022-04-24 03:00 | 4 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 39 | 24 | 45 | 34 | 47 | 49 | 44 | 46 | 0 | 0
2022-04-24 04:00 | 4 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 38 | 25 | 45 | 32 | 47 | 49 | 44 | 44 | 0 | 0
2022-04-24 05:00 | 4 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 38 | 27 | 45 | 34 | 47 | 49 | 44 | 45 | 0 | 0
2022-04-24 06:00 | 4 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 40 | 28 | 45 | 41 | 48 | 49 | 45 | 50 | 0 | 0
2022-04-24 07:00 | 4 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 44 | 34 | 45 | 46 | 49 | 50 | 47 | 55 | 0 | 0
2022-04-24 08:00 | 4 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 48 | 39 | 44 | 50 | 50 | 50 | 51 | 61 | 0 | 0
2022-04-24 09:00 | 4 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 53 | 45 | 45 | 52 | 51 | 50 | 54 | 66 | 0 | 0
2022-04-24 10:00 | 4 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 55 | 46 | 45 | 54 | 52 | 54 | 58 | 72 | 0 | 0
2022-04-24 11:00 | 4 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 60 | 46 | 45 | 55 | 52 | 55 | 63 | 76 | 0 | 0
2022-04-24 12:00 | 4 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 60 | 47 | 45 | 57 | 58 | 59 | 68 | 77 | 0 | 0
2022-04-24 13:00 | 4 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 61 | 50 | 45 | 59 | 58 | 59 | 70 | 81 | 0 | 0
2022-04-24 14:00 | 4 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 63 | 52 | 45 | 59 | 57 | 60 | 72 | 79 | 0 | 0
2022-04-24 15:00 | 4 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 64 | 55 | 45 | 61 | 58 | 61 | 70 | 78 | 0 | 0
2022-04-24 16:00 | 4 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 66 | 54 | 45 | 61 | 56 | 61 | 69 | 78 | 0 | 0
2022-04-24 17:00 | 4 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 65 | 54 | 45 | 59 | 54 | 59 | 68 | 77 | 0 | 0
2022-04-24 18:00 | 4 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 62 | 53 | 45 | 57 | 54 | 57 | 66 | 75 | 0 | 0
2022-04-24 19:00 | 4 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 60 | 49 | 45 | 54 | 53 | 55 | 63 | 73 | 0 | 0
2022-04-24 20:00 | 4 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 58 | 46 | 45 | 52 | 53 | 52 | 61 | 71 | 0 | 0
2022-04-24 21:00 | 4 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 56 | 42 | 45 | 52 | 52 | 50 | 59 | 66 | 0 | 0
2022-04-24 22:00 | 4 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 55 | 40 | 45 | 52 | 52 | 49 | 58 | 65 | 0 | 0
2022-04-24 23:00 | 4 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 53 | 38 | 45 | 48 | 51 | 47 | 56 | 63 | 0 | 0
2022-04-25 | 4 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 53 | 36 | 45 | 46 | 53 | 46 | 55 | 61 | 0 | 0
2022-04-25 01:00 | 4 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 51 | 37 | 45 | 46 | 53 | 47 | 56 | 61 | 0 | 0
2022-04-25 02:00 | 4 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 51 | 37 | 43 | 46 | 52 | 44 | 55 | 59 | 0 | 0
2022-04-25 03:00 | 4 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 50 | 38 | 41 | 46 | 51 | 45 | 55 | 57 | 0 | 0
2022-04-25 04:00 | 4 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 50 | 39 | 40 | 46 | 49 | 45 | 54 | 56 | 0 | 0
2022-04-25 05:00 | 4 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 50 | 40 | 40 | 48 | 49 | 44 | 54 | 55 | 0 | 0
2022-04-25 06:00 | 4 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 50 | 41 | 41 | 46 | 52 | 45 | 55 | 56 | 0 | 0
2022-04-25 07:00 | 4 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 51 | 42 | 41 | 46 | 55 | 47 | 55 | 56 | 0 | 0
2022-04-25 08:00 | 4 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 52 | 42 | 45 | 46 | 59 | 51 | 55 | 52 | 0 | 0
2022-04-25 09:00 | 4 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 55 | 43 | 44 | 46 | 62 | 53 | 57 | 56 | 0 | 0
2022-04-25 10:00 | 4 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 57 | 43 | 44 | 46 | 62 | 55 | 59 | 61 | 0 | 0
2022-04-25 11:00 | 4 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 60 | 42 | 43 | 46 | 63 | 57 | 61 | 67 | 0 | 0
2022-04-25 12:00 | 4 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 64 | 42 | 43 | 48 | 65 | 57 | 66 | 69 | 0 | 0
2022-04-25 13:00 | 4 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 57 | 42 | 42 | 54 | 66 | 59 | 68 | 73 | 0 | 0
2022-04-25 14:00 | 4 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 53 | 43 | 41 | 57 | 67 | 58 | 67 | 77 | 0 | 0
2022-04-25 15:00 | 4 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 51 | 43 | 41 | 57 | 65 | 56 | 69 | 78 | 0 | 0
2022-04-25 16:00 | 4 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 51 | 43 | 42 | 59 | 65 | 52 | 66 | 80 | 0 | 0
2022-04-25 17:00 | 4 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 50 | 43 | 43 | 57 | 64 | 51 | 64 | 78 | 0 | 0
2022-04-25 18:00 | 4 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 49 | 43 | 42 | 54 | 62 | 51 | 56 | 72 | 0 | 0
2022-04-25 19:00 | 4 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 48 | 40 | 42 | 52 | 61 | 52 | 53 | 67 | 0 | 0
2022-04-25 20:00 | 4 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 48 | 38 | 40 | 45 | 58 | 52 | 52 | 65 | 0 | 0
2022-04-25 21:00 | 4 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 47 | 35 | 39 | 39 | 57 | 51 | 52 | 64 | 0 | 0
2022-04-25 22:00 | 4 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 46 | 32 | 38 | 39 | 55 | 51 | 50 | 62 | 0 | 0
2022-04-25 23:00 | 4 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 44 | 30 | 37 | 45 | 52 | 50 | 49 | 59 | 0 | 0
2022-04-26 | 4 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 43 | 27 | 39 | 48 | 52 | 51 | 48 | 59 | 0 | 0
2022-04-26 01:00 | 4 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 42 | 26 | 39 | 46 | 52 | 50 | 46 | 57 | 0 | 0
2022-04-26 02:00 | 4 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 42 | 26 | 39 | 46 | 50 | 50 | 45 | 56 | 0 | 0
2022-04-26 03:00 | 4 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 41 | 25 | 39 | 45 | 48 | 50 | 43 | 55 | 0 | 0
2022-04-26 04:00 | 4 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 41 | 26 | 40 | 43 | 47 | 49 | 41 | 55 | 0 | 0
2022-04-26 05:00 | 4 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 40 | 28 | 39 | 39 | 47 | 49 | 41 | 56 | 0 | 0
2022-04-26 06:00 | 4 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 44 | 29 | 39 | 46 | 52 | 49 | 46 | 63 | 0 | 0
2022-04-26 07:00 | 4 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 46 | 34 | 39 | 48 | 55 | 50 | 49 | 72 | 0 | 0
2022-04-26 08:00 | 4 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 50 | 40 | 39 | 52 | 56 | 51 | 53 | 77 | 0 | 0
2022-04-26 09:00 | 4 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 69 | 52 | 45 | 38 | 52 | 58 | 53 | 56 | 83 | 0 | 0
2022-04-26 10:00 | 4 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 74 | 55 | 47 | 40 | 55 | 60 | 55 | 58 | 88 | 0 | 0
2022-04-26 11:00 | 4 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 76 | 56 | 48 | 40 | 55 | 63 | 56 | 59 | 90 | 0 | 0
2022-04-26 12:00 | 4 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 79 | 60 | 50 | 43 | 57 | 65 | 59 | 59 | 89 | 0 | 0
2022-04-26 13:00 | 4 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 81 | 58 | 51 | 41 | 61 | 66 | 60 | 59 | 88 | 0 | 0
2022-04-26 14:00 | 4 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 81 | 59 | 51 | 46 | 63 | 68 | 61 | 59 | 91 | 0 | 0
2022-04-26 15:00 | 4 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 82 | 60 | 52 | 45 | 63 | 65 | 63 | 60 | 89 | 0 | 0
2022-04-26 16:00 | 4 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 81 | 58 | 51 | 46 | 63 | 67 | 64 | 61 | 72 | 0 | 0
2022-04-26 17:00 | 4 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 79 | 57 | 50 | 47 | 61 | 65 | 64 | 60 | 68 | 0 | 0
2022-04-26 18:00 | 4 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 75 | 55 | 49 | 43 | 59 | 60 | 61 | 59 | 68 | 0 | 0
2022-04-26 19:00 | 4 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 73 | 52 | 47 | 40 | 55 | 58 | 58 | 56 | 67 | 0 | 0
2022-04-26 20:00 | 4 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 69 | 51 | 44 | 37 | 52 | 57 | 58 | 54 | 68 | 0 | 0
2022-04-26 21:00 | 4 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 49 | 42 | 36 | 45 | 55 | 55 | 53 | 66 | 0 | 0
2022-04-26 22:00 | 4 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 47 | 39 | 35 | 45 | 52 | 53 | 51 | 63 | 0 | 0
2022-04-26 23:00 | 4 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 45 | 37 | 35 | 43 | 52 | 52 | 51 | 61 | 0 | 0
2022-04-27 | 4 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 44 | 34 | 36 | 48 | 52 | 50 | 51 | 60 | 0 | 0
2022-04-27 01:00 | 4 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 43 | 35 | 36 | 46 | 54 | 49 | 50 | 59 | 0 | 0
2022-04-27 02:00 | 4 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 43 | 35 | 36 | 41 | 53 | 48 | 50 | 57 | 0 | 0
2022-04-27 03:00 | 4 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 42 | 36 | 37 | 39 | 50 | 47 | 50 | 57 | 0 | 0
2022-04-27 04:00 | 4 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 42 | 37 | 37 | 39 | 50 | 46 | 50 | 57 | 0 | 0
2022-04-27 05:00 | 4 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 43 | 37 | 36 | 39 | 52 | 45 | 51 | 58 | 0 | 0
2022-04-27 06:00 | 4 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 44 | 38 | 40 | 43 | 57 | 46 | 48 | 57 | 0 | 0
2022-04-27 07:00 | 4 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 45 | 39 | 48 | 46 | 60 | 50 | 47 | 59 | 0 | 0
2022-04-27 08:00 | 4 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 47 | 39 | 50 | 48 | 64 | 55 | 48 | 68 | 0 | 0
2022-04-27 09:00 | 4 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 46 | 40 | 55 | 52 | 67 | 58 | 49 | 75 | 0 | 0
2022-04-27 10:00 | 4 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 47 | 40 | 56 | 54 | 70 | 61 | 49 | 80 | 0 | 0
2022-04-27 11:00 | 4 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 47 | 40 | 60 | 55 | 73 | 65 | 50 | 87 | 0 | 0
2022-04-27 12:00 | 4 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 48 | 40 | 62 | 57 | 76 | 66 | 50 | 89 | 0 | 0
2022-04-27 13:00 | 4 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 47 | 40 | 63 | 59 | 78 | 68 | 51 | 91 | 0 | 0
2022-04-27 14:00 | 4 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 67 | 47 | 41 | 64 | 61 | 76 | 67 | 51 | 91 | 0 | 0
2022-04-27 15:00 | 4 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 69 | 47 | 41 | 65 | 61 | 77 | 67 | 57 | 91 | 0 | 0
2022-04-27 16:00 | 4 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 68 | 47 | 41 | 65 | 59 | 76 | 66 | 51 | 88 | 0 | 0
2022-04-27 17:00 | 4 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 48 | 41 | 64 | 59 | 74 | 64 | 51 | 86 | 0 | 0
2022-04-27 18:00 | 4 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 48 | 41 | 61 | 57 | 72 | 61 | 51 | 84 | 0 | 0
2022-04-27 19:00 | 4 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 47 | 41 | 60 | 57 | 67 | 58 | 50 | 83 | 0 | 0
2022-04-27 20:00 | 4 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 48 | 41 | 59 | 54 | 66 | 56 | 50 | 72 | 0 | 0
2022-04-27 21:00 | 4 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 48 | 41 | 60 | 52 | 65 | 54 | 50 | 70 | 0 | 0
2022-04-27 22:00 | 4 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 48 | 41 | 61 | 52 | 64 | 52 | 50 | 68 | 0 | 0
2022-04-27 23:00 | 4 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 48 | 41 | 60 | 50 | 64 | 50 | 50 | 64 | 0 | 0
2022-04-28 | 4 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 48 | 41 | 60 | 50 | 63 | 49 | 50 | 63 | 0 | 0
2022-04-28 01:00 | 4 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 48 | 41 | 56 | 50 | 62 | 46 | 50 | 61 | 0 | 0
2022-04-28 02:00 | 4 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 47 | 41 | 46 | 50 | 61 | 44 | 50 | 62 | 0 | 0
2022-04-28 03:00 | 4 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 47 | 41 | 43 | 50 | 59 | 43 | 49 | 62 | 0 | 0
2022-04-28 04:00 | 4 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 47 | 41 | 43 | 48 | 58 | 42 | 49 | 59 | 0 | 0
2022-04-28 05:00 | 4 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 47 | 42 | 41 | 50 | 59 | 41 | 50 | 59 | 0 | 0
2022-04-28 06:00 | 4 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 47 | 42 | 40 | 50 | 60 | 44 | 50 | 64 | 0 | 0
2022-04-28 07:00 | 4 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 48 | 42 | 39 | 52 | 62 | 49 | 50 | 68 | 0 | 0
2022-04-28 08:00 | 4 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 48 | 43 | 39 | 52 | 64 | 55 | 51 | 72 | 0 | 0
2022-04-28 09:00 | 4 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 48 | 43 | 41 | 54 | 65 | 59 | 51 | 83 | 0 | 0
2022-04-28 10:00 | 4 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 47 | 44 | 41 | 61 | 65 | 62 | 51 | 85 | 0 | 0
2022-04-28 11:00 | 4 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 46 | 44 | 40 | 63 | 67 | 64 | 50 | 88 | 0 | 0
2022-04-28 12:00 | 4 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 46 | 45 | 40 | 64 | 67 | 66 | 50 | 90 | 0 | 0
2022-04-28 13:00 | 4 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 47 | 45 | 39 | 70 | 68 | 66 | 50 | 89 | 0 | 0
2022-04-28 14:00 | 4 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 46 | 45 | 39 | 72 | 69 | 67 | 52 | 89 | 0 | 0
2022-04-28 15:00 | 4 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 46 | 45 | 39 | 72 | 68 | 66 | 52 | 88 | 0 | 0
2022-04-28 16:00 | 4 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 46 | 45 | 38 | 68 | 68 | 67 | 52 | 86 | 0 | 0
2022-04-28 17:00 | 4 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 45 | 44 | 39 | 66 | 67 | 64 | 51 | 84 | 0 | 0
2022-04-28 18:00 | 4 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 45 | 44 | 37 | 64 | 64 | 62 | 50 | 82 | 0 | 0
2022-04-28 19:00 | 4 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 44 | 44 | 36 | 61 | 62 | 60 | 49 | 81 | 0 | 0
2022-04-28 20:00 | 4 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 44 | 43 | 36 | 63 | 59 | 58 | 48 | 78 | 0 | 0
2022-04-28 21:00 | 4 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 44 | 43 | 38 | 64 | 58 | 54 | 48 | 73 | 0 | 0
2022-04-28 22:00 | 4 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 43 | 43 | 37 | 63 | 55 | 52 | 48 | 74 | 0 | 0
2022-04-28 23:00 | 4 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 43 | 42 | 35 | 61 | 55 | 50 | 47 | 74 | 0 | 0
2022-04-29 | 4 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 43 | 42 | 33 | 57 | 54 | 49 | 46 | 66 | 0 | 0
2022-04-29 01:00 | 4 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 42 | 42 | 32 | 55 | 51 | 47 | 46 | 68 | 0 | 0
2022-04-29 02:00 | 4 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 42 | 41 | 26 | 55 | 52 | 45 | 46 | 63 | 0 | 0
2022-04-29 03:00 | 4 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 42 | 41 | 24 | 54 | 51 | 45 | 46 | 62 | 0 | 0
2022-04-29 04:00 | 4 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 42 | 41 | 27 | 52 | 49 | 45 | 46 | 62 | 0 | 0
2022-04-29 05:00 | 4 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 42 | 41 | 26 | 52 | 51 | 44 | 46 | 61 | 0 | 0
2022-04-29 06:00 | 4 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 44 | 41 | 30 | 48 | 55 | 49 | 48 | 65 | 0 | 0
2022-04-29 07:00 | 4 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 44 | 42 | 38 | 48 | 60 | 55 | 49 | 69 | 0 | 0
2022-04-29 08:00 | 4 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 45 | 43 | 41 | 48 | 63 | 60 | 50 | 71 | 0 | 0
2022-04-29 09:00 | 4 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 47 | 44 | 41 | 48 | 65 | 63 | 52 | 71 | 0 | 0
2022-04-29 10:00 | 4 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 48 | 44 | 42 | 48 | 67 | 67 | 52 | 73 | 0 | 0
2022-04-29 11:00 | 4 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 49 | 43 | 43 | 50 | 68 | 70 | 52 | 75 | 0 | 0
2022-04-29 12:00 | 4 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 69 | 50 | 43 | 43 | 50 | 69 | 70 | 53 | 70 | 0 | 0
2022-04-29 13:00 | 4 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 71 | 51 | 44 | 45 | 50 | 69 | 72 | 53 | 63 | 0 | 0
2022-04-29 14:00 | 4 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 51 | 44 | 47 | 48 | 70 | 72 | 53 | 62 | 0 | 0
2022-04-29 15:00 | 4 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 71 | 57 | 45 | 48 | 48 | 70 | 70 | 53 | 62 | 0 | 0
2022-04-29 16:00 | 4 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 72 | 50 | 45 | 48 | 48 | 70 | 71 | 52 | 62 | 0 | 0
2022-04-29 17:00 | 4 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 68 | 50 | 45 | 48 | 46 | 69 | 69 | 52 | 62 | 0 | 0
2022-04-29 18:00 | 4 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 49 | 45 | 46 | 46 | 64 | 67 | 52 | 61 | 0 | 0
2022-04-29 19:00 | 4 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 48 | 42 | 42 | 46 | 62 | 66 | 51 | 60 | 0 | 0
2022-04-29 20:00 | 4 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 48 | 39 | 39 | 45 | 60 | 62 | 51 | 60 | 0 | 0
2022-04-29 21:00 | 4 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 48 | 36 | 35 | 45 | 57 | 62 | 51 | 59 | 0 | 0
2022-04-29 22:00 | 4 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 48 | 36 | 35 | 45 | 54 | 61 | 51 | 58 | 0 | 0
2022-04-29 23:00 | 4 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 47 | 36 | 34 | 45 | 55 | 59 | 50 | 57 | 0 | 0
2022-04-30 | 4 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 47 | 36 | 35 | 43 | 54 | 57 | 50 | 57 | 0 | 0
2022-04-30 01:00 | 4 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 47 | 37 | 36 | 43 | 55 | 55 | 50 | 57 | 0 | 0
2022-04-30 02:00 | 4 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 47 | 38 | 35 | 43 | 56 | 52 | 50 | 56 | 0 | 0
2022-04-30 03:00 | 4 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 46 | 39 | 36 | 43 | 56 | 49 | 50 | 56 | 0 | 0
2022-04-30 04:00 | 4 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 46 | 40 | 36 | 43 | 56 | 48 | 50 | 56 | 0 | 0
2022-04-30 05:00 | 4 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 47 | 40 | 37 | 43 | 56 | 44 | 50 | 56 | 0 | 0
2022-04-30 06:00 | 4 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 48 | 41 | 43 | 46 | 56 | 43 | 51 | 56 | 0 | 0
2022-04-30 07:00 | 4 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 49 | 44 | 51 | 50 | 56 | 44 | 53 | 57 | 0 | 0
2022-04-30 08:00 | 4 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 50 | 46 | 54 | 52 | 58 | 46 | 53 | 57 | 0 | 0
2022-04-30 09:00 | 4 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 69 | 53 | 49 | 54 | 54 | 54 | 49 | 55 | 57 | 0 | 0
2022-04-30 10:00 | 4 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 73 | 54 | 50 | 55 | 57 | 53 | 51 | 59 | 58 | 0 | 0
2022-04-30 11:00 | 4 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 77 | 56 | 51 | 54 | 61 | 53 | 53 | 59 | 57 | 0 | 0
2022-04-30 12:00 | 4 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 80 | 60 | 52 | 53 | 63 | 53 | 55 | 61 | 59 | 0 | 0
2022-04-30 13:00 | 4 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 81 | 62 | 53 | 55 | 61 | 50 | 56 | 62 | 63 | 0 | 0
2022-04-30 14:00 | 4 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 82 | 64 | 54 | 56 | 54 | 50 | 56 | 62 | 62 | 0 | 0
2022-04-30 15:00 | 4 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 83 | 64 | 55 | 58 | 54 | 50 | 55 | 63 | 63 | 0 | 0
2022-04-30 16:00 | 4 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 82 | 64 | 54 | 58 | 54 | 50 | 54 | 63 | 63 | 0 | 0
2022-04-30 17:00 | 4 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 81 | 64 | 53 | 57 | 54 | 50 | 52 | 62 | 62 | 0 | 0
2022-04-30 18:00 | 4 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 74 | 59 | 52 | 55 | 54 | 50 | 48 | 60 | 61 | 0 | 0
2022-04-30 19:00 | 4 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 72 | 56 | 51 | 50 | 55 | 51 | 44 | 59 | 59 | 0 | 0
2022-04-30 20:00 | 4 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 54 | 49 | 46 | 55 | 51 | 42 | 58 | 58 | 0 | 0
2022-04-30 21:00 | 4 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 52 | 49 | 48 | 55 | 51 | 42 | 55 | 55 | 0 | 0
2022-04-30 22:00 | 4 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 50 | 48 | 51 | 54 | 51 | 42 | 52 | 53 | 0 | 0
2022-04-30 23:00 | 4 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 47 | 47 | 53 | 54 | 51 | 41 | 49 | 50 | 0 | 0
2022-05-01 | 5 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 46 | 46 | 56 | 53 | 52 | 41 | 46 | 47 | #N/A | #N/A
2022-05-01 01:00 | 5 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 43 | 46 | 58 | 52 | 52 | 40 | 43 | 44 | #N/A | #N/A
2022-05-01 02:00 | 5 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 41 | 45 | 61 | 52 | 52 | 40 | 40 | 42 | #N/A | #N/A
2022-05-01 03:00 | 5 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 39 | 44 | 63 | 51 | 52 | 40 | 37 | 39 | #N/A | #N/A
2022-05-01 04:00 | 5 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 40 | 44 | 65 | 52 | 50 | 37 | 35 | 37 | #N/A | #N/A
2022-05-01 05:00 | 5 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 41 | 40 | 44 | 66 | 48 | 53 | 38 | 35 | 39 | #N/A | #N/A
2022-05-01 06:00 | 5 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 41 | 44 | 65 | 58 | 57 | 40 | 40 | 45 | #N/A | #N/A
2022-05-01 07:00 | 5 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 46 | 46 | 66 | 64 | 61 | 42 | 44 | 49 | #N/A | #N/A
2022-05-01 08:00 | 5 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 45 | 48 | 66 | 66 | 66 | 45 | 47 | 54 | #N/A | #N/A
2022-05-01 09:00 | 5 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 47 | 50 | 66 | 71 | 72 | 48 | 52 | 59 | #N/A | #N/A
2022-05-01 10:00 | 5 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 51 | 51 | 51 | 74 | 78 | 50 | 54 | 59 | #N/A | #N/A
2022-05-01 11:00 | 5 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 52 | 51 | 52 | 78 | 80 | 52 | 57 | 61 | #N/A | #N/A
2022-05-01 12:00 | 5 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 53 | 52 | 57 | 79 | 83 | 54 | 55 | 62 | #N/A | #N/A
2022-05-01 13:00 | 5 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 52 | 52 | 60 | 81 | 83 | 56 | 59 | 66 | #N/A | #N/A
2022-05-01 14:00 | 5 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 52 | 53 | 63 | 77 | 83 | 56 | 60 | 63 | #N/A | #N/A
2022-05-01 15:00 | 5 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 53 | 53 | 62 | 63 | 83 | 58 | 60 | 62 | #N/A | #N/A
2022-05-01 16:00 | 5 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 53 | 53 | 60 | 63 | 82 | 57 | 60 | 63 | #N/A | #N/A
2022-05-01 17:00 | 5 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 51 | 52 | 57 | 63 | 79 | 56 | 60 | 61 | #N/A | #N/A
2022-05-01 18:00 | 5 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 48 | 52 | 52 | 61 | 74 | 55 | 58 | 59 | #N/A | #N/A
2022-05-01 19:00 | 5 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 45 | 51 | 50 | 62 | 71 | 52 | 54 | 55 | #N/A | #N/A
2022-05-01 20:00 | 5 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 44 | 50 | 49 | 61 | 67 | 50 | 54 | 53 | #N/A | #N/A
2022-05-01 21:00 | 5 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 42 | 49 | 46 | 59 | 65 | 46 | 51 | 47 | #N/A | #N/A
2022-05-01 22:00 | 5 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 42 | 47 | 43 | 57 | 64 | 44 | 47 | 46 | #N/A | #N/A
2022-05-01 23:00 | 5 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 41 | 45 | 40 | 55 | 63 | 41 | 46 | 45 | #N/A | #N/A
2022-05-02 | 5 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 41 | 43 | 40 | 55 | 61 | 40 | 43 | 40 | #N/A | #N/A
2022-05-02 01:00 | 5 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 39 | 41 | 38 | 54 | 59 | 39 | 42 | 40 | #N/A | #N/A
2022-05-02 02:00 | 5 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 38 | 40 | 37 | 52 | 57 | 38 | 43 | 41 | #N/A | #N/A
2022-05-02 03:00 | 5 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 37 | 38 | 36 | 49 | 56 | 37 | 42 | 41 | #N/A | #N/A
2022-05-02 04:00 | 5 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 38 | 40 | 36 | 48 | 56 | 35 | 41 | 40 | #N/A | #N/A
2022-05-02 05:00 | 5 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 38 | 41 | 36 | 48 | 58 | 36 | 44 | 41 | #N/A | #N/A
2022-05-02 06:00 | 5 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 40 | 43 | 36 | 47 | 62 | 40 | 45 | 46 | #N/A | #N/A
2022-05-02 07:00 | 5 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 41 | 49 | 36 | 47 | 67 | 46 | 50 | 51 | #N/A | #N/A
2022-05-02 08:00 | 5 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 54 | 45 | 54 | 36 | 47 | 71 | 52 | 54 | 52 | #N/A | #N/A
2022-05-02 09:00 | 5 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 49 | 60 | 37 | 47 | 77 | 57 | 55 | 53 | #N/A | #N/A
2022-05-02 10:00 | 5 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 48 | 61 | 39 | 46 | 82 | 60 | 57 | 54 | #N/A | #N/A
2022-05-02 11:00 | 5 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 50 | 63 | 40 | 47 | 84 | 63 | 60 | 54 | #N/A | #N/A
2022-05-02 12:00 | 5 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 51 | 64 | 42 | 48 | 86 | 65 | 59 | 55 | #N/A | #N/A
2022-05-02 13:00 | 5 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 58 | 50 | 64 | 44 | 48 | 86 | 67 | 59 | 57 | #N/A | #N/A
2022-05-02 14:00 | 5 | 1 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 51 | 65 | 44 | 47 | 86 | 69 | 61 | 57 | #N/A | #N/A
2022-05-02 15:00 | 5 | 1 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 50 | 65 | 44 | 46 | 86 | 70 | 60 | 56 | #N/A | #N/A
2022-05-02 16:00 | 5 | 1 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 51 | 61 | 45 | 46 | 86 | 70 | 62 | 57 | #N/A | #N/A
2022-05-02 17:00 | 5 | 1 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 51 | 58 | 44 | 46 | 81 | 69 | 61 | 56 | #N/A | #N/A
2022-05-02 18:00 | 5 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 51 | 54 | 43 | 46 | 77 | 67 | 58 | 55 | #N/A | #N/A
2022-05-02 19:00 | 5 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 49 | 52 | 41 | 46 | 73 | 64 | 56 | 53 | #N/A | #N/A
2022-05-02 20:00 | 5 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 47 | 51 | 42 | 46 | 69 | 61 | 54 | 49 | #N/A | #N/A
2022-05-02 21:00 | 5 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 46 | 49 | 41 | 45 | 66 | 60 | 51 | 51 | #N/A | #N/A
2022-05-02 22:00 | 5 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 45 | 47 | 40 | 45 | 67 | 59 | 48 | 45 | #N/A | #N/A
2022-05-02 23:00 | 5 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 45 | 45 | 39 | 45 | 64 | 58 | 46 | 42 | #N/A | #N/A
2022-05-03 | 5 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 44 | 43 | 37 | 45 | 63 | 57 | 45 | 40 | #N/A | #N/A
2022-05-03 01:00 | 5 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 42 | 42 | 36 | 45 | 65 | 57 | 45 | 40 | #N/A | #N/A
2022-05-03 02:00 | 5 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 42 | 41 | 36 | 46 | 62 | 58 | 43 | 38 | #N/A | #N/A
2022-05-03 03:00 | 5 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 41 | 40 | 36 | 45 | 62 | 61 | 44 | 37 | #N/A | #N/A
2022-05-03 04:00 | 5 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 39 | 41 | 34 | 45 | 61 | 60 | 44 | 37 | #N/A | #N/A
2022-05-03 05:00 | 5 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 40 | 42 | 35 | 44 | 61 | 58 | 43 | 37 | #N/A | #N/A
2022-05-03 06:00 | 5 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 42 | 43 | 37 | 44 | 65 | 58 | 46 | 38 | #N/A | #N/A
2022-05-03 07:00 | 5 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 46 | 49 | 40 | 44 | 70 | 59 | 47 | 45 | #N/A | #N/A
2022-05-03 08:00 | 5 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 45 | 55 | 41 | 46 | 74 | 59 | 51 | 51 | #N/A | #N/A
2022-05-03 09:00 | 5 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 46 | 61 | 41 | 47 | 78 | 59 | 51 | 55 | #N/A | #N/A
2022-05-03 10:00 | 5 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 54 | 47 | 64 | 41 | 51 | 83 | 59 | 48 | 59 | #N/A | #N/A
2022-05-03 11:00 | 5 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 48 | 66 | 42 | 55 | 86 | 60 | 49 | 60 | #N/A | #N/A
2022-05-03 12:00 | 5 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 49 | 69 | 43 | 58 | 88 | 61 | 49 | 58 | #N/A | #N/A
2022-05-03 13:00 | 5 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 54 | 49 | 70 | 44 | 60 | 89 | 61 | 47 | 58 | #N/A | #N/A
2022-05-03 14:00 | 5 | 2 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 47 | 50 | 71 | 45 | 62 | 89 | 61 | 44 | 60 | #N/A | #N/A
2022-05-03 15:00 | 5 | 2 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 46 | 52 | 72 | 44 | 63 | 89 | 63 | 43 | 60 | #N/A | #N/A
2022-05-03 16:00 | 5 | 2 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 46 | 52 | 70 | 45 | 61 | 87 | 63 | 44 | 58 | #N/A | #N/A
2022-05-03 17:00 | 5 | 2 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 45 | 51 | 67 | 45 | 60 | 84 | 62 | 45 | 57 | #N/A | #N/A
2022-05-03 18:00 | 5 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 49 | 65 | 44 | 58 | 80 | 63 | 45 | 54 | #N/A | #N/A
2022-05-03 19:00 | 5 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 45 | 61 | 43 | 55 | 77 | 62 | 45 | 52 | #N/A | #N/A
2022-05-03 20:00 | 5 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 46 | 57 | 42 | 55 | 72 | 58 | 45 | 49 | #N/A | #N/A
2022-05-03 21:00 | 5 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 45 | 53 | 42 | 52 | 72 | 56 | 45 | 48 | #N/A | #N/A
2022-05-03 22:00 | 5 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 45 | 51 | 42 | 50 | 72 | 55 | 45 | 47 | #N/A | #N/A
2022-05-03 23:00 | 5 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 45 | 49 | 40 | 48 | 70 | 53 | 45 | 45 | #N/A | #N/A
2022-05-04 | 5 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 45 | 47 | 38 | 47 | 68 | 50 | 45 | 44 | #N/A | #N/A
2022-05-04 01:00 | 5 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 42 | 44 | 37 | 45 | 68 | 49 | 45 | 45 | #N/A | #N/A
2022-05-04 02:00 | 5 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 41 | 42 | 36 | 39 | 66 | 47 | 45 | 46 | #N/A | #N/A
2022-05-04 03:00 | 5 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 39 | 39 | 35 | 39 | 65 | 46 | 44 | 45 | #N/A | #N/A
2022-05-04 04:00 | 5 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 40 | 42 | 34 | 38 | 65 | 45 | 45 | 45 | #N/A | #N/A
2022-05-04 05:00 | 5 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 40 | 45 | 34 | 40 | 63 | 45 | 44 | 45 | #N/A | #N/A
2022-05-04 06:00 | 5 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 42 | 48 | 39 | 44 | 67 | 45 | 45 | 47 | #N/A | #N/A
2022-05-04 07:00 | 5 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 46 | 49 | 53 | 47 | 49 | 70 | 45 | 45 | 52 | #N/A | #N/A
2022-05-04 08:00 | 5 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 45 | 54 | 57 | 50 | 53 | 72 | 45 | 46 | 57 | #N/A | #N/A
2022-05-04 09:00 | 5 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 46 | 56 | 62 | 54 | 57 | 76 | 46 | 47 | 59 | #N/A | #N/A
2022-05-04 10:00 | 5 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 47 | 58 | 64 | 55 | 59 | 81 | 47 | 47 | 61 | #N/A | #N/A
2022-05-04 11:00 | 5 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 49 | 60 | 66 | 55 | 60 | 86 | 46 | 48 | 62 | #N/A | #N/A
2022-05-04 12:00 | 5 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 49 | 62 | 68 | 56 | 64 | 88 | 46 | 49 | 63 | #N/A | #N/A
2022-05-04 13:00 | 5 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 47 | 63 | 68 | 58 | 65 | 90 | 47 | 51 | 64 | #N/A | #N/A
2022-05-04 14:00 | 5 | 3 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 46 | 64 | 68 | 59 | 65 | 90 | 48 | 54 | 65 | #N/A | #N/A
2022-05-04 15:00 | 5 | 3 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 45 | 64 | 68 | 59 | 67 | 90 | 48 | 54 | 65 | #N/A | #N/A
2022-05-04 16:00 | 5 | 3 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 45 | 64 | 66 | 60 | 67 | 88 | 47 | 53 | 64 | #N/A | #N/A
2022-05-04 17:00 | 5 | 3 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 45 | 63 | 65 | 60 | 66 | 85 | 46 | 52 | 62 | #N/A | #N/A
2022-05-04 18:00 | 5 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 61 | 63 | 61 | 61 | 82 | 45 | 52 | 59 | #N/A | #N/A
2022-05-04 19:00 | 5 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 58 | 58 | 60 | 60 | 79 | 42 | 48 | 58 | #N/A | #N/A
2022-05-04 20:00 | 5 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 57 | 54 | 59 | 60 | 77 | 41 | 46 | 57 | #N/A | #N/A
2022-05-04 21:00 | 5 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 56 | 49 | 60 | 60 | 75 | 41 | 46 | 57 | #N/A | #N/A
2022-05-04 22:00 | 5 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 44 | 53 | 50 | 60 | 54 | 73 | 40 | 45 | 57 | #N/A | #N/A
2022-05-04 23:00 | 5 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 43 | 53 | 52 | 60 | 51 | 72 | 40 | 45 | 56 | #N/A | #N/A
2022-05-05 | 5 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 43 | 52 | 53 | 61 | 51 | 71 | 39 | 45 | 55 | #N/A | #N/A
2022-05-05 01:00 | 5 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 43 | 51 | 50 | 62 | 51 | 71 | 38 | 44 | 55 | #N/A | #N/A
2022-05-05 02:00 | 5 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 43 | 51 | 46 | 61 | 52 | 72 | 37 | 45 | 54 | #N/A | #N/A
2022-05-05 03:00 | 5 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 43 | 49 | 43 | 62 | 49 | 69 | 35 | 45 | 54 | #N/A | #N/A
2022-05-05 04:00 | 5 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 44 | 49 | 46 | 59 | 48 | 69 | 35 | 46 | 55 | #N/A | #N/A
2022-05-05 05:00 | 5 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 44 | 50 | 50 | 59 | 50 | 68 | 35 | 46 | 54 | #N/A | #N/A
2022-05-05 06:00 | 5 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 51 | 53 | 61 | 53 | 70 | 37 | 47 | 56 | #N/A | #N/A
2022-05-05 07:00 | 5 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 49 | 52 | 59 | 67 | 58 | 76 | 42 | 52 | 57 | #N/A | #N/A
2022-05-05 08:00 | 5 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 54 | 56 | 64 | 69 | 62 | 75 | 44 | 52 | 58 | #N/A | #N/A
2022-05-05 09:00 | 5 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 59 | 70 | 70 | 66 | 75 | 46 | 54 | 59 | #N/A | #N/A
2022-05-05 10:00 | 5 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 60 | 71 | 71 | 68 | 76 | 47 | 55 | 58 | #N/A | #N/A
2022-05-05 11:00 | 5 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 52 | 60 | 73 | 72 | 71 | 77 | 50 | 55 | 58 | #N/A | #N/A
2022-05-05 12:00 | 5 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 60 | 74 | 75 | 73 | 77 | 53 | 53 | 59 | #N/A | #N/A
2022-05-05 13:00 | 5 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 49 | 58 | 75 | 78 | 75 | 75 | 54 | 48 | 58 | #N/A | #N/A
2022-05-05 14:00 | 5 | 4 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 50 | 56 | 76 | 76 | 76 | 70 | 56 | 48 | 57 | #N/A | #N/A
2022-05-05 15:00 | 5 | 4 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 57 | 77 | 74 | 77 | 69 | 56 | 48 | 57 | #N/A | #N/A
2022-05-05 16:00 | 5 | 4 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 56 | 74 | 74 | 75 | 71 | 58 | 48 | 57 | #N/A | #N/A
2022-05-05 17:00 | 5 | 4 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 52 | 54 | 71 | 72 | 74 | 72 | 57 | 47 | 57 | #N/A | #N/A
2022-05-05 18:00 | 5 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 53 | 68 | 73 | 73 | 70 | 54 | 46 | 56 | #N/A | #N/A
2022-05-05 19:00 | 5 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 53 | 66 | 69 | 70 | 69 | 51 | 47 | 56 | #N/A | #N/A
2022-05-05 20:00 | 5 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 52 | 65 | 72 | 68 | 62 | 49 | 47 | 55 | #N/A | #N/A
2022-05-05 21:00 | 5 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 52 | 63 | 73 | 65 | 61 | 48 | 46 | 55 | #N/A | #N/A
2022-05-05 22:00 | 5 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 52 | 60 | 73 | 64 | 58 | 49 | 45 | 54 | #N/A | #N/A
2022-05-05 23:00 | 5 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 52 | 56 | 72 | 64 | 56 | 49 | 45 | 53 | #N/A | #N/A
2022-05-06 | 5 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 51 | 53 | 72 | 65 | 56 | 49 | 45 | 54 | #N/A | #N/A
2022-05-06 01:00 | 5 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 51 | 53 | 72 | 63 | 56 | 45 | 44 | 52 | #N/A | #N/A
2022-05-06 02:00 | 5 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 51 | 52 | 71 | 63 | 56 | 44 | 44 | 52 | #N/A | #N/A
2022-05-06 03:00 | 5 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 51 | 52 | 71 | 63 | 53 | 45 | 44 | 52 | #N/A | #N/A
2022-05-06 04:00 | 5 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 50 | 53 | 63 | 63 | 53 | 44 | 45 | 52 | #N/A | #N/A
2022-05-06 05:00 | 5 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 50 | 55 | 63 | 60 | 54 | 43 | 47 | 50 | #N/A | #N/A
2022-05-06 06:00 | 5 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 52 | 56 | 63 | 65 | 56 | 46 | 47 | 54 | #N/A | #N/A
2022-05-06 07:00 | 5 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 54 | 56 | 65 | 64 | 58 | 51 | 49 | 58 | #N/A | #N/A
2022-05-06 08:00 | 5 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 54 | 57 | 56 | 64 | 66 | 59 | 56 | 52 | 60 | #N/A | #N/A
2022-05-06 09:00 | 5 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 60 | 56 | 62 | 65 | 61 | 61 | 56 | 60 | #N/A | #N/A
2022-05-06 10:00 | 5 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 62 | 55 | 68 | 65 | 63 | 63 | 59 | 60 | #N/A | #N/A
2022-05-06 11:00 | 5 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 63 | 54 | 74 | 66 | 65 | 65 | 63 | 60 | #N/A | #N/A
2022-05-06 12:00 | 5 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 64 | 53 | 77 | 67 | 66 | 67 | 63 | 60 | #N/A | #N/A
2022-05-06 13:00 | 5 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 61 | 53 | 73 | 67 | 66 | 69 | 67 | 59 | #N/A | #N/A
2022-05-06 14:00 | 5 | 5 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 62 | 53 | 61 | 67 | 66 | 70 | 70 | 61 | #N/A | #N/A
2022-05-06 15:00 | 5 | 5 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 63 | 53 | 69 | 69 | 65 | 70 | 70 | 65 | #N/A | #N/A
2022-05-06 16:00 | 5 | 5 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 59 | 52 | 73 | 69 | 62 | 70 | 70 | 58 | #N/A | #N/A
2022-05-06 17:00 | 5 | 5 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 57 | 52 | 72 | 69 | 60 | 69 | 70 | 59 | #N/A | #N/A
2022-05-06 18:00 | 5 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 56 | 51 | 68 | 66 | 57 | 66 | 66 | 59 | #N/A | #N/A
2022-05-06 19:00 | 5 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 56 | 46 | 64 | 65 | 55 | 65 | 63 | 58 | #N/A | #N/A
2022-05-06 20:00 | 5 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 55 | 41 | 63 | 61 | 53 | 60 | 59 | 57 | #N/A | #N/A
2022-05-06 21:00 | 5 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 55 | 36 | 64 | 60 | 51 | 59 | 58 | 55 | #N/A | #N/A
2022-05-06 22:00 | 5 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 55 | 35 | 63 | 63 | 50 | 59 | 54 | 55 | #N/A | #N/A
2022-05-06 23:00 | 5 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 55 | 34 | 62 | 66 | 48 | 55 | 48 | 56 | #N/A | #N/A
2022-05-07 | 5 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 53 | 33 | 61 | 66 | 48 | 53 | 50 | 54 | #N/A | #N/A
2022-05-07 01:00 | 5 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 52 | 38 | 61 | 63 | 47 | 49 | 51 | 54 | #N/A | #N/A
2022-05-07 02:00 | 5 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 44 | 52 | 42 | 61 | 59 | 46 | 48 | 48 | 52 | #N/A | #N/A
2022-05-07 03:00 | 5 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 51 | 47 | 62 | 56 | 46 | 48 | 48 | 51 | #N/A | #N/A
2022-05-07 04:00 | 5 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 44 | 51 | 48 | 62 | 56 | 45 | 47 | 47 | 50 | #N/A | #N/A
2022-05-07 05:00 | 5 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 50 | 48 | 62 | 56 | 47 | 47 | 48 | 49 | #N/A | #N/A
2022-05-07 06:00 | 5 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 52 | 49 | 63 | 56 | 48 | 53 | 54 | 54 | #N/A | #N/A
2022-05-07 07:00 | 5 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 55 | 51 | 64 | 56 | 50 | 60 | 57 | 61 | #N/A | #N/A
2022-05-07 08:00 | 5 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 57 | 52 | 62 | 57 | 53 | 67 | 62 | 65 | #N/A | #N/A
2022-05-07 09:00 | 5 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 60 | 54 | 62 | 59 | 57 | 74 | 64 | 69 | #N/A | #N/A
2022-05-07 10:00 | 5 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 63 | 54 | 58 | 60 | 59 | 78 | 66 | 72 | #N/A | #N/A
2022-05-07 11:00 | 5 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 65 | 54 | 60 | 57 | 63 | 80 | 68 | 74 | #N/A | #N/A
2022-05-07 12:00 | 5 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 66 | 54 | 62 | 58 | 65 | 80 | 68 | 75 | #N/A | #N/A
2022-05-07 13:00 | 5 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 68 | 53 | 62 | 58 | 68 | 81 | 66 | 76 | #N/A | #N/A
2022-05-07 14:00 | 5 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 68 | 53 | 62 | 61 | 68 | 82 | 65 | 76 | #N/A | #N/A
2022-05-07 15:00 | 5 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 69 | 52 | 62 | 63 | 68 | 83 | 63 | 76 | #N/A | #N/A
2022-05-07 16:00 | 5 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 66 | 50 | 63 | 61 | 66 | 82 | 62 | 75 | #N/A | #N/A
2022-05-07 17:00 | 5 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 48 | 61 | 59 | 63 | 81 | 60 | 73 | #N/A | #N/A
2022-05-07 18:00 | 5 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 60 | 46 | 59 | 57 | 59 | 77 | 60 | 69 | #N/A | #N/A
2022-05-07 19:00 | 5 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 57 | 43 | 55 | 54 | 55 | 74 | 58 | 64 | #N/A | #N/A
2022-05-07 20:00 | 5 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 54 | 41 | 54 | 53 | 53 | 72 | 55 | 58 | #N/A | #N/A
2022-05-07 21:00 | 5 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 52 | 38 | 55 | 52 | 50 | 69 | 53 | 54 | #N/A | #N/A
2022-05-07 22:00 | 5 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 51 | 34 | 55 | 50 | 50 | 64 | 49 | 51 | #N/A | #N/A
2022-05-07 23:00 | 5 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 49 | 31 | 48 | 49 | 48 | 66 | 46 | 49 | #N/A | #N/A
2022-05-08 | 5 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 50 | 27 | 47 | 48 | 48 | 62 | 45 | 48 | #N/A | #N/A
2022-05-08 01:00 | 5 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 48 | 26 | 44 | 46 | 48 | 61 | 40 | 45 | #N/A | #N/A
2022-05-08 02:00 | 5 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 44 | 26 | 44 | 46 | 47 | 62 | 38 | 43 | #N/A | #N/A
2022-05-08 03:00 | 5 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 43 | 25 | 43 | 47 | 48 | 63 | 37 | 43 | #N/A | #N/A
2022-05-08 04:00 | 5 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 43 | 28 | 41 | 47 | 46 | 60 | 35 | 43 | #N/A | #N/A
2022-05-08 05:00 | 5 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 46 | 32 | 43 | 51 | 46 | 62 | 38 | 44 | #N/A | #N/A
2022-05-08 06:00 | 5 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 48 | 35 | 50 | 55 | 47 | 64 | 43 | 53 | #N/A | #N/A
2022-05-08 07:00 | 5 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 52 | 37 | 52 | 57 | 47 | 72 | 50 | 57 | #N/A | #N/A
2022-05-08 08:00 | 5 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 58 | 38 | 55 | 59 | 52 | 76 | 54 | 60 | #N/A | #N/A
2022-05-08 09:00 | 5 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 61 | 40 | 55 | 61 | 57 | 80 | 58 | 63 | #N/A | #N/A
2022-05-08 10:00 | 5 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 64 | 41 | 56 | 63 | 60 | 82 | 59 | 66 | #N/A | #N/A
2022-05-08 11:00 | 5 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 66 | 42 | 59 | 63 | 62 | 85 | 61 | 68 | #N/A | #N/A
2022-05-08 12:00 | 5 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 69 | 43 | 61 | 64 | 66 | 85 | 63 | 69 | #N/A | #N/A
2022-05-08 13:00 | 5 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 71 | 43 | 61 | 65 | 68 | 85 | 64 | 71 | #N/A | #N/A
2022-05-08 14:00 | 5 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 71 | 42 | 60 | 66 | 70 | 84 | 64 | 72 | #N/A | #N/A
2022-05-08 15:00 | 5 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 70 | 42 | 59 | 67 | 70 | 86 | 63 | 72 | #N/A | #N/A
2022-05-08 16:00 | 5 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 71 | 41 | 58 | 66 | 71 | 86 | 63 | 71 | #N/A | #N/A
2022-05-08 17:00 | 5 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 68 | 41 | 58 | 64 | 70 | 85 | 62 | 70 | #N/A | #N/A
2022-05-08 18:00 | 5 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 65 | 40 | 58 | 59 | 69 | 82 | 60 | 68 | #N/A | #N/A
2022-05-08 19:00 | 5 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 64 | 39 | 57 | 55 | 61 | 80 | 56 | 67 | #N/A | #N/A
2022-05-08 20:00 | 5 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 62 | 37 | 55 | 54 | 61 | 77 | 53 | 65 | #N/A | #N/A
2022-05-08 21:00 | 5 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 59 | 36 | 55 | 48 | 58 | 74 | 50 | 62 | #N/A | #N/A
2022-05-08 22:00 | 5 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 57 | 35 | 53 | 48 | 56 | 71 | 47 | 59 | #N/A | #N/A
2022-05-08 23:00 | 5 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 55 | 34 | 54 | 42 | 56 | 70 | 45 | 58 | #N/A | #N/A
2022-05-09 | 5 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 54 | 33 | 51 | 41 | 53 | 68 | 44 | 55 | #N/A | #N/A
2022-05-09 01:00 | 5 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 43 | 51 | 33 | 49 | 43 | 53 | 67 | 42 | 53 | #N/A | #N/A
2022-05-09 02:00 | 5 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 49 | 32 | 50 | 42 | 52 | 65 | 42 | 53 | #N/A | #N/A
2022-05-09 03:00 | 5 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 41 | 48 | 32 | 48 | 41 | 53 | 65 | 38 | 52 | #N/A | #N/A
2022-05-09 04:00 | 5 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 39 | 47 | 33 | 49 | 39 | 54 | 64 | 40 | 50 | #N/A | #N/A
2022-05-09 05:00 | 5 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 41 | 46 | 34 | 50 | 41 | 55 | 64 | 40 | 51 | #N/A | #N/A
2022-05-09 06:00 | 5 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 51 | 35 | 51 | 47 | 57 | 68 | 46 | 53 | #N/A | #N/A
2022-05-09 07:00 | 5 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 54 | 37 | 52 | 50 | 60 | 73 | 50 | 54 | #N/A | #N/A
2022-05-09 08:00 | 5 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 56 | 38 | 53 | 54 | 60 | 77 | 57 | 57 | #N/A | #N/A
2022-05-09 09:00 | 5 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 59 | 40 | 53 | 57 | 62 | 80 | 63 | 60 | #N/A | #N/A
2022-05-09 10:00 | 5 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 61 | 42 | 54 | 60 | 64 | 82 | 66 | 63 | #N/A | #N/A
2022-05-09 11:00 | 5 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 64 | 43 | 55 | 62 | 67 | 85 | 69 | 65 | #N/A | #N/A
2022-05-09 12:00 | 5 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 65 | 45 | 55 | 67 | 69 | 85 | 71 | 66 | #N/A | #N/A
2022-05-09 13:00 | 5 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 65 | 45 | 57 | 70 | 71 | 87 | 73 | 67 | #N/A | #N/A
2022-05-09 14:00 | 5 | 1 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 65 | 46 | 59 | 72 | 72 | 88 | 74 | 67 | #N/A | #N/A
2022-05-09 15:00 | 5 | 1 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 66 | 46 | 58 | 73 | 74 | 87 | 75 | 67 | #N/A | #N/A
2022-05-09 16:00 | 5 | 1 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 64 | 44 | 57 | 73 | 75 | 86 | 75 | 67 | #N/A | #N/A
2022-05-09 17:00 | 5 | 1 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 63 | 43 | 57 | 70 | 74 | 84 | 75 | 63 | #N/A | #N/A
2022-05-09 18:00 | 5 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 61 | 41 | 56 | 68 | 69 | 82 | 73 | 61 | #N/A | #N/A
2022-05-09 19:00 | 5 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 57 | 38 | 54 | 66 | 67 | 81 | 70 | 61 | #N/A | #N/A
2022-05-09 20:00 | 5 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 58 | 35 | 53 | 63 | 66 | 77 | 68 | 60 | #N/A | #N/A
2022-05-09 21:00 | 5 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 56 | 32 | 52 | 61 | 63 | 74 | 66 | 60 | #N/A | #N/A
2022-05-09 22:00 | 5 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 54 | 31 | 50 | 61 | 63 | 74 | 64 | 60 | #N/A | #N/A
2022-05-09 23:00 | 5 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 53 | 30 | 48 | 60 | 61 | 72 | 63 | 58 | #N/A | #N/A
2022-05-10 | 5 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 53 | 29 | 47 | 58 | 60 | 71 | 61 | 57 | #N/A | #N/A
2022-05-10 01:00 | 5 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 51 | 28 | 46 | 58 | 57 | 72 | 60 | 56 | #N/A | #N/A
2022-05-10 02:00 | 5 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 51 | 26 | 45 | 58 | 58 | 72 | 59 | 56 | #N/A | #N/A
2022-05-10 03:00 | 5 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 50 | 25 | 44 | 56 | 57 | 65 | 56 | 56 | #N/A | #N/A
2022-05-10 04:00 | 5 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 49 | 29 | 48 | 52 | 59 | 66 | 56 | 55 | #N/A | #N/A
2022-05-10 05:00 | 5 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 50 | 34 | 51 | 52 | 62 | 66 | 59 | 55 | #N/A | #N/A
2022-05-10 06:00 | 5 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 50 | 38 | 54 | 57 | 66 | 69 | 62 | 55 | #N/A | #N/A
2022-05-10 07:00 | 5 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 52 | 42 | 56 | 62 | 72 | 73 | 67 | 55 | #N/A | #N/A
2022-05-10 08:00 | 5 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 55 | 46 | 58 | 64 | 76 | 69 | 70 | 57 | #N/A | #N/A
2022-05-10 09:00 | 5 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 60 | 50 | 63 | 69 | 77 | 69 | 74 | 58 | #N/A | #N/A
2022-05-10 10:00 | 5 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 63 | 53 | 65 | 72 | 79 | 69 | 75 | 61 | #N/A | #N/A
2022-05-10 11:00 | 5 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 62 | 57 | 65 | 75 | 81 | 67 | 77 | 64 | #N/A | #N/A
2022-05-10 12:00 | 5 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 65 | 60 | 65 | 77 | 81 | 70 | 80 | 65 | #N/A | #N/A
2022-05-10 13:00 | 5 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 64 | 60 | 65 | 78 | 82 | 75 | 80 | 60 | #N/A | #N/A
2022-05-10 14:00 | 5 | 2 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 66 | 60 | 64 | 79 | 82 | 76 | 81 | 65 | #N/A | #N/A
2022-05-10 15:00 | 5 | 2 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 68 | 60 | 64 | 79 | 82 | 77 | 81 | 63 | #N/A | #N/A
2022-05-10 16:00 | 5 | 2 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 67 | 59 | 64 | 78 | 82 | 78 | 81 | 63 | #N/A | #N/A
2022-05-10 17:00 | 5 | 2 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 64 | 58 | 63 | 76 | 81 | 76 | 80 | 66 | #N/A | #N/A
2022-05-10 18:00 | 5 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 62 | 57 | 62 | 74 | 79 | 75 | 77 | 64 | #N/A | #N/A
2022-05-10 19:00 | 5 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 58 | 54 | 59 | 71 | 75 | 72 | 72 | 59 | #N/A | #N/A
2022-05-10 20:00 | 5 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 57 | 52 | 57 | 71 | 72 | 69 | 70 | 56 | #N/A | #N/A
2022-05-10 21:00 | 5 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 58 | 49 | 52 | 71 | 70 | 68 | 67 | 54 | #N/A | #N/A
2022-05-10 22:00 | 5 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 56 | 50 | 49 | 69 | 67 | 69 | 62 | 53 | #N/A | #N/A
2022-05-10 23:00 | 5 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 55 | 52 | 49 | 64 | 66 | 67 | 61 | 53 | #N/A | #N/A
2022-05-11 | 5 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 54 | 53 | 46 | 66 | 62 | 65 | 57 | 53 | #N/A | #N/A
2022-05-11 01:00 | 5 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 54 | 51 | 46 | 64 | 62 | 62 | 57 | 53 | #N/A | #N/A
2022-05-11 02:00 | 5 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 53 | 50 | 44 | 62 | 62 | 64 | 58 | 53 | #N/A | #N/A
2022-05-11 03:00 | 5 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 53 | 48 | 43 | 58 | 59 | 63 | 56 | 52 | #N/A | #N/A
2022-05-11 04:00 | 5 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 52 | 48 | 43 | 58 | 59 | 61 | 53 | 53 | #N/A | #N/A
2022-05-11 05:00 | 5 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 52 | 48 | 43 | 60 | 61 | 63 | 56 | 53 | #N/A | #N/A
2022-05-11 06:00 | 5 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 53 | 48 | 51 | 64 | 66 | 64 | 58 | 56 | #N/A | #N/A
2022-05-11 07:00 | 5 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 53 | 49 | 61 | 66 | 70 | 69 | 66 | 60 | #N/A | #N/A
2022-05-11 08:00 | 5 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 51 | 50 | 63 | 71 | 74 | 75 | 69 | 60 | #N/A | #N/A
2022-05-11 09:00 | 5 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 51 | 51 | 63 | 74 | 79 | 80 | 74 | 65 | #N/A | #N/A
2022-05-11 10:00 | 5 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 50 | 54 | 63 | 77 | 83 | 82 | 80 | 64 | #N/A | #N/A
2022-05-11 11:00 | 5 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 52 | 56 | 64 | 80 | 85 | 85 | 81 | 65 | #N/A | #N/A
2022-05-11 12:00 | 5 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 51 | 59 | 65 | 79 | 86 | 83 | 81 | 64 | #N/A | #N/A
2022-05-11 13:00 | 5 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 52 | 61 | 65 | 79 | 86 | 83 | 83 | 65 | #N/A | #N/A
2022-05-11 14:00 | 5 | 3 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 50 | 62 | 68 | 82 | 85 | 85 | 83 | 67 | #N/A | #N/A
2022-05-11 15:00 | 5 | 3 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 50 | 64 | 68 | 81 | 86 | 87 | 83 | 67 | #N/A | #N/A
2022-05-11 16:00 | 5 | 3 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 48 | 62 | 67 | 78 | 84 | 85 | 83 | 65 | #N/A | #N/A
2022-05-11 17:00 | 5 | 3 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 49 | 60 | 64 | 78 | 83 | 79 | 82 | 64 | #N/A | #N/A
2022-05-11 18:00 | 5 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 48 | 58 | 62 | 75 | 79 | 75 | 79 | 61 | #N/A | #N/A
2022-05-11 19:00 | 5 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 46 | 56 | 61 | 73 | 76 | 73 | 76 | 56 | #N/A | #N/A
2022-05-11 20:00 | 5 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 45 | 55 | 60 | 73 | 73 | 71 | 74 | 51 | #N/A | #N/A
2022-05-11 21:00 | 5 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 45 | 53 | 58 | 72 | 70 | 71 | 74 | 48 | #N/A | #N/A
2022-05-11 22:00 | 5 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 44 | 53 | 54 | 72 | 71 | 69 | 73 | 48 | #N/A | #N/A
2022-05-11 23:00 | 5 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 43 | 53 | 52 | 71 | 70 | 68 | 72 | 46 | #N/A | #N/A
2022-05-12 | 5 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 40 | 53 | 50 | 70 | 69 | 67 | 70 | 43 | #N/A | #N/A
2022-05-12 01:00 | 5 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 42 | 52 | 48 | 69 | 66 | 66 | 67 | 41 | #N/A | #N/A
2022-05-12 02:00 | 5 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 42 | 51 | 49 | 68 | 64 | 67 | 69 | 40 | #N/A | #N/A
2022-05-12 03:00 | 5 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 38 | 50 | 47 | 67 | 64 | 65 | 68 | 40 | #N/A | #N/A
2022-05-12 04:00 | 5 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 31 | 49 | 47 | 64 | 62 | 64 | 68 | 39 | #N/A | #N/A
2022-05-12 05:00 | 5 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 34 | 49 | 47 | 66 | 65 | 64 | 68 | 41 | #N/A | #N/A
2022-05-12 06:00 | 5 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 42 | 48 | 52 | 67 | 68 | 66 | 67 | 45 | #N/A | #N/A
2022-05-12 07:00 | 5 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 47 | 50 | 55 | 69 | 71 | 69 | 69 | 51 | #N/A | #N/A
2022-05-12 08:00 | 5 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 51 | 52 | 57 | 71 | 76 | 74 | 68 | 55 | #N/A | #N/A
2022-05-12 09:00 | 5 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 56 | 54 | 60 | 74 | 80 | 76 | 67 | 61 | #N/A | #N/A
2022-05-12 10:00 | 5 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 60 | 58 | 60 | 76 | 84 | 79 | 59 | 64 | #N/A | #N/A
2022-05-12 11:00 | 5 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 62 | 61 | 63 | 78 | 83 | 82 | 56 | 66 | #N/A | #N/A
2022-05-12 12:00 | 5 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 65 | 65 | 64 | 80 | 83 | 78 | 55 | 69 | #N/A | #N/A
2022-05-12 13:00 | 5 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 67 | 63 | 66 | 79 | 79 | 72 | 56 | 71 | #N/A | #N/A
2022-05-12 14:00 | 5 | 4 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 68 | 62 | 64 | 76 | 81 | 73 | 61 | 73 | #N/A | #N/A
2022-05-12 15:00 | 5 | 4 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 69 | 60 | 65 | 76 | 80 | 79 | 64 | 72 | #N/A | #N/A
2022-05-12 16:00 | 5 | 4 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 68 | 60 | 64 | 73 | 77 | 77 | 65 | 72 | #N/A | #N/A
2022-05-12 17:00 | 5 | 4 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 68 | 59 | 63 | 66 | 77 | 65 | 63 | 71 | #N/A | #N/A
2022-05-12 18:00 | 5 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 65 | 59 | 60 | 66 | 76 | 64 | 60 | 69 | #N/A | #N/A
2022-05-12 19:00 | 5 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 62 | 59 | 56 | 65 | 70 | 65 | 57 | 68 | #N/A | #N/A
2022-05-12 20:00 | 5 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 61 | 58 | 55 | 64 | 65 | 65 | 54 | 68 | #N/A | #N/A
2022-05-12 21:00 | 5 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 61 | 58 | 52 | 64 | 63 | 64 | 52 | 67 | #N/A | #N/A
2022-05-12 22:00 | 5 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 60 | 58 | 51 | 62 | 62 | 60 | 49 | 65 | #N/A | #N/A
2022-05-12 23:00 | 5 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 58 | 58 | 50 | 63 | 60 | 57 | 48 | 62 | #N/A | #N/A
2022-05-13 | 5 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 57 | 58 | 59 | 63 | 59 | 56 | 44 | 60 | #N/A | #N/A
2022-05-13 01:00 | 5 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 55 | 58 | 58 | 64 | 58 | 54 | 42 | 59 | #N/A | #N/A
2022-05-13 02:00 | 5 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 55 | 57 | 59 | 64 | 57 | 52 | 40 | 58 | #N/A | #N/A
2022-05-13 03:00 | 5 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 56 | 57 | 59 | 64 | 56 | 51 | 39 | 57 | #N/A | #N/A
2022-05-13 04:00 | 5 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 56 | 57 | 59 | 62 | 55 | 51 | 39 | 56 | #N/A | #N/A
2022-05-13 05:00 | 5 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 56 | 57 | 60 | 62 | 55 | 51 | 41 | 57 | #N/A | #N/A
2022-05-13 06:00 | 5 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 59 | 57 | 61 | 64 | 56 | 51 | 45 | 60 | #N/A | #N/A
2022-05-13 07:00 | 5 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 63 | 58 | 62 | 65 | 58 | 51 | 54 | 63 | #N/A | #N/A
2022-05-13 08:00 | 5 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 68 | 58 | 67 | 68 | 59 | 51 | 58 | 67 | #N/A | #N/A
2022-05-13 09:00 | 5 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 72 | 59 | 68 | 69 | 62 | 53 | 60 | 71 | #N/A | #N/A
2022-05-13 10:00 | 5 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 74 | 62 | 70 | 73 | 64 | 54 | 63 | 75 | #N/A | #N/A
2022-05-13 11:00 | 5 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 75 | 64 | 70 | 74 | 66 | 55 | 65 | 82 | #N/A | #N/A
2022-05-13 12:00 | 5 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 77 | 67 | 71 | 79 | 68 | 57 | 67 | 82 | #N/A | #N/A
2022-05-13 13:00 | 5 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 75 | 68 | 67 | 81 | 70 | 58 | 68 | 81 | #N/A | #N/A
2022-05-13 14:00 | 5 | 5 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 51 | 70 | 68 | 81 | 70 | 59 | 69 | 84 | #N/A | #N/A
2022-05-13 15:00 | 5 | 5 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 50 | 71 | 70 | 83 | 70 | 60 | 68 | 82 | #N/A | #N/A
2022-05-13 16:00 | 5 | 5 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 48 | 69 | 72 | 81 | 70 | 60 | 68 | 62 | #N/A | #N/A
2022-05-13 17:00 | 5 | 5 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 48 | 66 | 69 | 79 | 69 | 59 | 65 | 62 | #N/A | #N/A
2022-05-13 18:00 | 5 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 47 | 64 | 69 | 78 | 67 | 57 | 62 | 60 | #N/A | #N/A
2022-05-13 19:00 | 5 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 46 | 59 | 67 | 71 | 64 | 55 | 57 | 59 | #N/A | #N/A
2022-05-13 20:00 | 5 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 46 | 55 | 66 | 69 | 62 | 52 | 55 | 57 | #N/A | #N/A
2022-05-13 21:00 | 5 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 45 | 50 | 65 | 71 | 61 | 51 | 53 | 54 | #N/A | #N/A
2022-05-13 22:00 | 5 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 43 | 49 | 62 | 68 | 59 | 49 | 49 | 54 | #N/A | #N/A
2022-05-13 23:00 | 5 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 43 | 47 | 60 | 63 | 57 | 49 | 47 | 53 | #N/A | #N/A
2022-05-14 | 5 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 43 | 45 | 46 | 60 | 64 | 56 | 49 | 46 | 52 | #N/A | #N/A
2022-05-14 01:00 | 5 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 44 | 46 | 59 | 59 | 54 | 48 | 46 | 52 | #N/A | #N/A
2022-05-14 02:00 | 5 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 42 | 46 | 58 | 62 | 53 | 44 | 43 | 50 | #N/A | #N/A
2022-05-14 03:00 | 5 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 39 | 42 | 46 | 58 | 64 | 51 | 45 | 43 | 47 | #N/A | #N/A
2022-05-14 04:00 | 5 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 40 | 42 | 46 | 57 | 63 | 51 | 44 | 43 | 47 | #N/A | #N/A
2022-05-14 05:00 | 5 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 38 | 47 | 57 | 62 | 51 | 44 | 43 | 46 | #N/A | #N/A
2022-05-14 06:00 | 5 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 43 | 47 | 60 | 64 | 55 | 50 | 49 | 51 | #N/A | #N/A
2022-05-14 07:00 | 5 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 47 | 45 | 60 | 67 | 60 | 56 | 54 | 55 | #N/A | #N/A
2022-05-14 08:00 | 5 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 51 | 44 | 62 | 69 | 62 | 59 | 57 | 58 | #N/A | #N/A
2022-05-14 09:00 | 5 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 53 | 42 | 64 | 71 | 65 | 62 | 62 | 61 | #N/A | #N/A
2022-05-14 10:00 | 5 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 55 | 42 | 61 | 73 | 65 | 65 | 66 | 63 | #N/A | #N/A
2022-05-14 11:00 | 5 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 57 | 43 | 63 | 75 | 67 | 67 | 67 | 67 | #N/A | #N/A
2022-05-14 12:00 | 5 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 60 | 43 | 63 | 76 | 67 | 69 | 66 | 68 | #N/A | #N/A
2022-05-14 13:00 | 5 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 61 | 43 | 64 | 78 | 69 | 68 | 69 | 70 | #N/A | #N/A
2022-05-14 14:00 | 5 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 62 | 42 | 65 | 78 | 69 | 70 | 72 | 71 | #N/A | #N/A
2022-05-14 15:00 | 5 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 62 | 42 | 65 | 80 | 68 | 71 | 72 | 72 | #N/A | #N/A
2022-05-14 16:00 | 5 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 62 | 42 | 68 | 79 | 68 | 69 | 71 | 73 | #N/A | #N/A
2022-05-14 17:00 | 5 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 61 | 41 | 66 | 77 | 66 | 69 | 69 | 71 | #N/A | #N/A
2022-05-14 18:00 | 5 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 57 | 41 | 63 | 73 | 64 | 66 | 66 | 69 | #N/A | #N/A
2022-05-14 19:00 | 5 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 54 | 41 | 61 | 68 | 62 | 63 | 65 | 59 | #N/A | #N/A
2022-05-14 20:00 | 5 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 54 | 40 | 59 | 66 | 60 | 61 | 65 | 59 | #N/A | #N/A
2022-05-14 21:00 | 5 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 53 | 40 | 58 | 60 | 59 | 58 | 64 | 54 | #N/A | #N/A
2022-05-14 22:00 | 5 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 48 | 38 | 58 | 61 | 57 | 58 | 63 | 50 | #N/A | #N/A
2022-05-14 23:00 | 5 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 47 | 36 | 58 | 65 | 55 | 57 | 62 | 49 | #N/A | #N/A
2022-05-15 | 5 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 45 | 34 | 58 | 60 | 54 | 55 | 62 | 48 | #N/A | #N/A
2022-05-15 01:00 | 5 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 43 | 31 | 58 | 56 | 53 | 54 | 62 | 44 | #N/A | #N/A
2022-05-15 02:00 | 5 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 42 | 29 | 58 | 55 | 52 | 54 | 60 | 44 | #N/A | #N/A
2022-05-15 03:00 | 5 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 42 | 26 | 58 | 53 | 52 | 52 | 60 | 44 | #N/A | #N/A
2022-05-15 04:00 | 5 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 42 | 29 | 58 | 52 | 51 | 50 | 59 | 42 | #N/A | #N/A
2022-05-15 05:00 | 5 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 47 | 33 | 58 | 51 | 52 | 52 | 59 | 44 | #N/A | #N/A
2022-05-15 06:00 | 5 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 50 | 36 | 60 | 51 | 56 | 55 | 59 | 48 | #N/A | #N/A
2022-05-15 07:00 | 5 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 57 | 40 | 64 | 51 | 60 | 61 | 60 | 53 | #N/A | #N/A
2022-05-15 08:00 | 5 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 62 | 43 | 68 | 52 | 64 | 63 | 62 | 62 | #N/A | #N/A
2022-05-15 09:00 | 5 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 65 | 47 | 69 | 55 | 66 | 64 | 62 | 64 | #N/A | #N/A
2022-05-15 10:00 | 5 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 67 | 47 | 70 | 57 | 67 | 66 | 64 | 68 | #N/A | #N/A
2022-05-15 11:00 | 5 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 69 | 47 | 75 | 56 | 68 | 65 | 66 | 72 | #N/A | #N/A
2022-05-15 12:00 | 5 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 72 | 47 | 77 | 56 | 70 | 62 | 65 | 73 | #N/A | #N/A
2022-05-15 13:00 | 5 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 73 | 48 | 76 | 55 | 71 | 63 | 64 | 74 | #N/A | #N/A
2022-05-15 14:00 | 5 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 73 | 49 | 74 | 55 | 71 | 63 | 63 | 74 | #N/A | #N/A
2022-05-15 15:00 | 5 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 73 | 50 | 77 | 55 | 73 | 67 | 63 | 74 | #N/A | #N/A
2022-05-15 16:00 | 5 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 72 | 49 | 74 | 57 | 74 | 69 | 62 | 73 | #N/A | #N/A
2022-05-15 17:00 | 5 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 70 | 49 | 72 | 57 | 73 | 67 | 60 | 72 | #N/A | #N/A
2022-05-15 18:00 | 5 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 68 | 48 | 70 | 56 | 70 | 64 | 57 | 70 | #N/A | #N/A
2022-05-15 19:00 | 5 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 64 | 47 | 69 | 56 | 69 | 59 | 54 | 69 | #N/A | #N/A
2022-05-15 20:00 | 5 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 62 | 45 | 68 | 57 | 67 | 56 | 52 | 68 | #N/A | #N/A
2022-05-15 21:00 | 5 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 61 | 44 | 67 | 57 | 60 | 55 | 50 | 67 | #N/A | #N/A
2022-05-15 22:00 | 5 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 57 | 41 | 67 | 55 | 60 | 51 | 49 | 65 | #N/A | #N/A
2022-05-15 23:00 | 5 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 55 | 37 | 68 | 54 | 56 | 48 | 47 | 64 | #N/A | #N/A
2022-05-16 | 5 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 54 | 34 | 64 | 54 | 55 | 48 | 47 | 62 | #N/A | #N/A
2022-05-16 01:00 | 5 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 53 | 33 | 65 | 54 | 53 | 49 | 46 | 62 | #N/A | #N/A
2022-05-16 02:00 | 5 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 44 | 54 | 32 | 64 | 53 | 55 | 47 | 42 | 61 | #N/A | #N/A
2022-05-16 03:00 | 5 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 53 | 31 | 64 | 53 | 54 | 46 | 42 | 61 | #N/A | #N/A
2022-05-16 04:00 | 5 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 53 | 34 | 66 | 53 | 52 | 44 | 41 | 60 | #N/A | #N/A
2022-05-16 05:00 | 5 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 53 | 37 | 66 | 53 | 55 | 44 | 40 | 60 | #N/A | #N/A
2022-05-16 06:00 | 5 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 54 | 40 | 67 | 54 | 56 | 45 | 45 | 59 | #N/A | #N/A
2022-05-16 07:00 | 5 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 56 | 44 | 69 | 54 | 60 | 50 | 49 | 59 | #N/A | #N/A
2022-05-16 08:00 | 5 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 55 | 47 | 71 | 55 | 59 | 54 | 52 | 60 | #N/A | #N/A
2022-05-16 09:00 | 5 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 55 | 51 | 73 | 55 | 61 | 57 | 56 | 61 | #N/A | #N/A
2022-05-16 10:00 | 5 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 62 | 53 | 72 | 56 | 64 | 58 | 58 | 62 | #N/A | #N/A
2022-05-16 11:00 | 5 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 65 | 55 | 70 | 56 | 67 | 59 | 61 | 62 | #N/A | #N/A
2022-05-16 12:00 | 5 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 68 | 57 | 70 | 58 | 69 | 61 | 64 | 63 | #N/A | #N/A
2022-05-16 13:00 | 5 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 69 | 58 | 69 | 58 | 69 | 62 | 65 | 63 | #N/A | #N/A
2022-05-16 14:00 | 5 | 1 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 69 | 60 | 69 | 58 | 69 | 63 | 68 | 65 | #N/A | #N/A
2022-05-16 15:00 | 5 | 1 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 70 | 61 | 70 | 58 | 68 | 63 | 69 | 65 | #N/A | #N/A
2022-05-16 16:00 | 5 | 1 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 57 | 60 | 69 | 59 | 66 | 63 | 69 | 64 | #N/A | #N/A
2022-05-16 17:00 | 5 | 1 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 57 | 59 | 68 | 59 | 64 | 62 | 68 | 62 | #N/A | #N/A
2022-05-16 18:00 | 5 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 57 | 58 | 68 | 58 | 60 | 60 | 66 | 61 | #N/A | #N/A
2022-05-16 19:00 | 5 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 55 | 55 | 67 | 57 | 58 | 56 | 61 | 58 | #N/A | #N/A
2022-05-16 20:00 | 5 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 54 | 52 | 65 | 55 | 56 | 53 | 60 | 59 | #N/A | #N/A
2022-05-16 21:00 | 5 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 54 | 49 | 64 | 55 | 54 | 50 | 58 | 57 | #N/A | #N/A
2022-05-16 22:00 | 5 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 54 | 48 | 63 | 56 | 53 | 49 | 59 | 56 | #N/A | #N/A
2022-05-16 23:00 | 5 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 53 | 46 | 61 | 56 | 52 | 46 | 58 | 56 | #N/A | #N/A
2022-05-17 | 5 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 53 | 45 | 60 | 56 | 54 | 42 | 54 | 55 | #N/A | #N/A
2022-05-17 01:00 | 5 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 52 | 45 | 61 | 56 | 54 | 43 | 56 | 55 | #N/A | #N/A
2022-05-17 02:00 | 5 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 49 | 45 | 61 | 55 | 54 | 41 | 56 | 55 | #N/A | #N/A
2022-05-17 03:00 | 5 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 48 | 45 | 61 | 55 | 54 | 38 | 55 | 55 | #N/A | #N/A
2022-05-17 04:00 | 5 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 48 | 47 | 61 | 56 | 53 | 40 | 51 | 56 | #N/A | #N/A
2022-05-17 05:00 | 5 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 49 | 48 | 60 | 57 | 54 | 36 | 54 | 55 | #N/A | #N/A
2022-05-17 06:00 | 5 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 51 | 50 | 63 | 58 | 54 | 45 | 57 | 56 | #N/A | #N/A
2022-05-17 07:00 | 5 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 52 | 53 | 66 | 58 | 54 | 51 | 61 | 57 | #N/A | #N/A
2022-05-17 08:00 | 5 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 54 | 55 | 67 | 59 | 54 | 55 | 67 | 62 | #N/A | #N/A
2022-05-17 09:00 | 5 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 56 | 58 | 70 | 59 | 58 | 58 | 71 | 66 | #N/A | #N/A
2022-05-17 10:00 | 5 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 57 | 60 | 72 | 59 | 59 | 61 | 74 | 68 | #N/A | #N/A
2022-05-17 11:00 | 5 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 60 | 61 | 71 | 59 | 59 | 63 | 77 | 72 | #N/A | #N/A
2022-05-17 12:00 | 5 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 61 | 63 | 70 | 57 | 60 | 65 | 80 | 74 | #N/A | #N/A
2022-05-17 13:00 | 5 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 64 | 61 | 74 | 57 | 61 | 67 | 82 | 67 | #N/A | #N/A
2022-05-17 14:00 | 5 | 2 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 65 | 58 | 75 | 59 | 60 | 68 | 83 | 62 | #N/A | #N/A
2022-05-17 15:00 | 5 | 2 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 65 | 56 | 76 | 58 | 61 | 69 | 84 | 60 | #N/A | #N/A
2022-05-17 16:00 | 5 | 2 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 63 | 54 | 77 | 58 | 60 | 70 | 83 | 60 | #N/A | #N/A
2022-05-17 17:00 | 5 | 2 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 60 | 51 | 78 | 58 | 60 | 69 | 83 | 61 | #N/A | #N/A
2022-05-17 18:00 | 5 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 58 | 49 | 75 | 58 | 59 | 66 | 80 | 60 | #N/A | #N/A
2022-05-17 19:00 | 5 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 55 | 48 | 73 | 56 | 58 | 61 | 77 | 59 | #N/A | #N/A
2022-05-17 20:00 | 5 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 54 | 47 | 72 | 56 | 57 | 62 | 69 | 58 | #N/A | #N/A
2022-05-17 21:00 | 5 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 53 | 46 | 71 | 56 | 57 | 56 | 71 | 58 | #N/A | #N/A
2022-05-17 22:00 | 5 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 53 | 46 | 71 | 56 | 57 | 52 | 68 | 58 | #N/A | #N/A
2022-05-17 23:00 | 5 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 52 | 46 | 70 | 56 | 55 | 48 | 65 | 57 | #N/A | #N/A
2022-05-18 | 5 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 51 | 46 | 70 | 56 | 57 | 49 | 66 | 56 | #N/A | #N/A
2022-05-18 01:00 | 5 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 51 | 47 | 69 | 54 | 57 | 47 | 59 | 55 | #N/A | #N/A
2022-05-18 02:00 | 5 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 52 | 47 | 71 | 54 | 57 | 47 | 57 | 54 | #N/A | #N/A
2022-05-18 03:00 | 5 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 52 | 48 | 69 | 53 | 57 | 46 | 57 | 54 | #N/A | #N/A
2022-05-18 04:00 | 5 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 52 | 49 | 69 | 53 | 56 | 45 | 56 | 54 | #N/A | #N/A
2022-05-18 05:00 | 5 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 52 | 50 | 69 | 53 | 56 | 44 | 61 | 54 | #N/A | #N/A
2022-05-18 06:00 | 5 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 51 | 51 | 72 | 53 | 57 | 52 | 63 | 54 | #N/A | #N/A
2022-05-18 07:00 | 5 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 51 | 52 | 75 | 52 | 58 | 58 | 68 | 54 | #N/A | #N/A
2022-05-18 08:00 | 5 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 52 | 52 | 76 | 54 | 59 | 63 | 72 | 56 | #N/A | #N/A
2022-05-18 09:00 | 5 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 53 | 53 | 79 | 57 | 59 | 67 | 75 | 56 | #N/A | #N/A
2022-05-18 10:00 | 5 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 54 | 54 | 81 | 57 | 60 | 69 | 79 | 57 | #N/A | #N/A
2022-05-18 11:00 | 5 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 56 | 56 | 76 | 62 | 60 | 70 | 83 | 58 | #N/A | #N/A
2022-05-18 12:00 | 5 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 56 | 57 | 76 | 60 | 61 | 72 | 82 | 59 | #N/A | #N/A
2022-05-18 13:00 | 5 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 57 | 57 | 77 | 63 | 61 | 74 | 78 | 59 | #N/A | #N/A
2022-05-18 14:00 | 5 | 3 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 57 | 58 | 77 | 61 | 61 | 74 | 67 | 59 | #N/A | #N/A
2022-05-18 15:00 | 5 | 3 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 57 | 58 | 78 | 60 | 61 | 75 | 69 | 60 | #N/A | #N/A
2022-05-18 16:00 | 5 | 3 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 57 | 59 | 77 | 57 | 61 | 74 | 68 | 61 | #N/A | #N/A
2022-05-18 17:00 | 5 | 3 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 57 | 59 | 79 | 55 | 61 | 74 | 67 | 61 | #N/A | #N/A
2022-05-18 18:00 | 5 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 57 | 60 | 64 | 54 | 61 | 72 | 63 | 61 | #N/A | #N/A
2022-05-18 19:00 | 5 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 56 | 59 | 66 | 52 | 61 | 69 | 62 | 62 | #N/A | #N/A
2022-05-18 20:00 | 5 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 56 | 58 | 66 | 50 | 61 | 67 | 62 | 62 | #N/A | #N/A
2022-05-18 21:00 | 5 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 55 | 57 | 66 | 49 | 60 | 62 | 61 | 62 | #N/A | #N/A
2022-05-18 22:00 | 5 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 55 | 57 | 65 | 46 | 60 | 62 | 60 | 61 | #N/A | #N/A
2022-05-18 23:00 | 5 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 55 | 56 | 66 | 46 | 60 | 62 | 59 | 62 | #N/A | #N/A
2022-05-19 | 5 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 55 | 56 | 63 | 46 | 60 | 59 | 59 | 62 | #N/A | #N/A
2022-05-19 01:00 | 5 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 55 | 55 | 60 | 44 | 60 | 57 | 56 | 60 | #N/A | #N/A
2022-05-19 02:00 | 5 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 55 | 54 | 59 | 42 | 60 | 55 | 55 | 59 | #N/A | #N/A
2022-05-19 03:00 | 5 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 55 | 53 | 59 | 44 | 60 | 57 | 52 | 59 | #N/A | #N/A
2022-05-19 04:00 | 5 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 55 | 55 | 59 | 43 | 60 | 55 | 52 | 58 | #N/A | #N/A
2022-05-19 05:00 | 5 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 55 | 56 | 61 | 44 | 61 | 54 | 51 | 58 | #N/A | #N/A
2022-05-19 06:00 | 5 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 56 | 58 | 61 | 49 | 62 | 59 | 51 | 58 | #N/A | #N/A
2022-05-19 07:00 | 5 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 56 | 57 | 62 | 51 | 63 | 63 | 51 | 58 | #N/A | #N/A
2022-05-19 08:00 | 5 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 52 | 57 | 56 | 57 | 54 | 65 | 65 | 53 | 58 | #N/A | #N/A
2022-05-19 09:00 | 5 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 58 | 55 | 61 | 57 | 69 | 68 | 53 | 60 | #N/A | #N/A
2022-05-19 10:00 | 5 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 52 | 57 | 56 | 62 | 58 | 73 | 71 | 53 | 60 | #N/A | #N/A
2022-05-19 11:00 | 5 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 58 | 57 | 63 | 62 | 73 | 73 | 54 | 61 | #N/A | #N/A
2022-05-19 12:00 | 5 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 57 | 58 | 58 | 63 | 75 | 74 | 54 | 62 | #N/A | #N/A
2022-05-19 13:00 | 5 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 52 | 58 | 59 | 55 | 65 | 76 | 73 | 54 | 62 | #N/A | #N/A
2022-05-19 14:00 | 5 | 4 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 58 | 59 | 57 | 68 | 76 | 75 | 54 | 63 | #N/A | #N/A
2022-05-19 15:00 | 5 | 4 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 52 | 57 | 60 | 58 | 69 | 76 | 74 | 54 | 62 | #N/A | #N/A
2022-05-19 16:00 | 5 | 4 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 52 | 57 | 58 | 55 | 69 | 77 | 74 | 53 | 63 | #N/A | #N/A
2022-05-19 17:00 | 5 | 4 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 57 | 57 | 56 | 69 | 77 | 75 | 52 | 62 | #N/A | #N/A
2022-05-19 18:00 | 5 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 57 | 55 | 53 | 66 | 74 | 72 | 52 | 61 | #N/A | #N/A
2022-05-19 19:00 | 5 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 56 | 52 | 53 | 64 | 70 | 66 | 52 | 60 | #N/A | #N/A
2022-05-19 20:00 | 5 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 56 | 50 | 52 | 64 | 68 | 63 | 52 | 60 | #N/A | #N/A
2022-05-19 21:00 | 5 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 56 | 47 | 51 | 62 | 68 | 63 | 52 | 59 | #N/A | #N/A
2022-05-19 22:00 | 5 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 55 | 46 | 51 | 58 | 68 | 61 | 49 | 59 | #N/A | #N/A
2022-05-19 23:00 | 5 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 55 | 44 | 50 | 54 | 69 | 59 | 48 | 59 | #N/A | #N/A
2022-05-20 | 5 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 55 | 43 | 50 | 52 | 61 | 58 | 47 | 60 | #N/A | #N/A
2022-05-20 01:00 | 5 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 55 | 43 | 51 | 49 | 63 | 57 | 45 | 59 | #N/A | #N/A
2022-05-20 02:00 | 5 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 54 | 42 | 51 | 49 | 62 | 56 | 45 | 58 | #N/A | #N/A
2022-05-20 03:00 | 5 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 54 | 42 | 50 | 48 | 61 | 55 | 45 | 58 | #N/A | #N/A
2022-05-20 04:00 | 5 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 54 | 44 | 50 | 47 | 60 | 55 | 45 | 58 | #N/A | #N/A
2022-05-20 05:00 | 5 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 55 | 45 | 50 | 49 | 58 | 54 | 45 | 59 | #N/A | #N/A
2022-05-20 06:00 | 5 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 56 | 47 | 51 | 55 | 58 | 58 | 46 | 59 | #N/A | #N/A
2022-05-20 07:00 | 5 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 48 | 57 | 51 | 50 | 61 | 59 | 63 | 47 | 62 | #N/A | #N/A
2022-05-20 08:00 | 5 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 50 | 58 | 55 | 49 | 64 | 60 | 67 | 47 | 63 | #N/A | #N/A
2022-05-20 09:00 | 5 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 50 | 59 | 59 | 50 | 67 | 61 | 69 | 48 | 63 | #N/A | #N/A
2022-05-20 10:00 | 5 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 62 | 61 | 50 | 73 | 61 | 73 | 49 | 64 | #N/A | #N/A
2022-05-20 11:00 | 5 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 50 | 66 | 63 | 50 | 77 | 64 | 76 | 49 | 67 | #N/A | #N/A
2022-05-20 12:00 | 5 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 50 | 67 | 65 | 55 | 78 | 64 | 78 | 50 | 71 | #N/A | #N/A
2022-05-20 13:00 | 5 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 50 | 69 | 65 | 55 | 80 | 65 | 78 | 51 | 66 | #N/A | #N/A
2022-05-20 14:00 | 5 | 5 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 50 | 68 | 66 | 56 | 80 | 66 | 79 | 51 | 65 | #N/A | #N/A
2022-05-20 15:00 | 5 | 5 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 71 | 66 | 53 | 80 | 66 | 80 | 52 | 65 | #N/A | #N/A
2022-05-20 16:00 | 5 | 5 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 67 | 65 | 53 | 79 | 64 | 79 | 52 | 67 | #N/A | #N/A
2022-05-20 17:00 | 5 | 5 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 51 | 67 | 64 | 52 | 78 | 62 | 78 | 52 | 66 | #N/A | #N/A
2022-05-20 18:00 | 5 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 64 | 63 | 51 | 75 | 58 | 75 | 52 | 65 | #N/A | #N/A
2022-05-20 19:00 | 5 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 62 | 61 | 51 | 71 | 55 | 72 | 51 | 64 | #N/A | #N/A
2022-05-20 20:00 | 5 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 61 | 60 | 51 | 71 | 55 | 68 | 51 | 63 | #N/A | #N/A
2022-05-20 21:00 | 5 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 60 | 58 | 51 | 69 | 54 | 69 | 51 | 63 | #N/A | #N/A
2022-05-20 22:00 | 5 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 59 | 56 | 51 | 68 | 54 | 67 | 51 | 62 | #N/A | #N/A
2022-05-20 23:00 | 5 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 59 | 55 | 51 | 64 | 54 | 65 | 51 | 62 | #N/A | #N/A
2022-05-21 | 5 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 58 | 53 | 51 | 59 | 54 | 65 | 52 | 60 | #N/A | #N/A
2022-05-21 01:00 | 5 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 57 | 53 | 51 | 62 | 53 | 64 | 53 | 58 | #N/A | #N/A
2022-05-21 02:00 | 5 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 57 | 52 | 51 | 58 | 53 | 62 | 53 | 58 | #N/A | #N/A
2022-05-21 03:00 | 5 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 57 | 52 | 51 | 57 | 53 | 61 | 53 | 58 | #N/A | #N/A
2022-05-21 04:00 | 5 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 57 | 52 | 51 | 59 | 53 | 61 | 52 | 57 | #N/A | #N/A
2022-05-21 05:00 | 5 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 57 | 53 | 52 | 60 | 54 | 61 | 51 | 58 | #N/A | #N/A
2022-05-21 06:00 | 5 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 58 | 53 | 52 | 63 | 55 | 61 | 53 | 61 | #N/A | #N/A
2022-05-21 07:00 | 5 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 59 | 54 | 52 | 67 | 56 | 63 | 56 | 61 | #N/A | #N/A
2022-05-21 08:00 | 5 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 61 | 56 | 54 | 69 | 57 | 66 | 57 | 64 | #N/A | #N/A
2022-05-21 09:00 | 5 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 61 | 57 | 56 | 70 | 57 | 68 | 60 | 68 | #N/A | #N/A
2022-05-21 10:00 | 5 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 64 | 59 | 55 | 74 | 57 | 72 | 64 | 71 | #N/A | #N/A
2022-05-21 11:00 | 5 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 67 | 60 | 56 | 78 | 57 | 73 | 66 | 69 | #N/A | #N/A
2022-05-21 12:00 | 5 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 68 | 62 | 55 | 78 | 58 | 75 | 66 | 73 | #N/A | #N/A
2022-05-21 13:00 | 5 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 65 | 63 | 56 | 81 | 58 | 73 | 67 | 73 | #N/A | #N/A
2022-05-21 14:00 | 5 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 66 | 64 | 56 | 81 | 58 | 74 | 69 | 71 | #N/A | #N/A
2022-05-21 15:00 | 5 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 67 | 65 | 53 | 65 | 58 | 73 | 71 | 71 | #N/A | #N/A
2022-05-21 16:00 | 5 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 66 | 63 | 53 | 65 | 57 | 72 | 69 | 72 | #N/A | #N/A
2022-05-21 17:00 | 5 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 59 | 62 | 52 | 64 | 57 | 69 | 69 | 70 | #N/A | #N/A
2022-05-21 18:00 | 5 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 60 | 60 | 52 | 64 | 58 | 64 | 67 | 69 | #N/A | #N/A
2022-05-21 19:00 | 5 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 57 | 51 | 63 | 59 | 58 | 64 | 67 | #N/A | #N/A
2022-05-21 20:00 | 5 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 58 | 53 | 52 | 63 | 59 | 55 | 61 | 67 | #N/A | #N/A
2022-05-21 21:00 | 5 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 57 | 50 | 52 | 62 | 59 | 53 | 62 | 64 | #N/A | #N/A
2022-05-21 22:00 | 5 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 57 | 48 | 51 | 62 | 60 | 50 | 62 | 63 | #N/A | #N/A
2022-05-21 23:00 | 5 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 57 | 47 | 51 | 61 | 60 | 48 | 60 | 61 | #N/A | #N/A
2022-05-22 | 5 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 56 | 45 | 50 | 60 | 60 | 46 | 60 | 58 | #N/A | #N/A
2022-05-22 01:00 | 5 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 57 | 43 | 50 | 58 | 60 | 44 | 59 | 60 | #N/A | #N/A
2022-05-22 02:00 | 5 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 56 | 40 | 51 | 55 | 60 | 43 | 59 | 59 | #N/A | #N/A
2022-05-22 03:00 | 5 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 56 | 38 | 51 | 54 | 61 | 44 | 58 | 59 | #N/A | #N/A
2022-05-22 04:00 | 5 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 56 | 43 | 51 | 53 | 61 | 42 | 57 | 59 | #N/A | #N/A
2022-05-22 05:00 | 5 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 57 | 48 | 52 | 55 | 61 | 43 | 58 | 60 | #N/A | #N/A
2022-05-22 06:00 | 5 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 58 | 53 | 53 | 57 | 62 | 47 | 59 | 60 | #N/A | #N/A
2022-05-22 07:00 | 5 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 60 | 58 | 54 | 59 | 62 | 51 | 63 | 62 | #N/A | #N/A
2022-05-22 08:00 | 5 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 60 | 62 | 56 | 60 | 64 | 54 | 65 | 65 | #N/A | #N/A
2022-05-22 09:00 | 5 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 63 | 67 | 57 | 62 | 65 | 55 | 69 | 70 | #N/A | #N/A
2022-05-22 10:00 | 5 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 68 | 69 | 55 | 64 | 67 | 58 | 71 | 72 | #N/A | #N/A
2022-05-22 11:00 | 5 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 68 | 72 | 54 | 65 | 70 | 61 | 75 | 77 | #N/A | #N/A
2022-05-22 12:00 | 5 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 70 | 74 | 57 | 67 | 71 | 64 | 75 | 77 | #N/A | #N/A
2022-05-22 13:00 | 5 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 72 | 75 | 57 | 67 | 72 | 66 | 78 | 75 | #N/A | #N/A
2022-05-22 14:00 | 5 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 70 | 75 | 57 | 68 | 73 | 69 | 77 | 78 | #N/A | #N/A
2022-05-22 15:00 | 5 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 72 | 76 | 55 | 68 | 72 | 68 | 78 | 80 | #N/A | #N/A
2022-05-22 16:00 | 5 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 73 | 74 | 52 | 67 | 68 | 67 | 77 | 79 | #N/A | #N/A
2022-05-22 17:00 | 5 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 72 | 73 | 52 | 66 | 68 | 66 | 75 | 75 | #N/A | #N/A
2022-05-22 18:00 | 5 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 67 | 71 | 51 | 63 | 65 | 64 | 73 | 73 | #N/A | #N/A
2022-05-22 19:00 | 5 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 66 | 66 | 51 | 60 | 63 | 61 | 71 | 70 | #N/A | #N/A
2022-05-22 20:00 | 5 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 63 | 62 | 51 | 58 | 62 | 60 | 70 | 69 | #N/A | #N/A
2022-05-22 21:00 | 5 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 61 | 57 | 51 | 56 | 61 | 59 | 66 | 66 | #N/A | #N/A
2022-05-22 22:00 | 5 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 60 | 55 | 50 | 54 | 60 | 59 | 65 | 65 | #N/A | #N/A
2022-05-22 23:00 | 5 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 59 | 52 | 51 | 54 | 60 | 58 | 65 | 63 | #N/A | #N/A
2022-05-23 | 5 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 59 | 50 | 50 | 55 | 60 | 56 | 64 | 62 | #N/A | #N/A
2022-05-23 01:00 | 5 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 57 | 49 | 50 | 56 | 59 | 54 | 62 | 61 | #N/A | #N/A
2022-05-23 02:00 | 5 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 58 | 48 | 49 | 57 | 59 | 55 | 64 | 59 | #N/A | #N/A
2022-05-23 03:00 | 5 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 57 | 47 | 47 | 57 | 60 | 55 | 62 | 58 | #N/A | #N/A
2022-05-23 04:00 | 5 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 57 | 48 | 46 | 55 | 60 | 55 | 62 | 58 | #N/A | #N/A
2022-05-23 05:00 | 5 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 59 | 49 | 46 | 55 | 60 | 55 | 64 | 58 | #N/A | #N/A
2022-05-23 06:00 | 5 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 50 | 50 | 54 | 62 | 56 | 63 | 59 | #N/A | #N/A
2022-05-23 07:00 | 5 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 64 | 58 | 54 | 54 | 62 | 58 | 66 | 61 | #N/A | #N/A
2022-05-23 08:00 | 5 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 68 | 66 | 56 | 53 | 65 | 59 | 67 | 68 | #N/A | #N/A
2022-05-23 09:00 | 5 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 72 | 74 | 57 | 54 | 68 | 60 | 73 | 72 | #N/A | #N/A
2022-05-23 10:00 | 5 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 74 | 75 | 57 | 55 | 69 | 60 | 76 | 76 | #N/A | #N/A
2022-05-23 11:00 | 5 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 76 | 77 | 59 | 55 | 68 | 60 | 79 | 80 | #N/A | #N/A
2022-05-23 12:00 | 5 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 77 | 78 | 58 | 55 | 69 | 62 | 79 | 83 | #N/A | #N/A
2022-05-23 13:00 | 5 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 79 | 79 | 54 | 56 | 71 | 61 | 77 | 84 | #N/A | #N/A
2022-05-23 14:00 | 5 | 1 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 78 | 79 | 54 | 57 | 72 | 61 | 81 | 82 | #N/A | #N/A
2022-05-23 15:00 | 5 | 1 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 77 | 80 | 55 | 58 | 72 | 61 | 83 | 81 | #N/A | #N/A
2022-05-23 16:00 | 5 | 1 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 73 | 78 | 55 | 58 | 69 | 61 | 80 | 80 | #N/A | #N/A
2022-05-23 17:00 | 5 | 1 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 73 | 77 | 54 | 57 | 68 | 61 | 78 | 80 | #N/A | #N/A
2022-05-23 18:00 | 5 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 73 | 75 | 54 | 56 | 67 | 61 | 76 | 77 | #N/A | #N/A
2022-05-23 19:00 | 5 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 71 | 71 | 53 | 55 | 65 | 60 | 75 | 76 | #N/A | #N/A
2022-05-23 20:00 | 5 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 70 | 67 | 53 | 53 | 64 | 61 | 73 | 72 | #N/A | #N/A
2022-05-23 21:00 | 5 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 70 | 63 | 51 | 52 | 63 | 60 | 68 | 70 | #N/A | #N/A
2022-05-23 22:00 | 5 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 69 | 61 | 52 | 51 | 63 | 60 | 63 | 68 | #N/A | #N/A
2022-05-23 23:00 | 5 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 67 | 60 | 52 | 50 | 63 | 60 | 62 | 67 | #N/A | #N/A
2022-05-24 | 5 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 67 | 58 | 52 | 49 | 62 | 59 | 61 | 70 | #N/A | #N/A
2022-05-24 01:00 | 5 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 63 | 57 | 52 | 49 | 62 | 59 | 60 | 67 | #N/A | #N/A
2022-05-24 02:00 | 5 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 63 | 57 | 53 | 50 | 62 | 58 | 59 | 63 | #N/A | #N/A
2022-05-24 03:00 | 5 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 60 | 56 | 52 | 49 | 61 | 58 | 58 | 62 | #N/A | #N/A
2022-05-24 04:00 | 5 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 59 | 58 | 53 | 49 | 61 | 58 | 58 | 64 | #N/A | #N/A
2022-05-24 05:00 | 5 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 59 | 59 | 53 | 50 | 62 | 58 | 58 | 64 | #N/A | #N/A
2022-05-24 06:00 | 5 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 58 | 61 | 55 | 53 | 63 | 58 | 59 | 63 | #N/A | #N/A
2022-05-24 07:00 | 5 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 57 | 64 | 57 | 58 | 65 | 60 | 61 | 63 | #N/A | #N/A
2022-05-24 08:00 | 5 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 56 | 67 | 58 | 61 | 67 | 62 | 62 | 64 | #N/A | #N/A
2022-05-24 09:00 | 5 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 54 | 70 | 61 | 64 | 70 | 65 | 65 | 69 | #N/A | #N/A
2022-05-24 10:00 | 5 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 51 | 72 | 62 | 68 | 72 | 66 | 62 | 72 | #N/A | #N/A
2022-05-24 11:00 | 5 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 52 | 73 | 64 | 70 | 72 | 67 | 63 | 71 | #N/A | #N/A
2022-05-24 12:00 | 5 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 55 | 75 | 64 | 70 | 74 | 65 | 66 | 73 | #N/A | #N/A
2022-05-24 13:00 | 5 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 58 | 75 | 65 | 70 | 77 | 63 | 65 | 77 | #N/A | #N/A
2022-05-24 14:00 | 5 | 2 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 57 | 75 | 63 | 71 | 77 | 64 | 65 | 74 | #N/A | #N/A
2022-05-24 15:00 | 5 | 2 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 57 | 75 | 63 | 71 | 75 | 63 | 65 | 78 | #N/A | #N/A
2022-05-24 16:00 | 5 | 2 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 54 | 73 | 65 | 72 | 76 | 60 | 66 | 65 | #N/A | #N/A
2022-05-24 17:00 | 5 | 2 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 53 | 72 | 64 | 70 | 74 | 59 | 64 | 64 | #N/A | #N/A
2022-05-24 18:00 | 5 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 52 | 70 | 62 | 67 | 71 | 57 | 62 | 63 | #N/A | #N/A
2022-05-24 19:00 | 5 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 52 | 67 | 59 | 64 | 68 | 57 | 60 | 61 | #N/A | #N/A
2022-05-24 20:00 | 5 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 52 | 64 | 58 | 64 | 66 | 57 | 57 | 57 | #N/A | #N/A
2022-05-24 21:00 | 5 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 51 | 61 | 56 | 60 | 63 | 57 | 56 | 57 | #N/A | #N/A
2022-05-24 22:00 | 5 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 51 | 59 | 54 | 59 | 62 | 56 | 54 | 56 | #N/A | #N/A
2022-05-24 23:00 | 5 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 51 | 58 | 52 | 55 | 61 | 55 | 53 | 56 | #N/A | #N/A
2022-05-25 | 5 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 50 | 56 | 51 | 54 | 61 | 54 | 51 | 54 | #N/A | #N/A
2022-05-25 01:00 | 5 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 50 | 55 | 50 | 52 | 61 | 54 | 51 | 54 | #N/A | #N/A
2022-05-25 02:00 | 5 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 48 | 53 | 50 | 52 | 60 | 54 | 52 | 53 | #N/A | #N/A
2022-05-25 03:00 | 5 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 47 | 52 | 49 | 52 | 60 | 53 | 50 | 52 | #N/A | #N/A
2022-05-25 04:00 | 5 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 46 | 53 | 49 | 52 | 60 | 53 | 51 | 52 | #N/A | #N/A
2022-05-25 05:00 | 5 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 45 | 55 | 51 | 54 | 59 | 52 | 53 | 52 | #N/A | #N/A
2022-05-25 06:00 | 5 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 44 | 56 | 54 | 57 | 60 | 52 | 56 | 51 | #N/A | #N/A
2022-05-25 07:00 | 5 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 46 | 60 | 62 | 62 | 59 | 52 | 59 | 52 | #N/A | #N/A
2022-05-25 08:00 | 5 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 47 | 63 | 60 | 67 | 60 | 53 | 60 | 52 | #N/A | #N/A
2022-05-25 09:00 | 5 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 46 | 67 | 62 | 70 | 60 | 52 | 61 | 53 | #N/A | #N/A
2022-05-25 10:00 | 5 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 47 | 68 | 66 | 72 | 64 | 50 | 62 | 50 | #N/A | #N/A
2022-05-25 11:00 | 5 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 46 | 69 | 65 | 73 | 63 | 50 | 63 | 54 | #N/A | #N/A
2022-05-25 12:00 | 5 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 44 | 70 | 67 | 75 | 66 | 50 | 65 | 54 | #N/A | #N/A
2022-05-25 13:00 | 5 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 46 | 69 | 64 | 76 | 67 | 49 | 66 | 53 | #N/A | #N/A
2022-05-25 14:00 | 5 | 3 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 44 | 68 | 66 | 78 | 67 | 49 | 66 | 56 | #N/A | #N/A
2022-05-25 15:00 | 5 | 3 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 44 | 67 | 65 | 78 | 66 | 49 | 66 | 53 | #N/A | #N/A
2022-05-25 16:00 | 5 | 3 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 44 | 64 | 66 | 79 | 64 | 49 | 65 | 53 | #N/A | #N/A
2022-05-25 17:00 | 5 | 3 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 44 | 62 | 65 | 76 | 63 | 49 | 64 | 52 | #N/A | #N/A
2022-05-25 18:00 | 5 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 45 | 59 | 61 | 70 | 62 | 49 | 62 | 51 | #N/A | #N/A
2022-05-25 19:00 | 5 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 44 | 54 | 59 | 66 | 61 | 48 | 61 | 50 | #N/A | #N/A
2022-05-25 20:00 | 5 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 44 | 50 | 58 | 64 | 60 | 48 | 61 | 48 | #N/A | #N/A
2022-05-25 21:00 | 5 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 44 | 45 | 58 | 64 | 59 | 48 | 60 | 46 | #N/A | #N/A
2022-05-25 22:00 | 5 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 43 | 42 | 56 | 63 | 59 | 47 | 59 | 44 | #N/A | #N/A
2022-05-25 23:00 | 5 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 43 | 40 | 55 | 63 | 59 | 47 | 57 | 43 | #N/A | #N/A
2022-05-26 | 5 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 43 | 37 | 54 | 60 | 59 | 47 | 57 | 43 | #N/A | #N/A
2022-05-26 01:00 | 5 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 43 | 37 | 54 | 60 | 59 | 47 | 58 | 44 | #N/A | #N/A
2022-05-26 02:00 | 5 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 41 | 38 | 53 | 57 | 58 | 46 | 58 | 43 | #N/A | #N/A
2022-05-26 03:00 | 5 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 40 | 38 | 54 | 59 | 58 | 46 | 58 | 42 | #N/A | #N/A
2022-05-26 04:00 | 5 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 39 | 40 | 55 | 56 | 58 | 44 | 58 | 42 | #N/A | #N/A
2022-05-26 05:00 | 5 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 41 | 42 | 56 | 58 | 57 | 44 | 58 | 44 | #N/A | #N/A
2022-05-26 06:00 | 5 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 43 | 44 | 59 | 61 | 59 | 45 | 60 | 49 | #N/A | #N/A
2022-05-26 07:00 | 5 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 47 | 48 | 64 | 66 | 59 | 46 | 60 | 52 | #N/A | #N/A
2022-05-26 08:00 | 5 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 50 | 51 | 72 | 70 | 60 | 47 | 61 | 56 | #N/A | #N/A
2022-05-26 09:00 | 5 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 53 | 55 | 76 | 75 | 61 | 47 | 62 | 60 | #N/A | #N/A
2022-05-26 10:00 | 5 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 55 | 57 | 79 | 78 | 61 | 47 | 63 | 63 | #N/A | #N/A
2022-05-26 11:00 | 5 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 57 | 58 | 80 | 79 | 61 | 48 | 63 | 66 | #N/A | #N/A
2022-05-26 12:00 | 5 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 58 | 60 | 79 | 81 | 60 | 48 | 63 | 68 | #N/A | #N/A
2022-05-26 13:00 | 5 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 59 | 60 | 75 | 82 | 62 | 48 | 63 | 70 | #N/A | #N/A
2022-05-26 14:00 | 5 | 4 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 61 | 60 | 73 | 83 | 61 | 48 | 63 | 72 | #N/A | #N/A
2022-05-26 15:00 | 5 | 4 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 62 | 60 | 75 | 82 | 62 | 47 | 64 | 71 | #N/A | #N/A
2022-05-26 16:00 | 5 | 4 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 62 | 57 | 76 | 81 | 61 | 49 | 63 | 72 | #N/A | #N/A
2022-05-26 17:00 | 5 | 4 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 62 | 55 | 75 | 79 | 61 | 48 | 61 | 71 | #N/A | #N/A
2022-05-26 18:00 | 5 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 60 | 52 | 73 | 74 | 61 | 48 | 59 | 67 | #N/A | #N/A
2022-05-26 19:00 | 5 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 58 | 48 | 70 | 73 | 60 | 46 | 59 | 64 | #N/A | #N/A
2022-05-26 20:00 | 5 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 57 | 44 | 68 | 72 | 61 | 45 | 58 | 58 | #N/A | #N/A
2022-05-26 21:00 | 5 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 54 | 40 | 68 | 67 | 61 | 44 | 58 | 53 | #N/A | #N/A
2022-05-26 22:00 | 5 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 53 | 39 | 71 | 64 | 61 | 45 | 58 | 50 | #N/A | #N/A
2022-05-26 23:00 | 5 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 53 | 39 | 69 | 62 | 61 | 45 | 57 | 49 | #N/A | #N/A
2022-05-27 | 5 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 52 | 38 | 67 | 61 | 61 | 46 | 57 | 47 | #N/A | #N/A
2022-05-27 01:00 | 5 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 50 | 36 | 67 | 60 | 61 | 46 | 57 | 46 | #N/A | #N/A
2022-05-27 02:00 | 5 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 49 | 34 | 66 | 59 | 61 | 47 | 57 | 45 | #N/A | #N/A
2022-05-27 03:00 | 5 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 51 | 32 | 65 | 60 | 60 | 49 | 54 | 44 | #N/A | #N/A
2022-05-27 04:00 | 5 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 51 | 35 | 64 | 58 | 60 | 49 | 54 | 43 | #N/A | #N/A
2022-05-27 05:00 | 5 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 52 | 38 | 65 | 59 | 61 | 48 | 55 | 46 | #N/A | #N/A
2022-05-27 06:00 | 5 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 56 | 41 | 65 | 67 | 61 | 48 | 55 | 50 | #N/A | #N/A
2022-05-27 07:00 | 5 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 59 | 46 | 66 | 67 | 61 | 49 | 56 | 56 | #N/A | #N/A
2022-05-27 08:00 | 5 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 63 | 51 | 67 | 71 | 64 | 50 | 58 | 62 | #N/A | #N/A
2022-05-27 09:00 | 5 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 67 | 56 | 68 | 77 | 65 | 51 | 59 | 67 | #N/A | #N/A
2022-05-27 10:00 | 5 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 69 | 58 | 67 | 80 | 68 | 51 | 60 | 71 | #N/A | #N/A
2022-05-27 11:00 | 5 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 72 | 59 | 66 | 80 | 68 | 52 | 60 | 75 | #N/A | #N/A
2022-05-27 12:00 | 5 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 58 | 75 | 61 | 66 | 82 | 70 | 53 | 60 | 78 | #N/A | #N/A
2022-05-27 13:00 | 5 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 76 | 59 | 65 | 80 | 71 | 53 | 60 | 80 | #N/A | #N/A
2022-05-27 14:00 | 5 | 5 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 78 | 58 | 65 | 83 | 73 | 54 | 62 | 81 | #N/A | #N/A
2022-05-27 15:00 | 5 | 5 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 78 | 56 | 64 | 82 | 72 | 55 | 63 | 82 | #N/A | #N/A
2022-05-27 16:00 | 5 | 5 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 77 | 54 | 66 | 81 | 72 | 58 | 63 | 81 | #N/A | #N/A
2022-05-27 17:00 | 5 | 5 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 76 | 53 | 66 | 80 | 67 | 59 | 63 | 80 | #N/A | #N/A
2022-05-27 18:00 | 5 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 73 | 51 | 65 | 77 | 67 | 57 | 62 | 78 | #N/A | #N/A
2022-05-27 19:00 | 5 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 71 | 48 | 65 | 75 | 65 | 55 | 61 | 73 | #N/A | #N/A
2022-05-27 20:00 | 5 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 69 | 45 | 63 | 75 | 65 | 55 | 60 | 66 | #N/A | #N/A
2022-05-27 21:00 | 5 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 67 | 42 | 61 | 74 | 61 | 54 | 60 | 61 | #N/A | #N/A
2022-05-27 22:00 | 5 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 64 | 42 | 63 | 70 | 61 | 55 | 60 | 58 | #N/A | #N/A
2022-05-27 23:00 | 5 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 63 | 42 | 63 | 70 | 60 | 54 | 60 | 57 | #N/A | #N/A
2022-05-28 | 5 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 62 | 42 | 63 | 68 | 60 | 54 | 60 | 56 | #N/A | #N/A
2022-05-28 01:00 | 5 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 62 | 43 | 62 | 67 | 59 | 53 | 60 | 53 | #N/A | #N/A
2022-05-28 02:00 | 5 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 61 | 44 | 60 | 67 | 59 | 53 | 59 | 52 | #N/A | #N/A
2022-05-28 03:00 | 5 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 58 | 45 | 60 | 66 | 59 | 53 | 59 | 51 | #N/A | #N/A
2022-05-28 04:00 | 5 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 59 | 47 | 57 | 63 | 58 | 53 | 59 | 50 | #N/A | #N/A
2022-05-28 05:00 | 5 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 57 | 48 | 59 | 62 | 60 | 53 | 60 | 53 | #N/A | #N/A
2022-05-28 06:00 | 5 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 63 | 50 | 60 | 65 | 61 | 54 | 62 | 57 | #N/A | #N/A
2022-05-28 07:00 | 5 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 66 | 53 | 65 | 69 | 63 | 55 | 63 | 62 | #N/A | #N/A
2022-05-28 08:00 | 5 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 69 | 57 | 69 | 70 | 65 | 57 | 65 | 68 | #N/A | #N/A
2022-05-28 09:00 | 5 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 73 | 60 | 67 | 68 | 66 | 56 | 68 | 74 | #N/A | #N/A
2022-05-28 10:00 | 5 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 76 | 62 | 66 | 67 | 67 | 56 | 72 | 78 | #N/A | #N/A
2022-05-28 11:00 | 5 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 77 | 65 | 69 | 67 | 70 | 57 | 76 | 82 | #N/A | #N/A
2022-05-28 12:00 | 5 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 79 | 67 | 71 | 66 | 72 | 60 | 79 | 85 | #N/A | #N/A
2022-05-28 13:00 | 5 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 80 | 66 | 72 | 64 | 74 | 62 | 81 | 86 | #N/A | #N/A
2022-05-28 14:00 | 5 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 80 | 66 | 73 | 64 | 73 | 64 | 83 | 87 | #N/A | #N/A
2022-05-28 15:00 | 5 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 81 | 65 | 74 | 64 | 75 | 61 | 83 | 85 | #N/A | #N/A
2022-05-28 16:00 | 5 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 80 | 64 | 73 | 62 | 74 | 57 | 73 | 84 | #N/A | #N/A
2022-05-28 17:00 | 5 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 79 | 64 | 73 | 61 | 73 | 56 | 70 | 82 | #N/A | #N/A
2022-05-28 18:00 | 5 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 75 | 63 | 73 | 61 | 72 | 56 | 71 | 80 | #N/A | #N/A
2022-05-28 19:00 | 5 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 71 | 59 | 66 | 60 | 70 | 55 | 69 | 77 | #N/A | #N/A
2022-05-28 20:00 | 5 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 56 | 64 | 59 | 69 | 55 | 67 | 70 | #N/A | #N/A
2022-05-28 21:00 | 5 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 66 | 52 | 64 | 57 | 67 | 55 | 65 | 66 | #N/A | #N/A
2022-05-28 22:00 | 5 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 66 | 51 | 64 | 58 | 62 | 55 | 66 | 64 | #N/A | #N/A
2022-05-28 23:00 | 5 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 67 | 49 | 62 | 58 | 61 | 55 | 64 | 61 | #N/A | #N/A
2022-05-29 | 5 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 66 | 48 | 62 | 57 | 59 | 54 | 63 | 60 | #N/A | #N/A
2022-05-29 01:00 | 5 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 49 | 60 | 55 | 57 | 54 | 62 | 60 | #N/A | #N/A
2022-05-29 02:00 | 5 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 60 | 49 | 60 | 54 | 58 | 54 | 61 | 57 | #N/A | #N/A
2022-05-29 03:00 | 5 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 50 | 58 | 53 | 58 | 53 | 61 | 54 | #N/A | #N/A
2022-05-29 04:00 | 5 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 59 | 51 | 58 | 53 | 57 | 53 | 62 | 54 | #N/A | #N/A
2022-05-29 05:00 | 5 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 57 | 51 | 60 | 54 | 59 | 53 | 62 | 56 | #N/A | #N/A
2022-05-29 06:00 | 5 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 62 | 52 | 65 | 56 | 63 | 53 | 64 | 61 | #N/A | #N/A
2022-05-29 07:00 | 5 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 67 | 56 | 68 | 59 | 66 | 55 | 69 | 65 | #N/A | #N/A
2022-05-29 08:00 | 5 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 71 | 60 | 70 | 59 | 68 | 58 | 74 | 71 | #N/A | #N/A
2022-05-29 09:00 | 5 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 73 | 64 | 75 | 60 | 68 | 58 | 79 | 75 | #N/A | #N/A
2022-05-29 10:00 | 5 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 88 | 76 | 67 | 77 | 60 | 69 | 61 | 81 | 80 | #N/A | #N/A
2022-05-29 11:00 | 5 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 88 | 78 | 71 | 73 | 61 | 70 | 61 | 83 | 84 | #N/A | #N/A
2022-05-29 12:00 | 5 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 91 | 78 | 74 | 74 | 64 | 73 | 59 | 86 | 86 | #N/A | #N/A
2022-05-29 13:00 | 5 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 93 | 80 | 71 | 74 | 65 | 73 | 61 | 87 | 87 | #N/A | #N/A
2022-05-29 14:00 | 5 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 92 | 78 | 68 | 76 | 66 | 72 | 63 | 87 | 88 | #N/A | #N/A
2022-05-29 15:00 | 5 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 88 | 78 | 65 | 78 | 67 | 74 | 65 | 87 | 86 | #N/A | #N/A
2022-05-29 16:00 | 5 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 88 | 79 | 64 | 76 | 66 | 75 | 63 | 87 | 84 | #N/A | #N/A
2022-05-29 17:00 | 5 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 77 | 64 | 77 | 64 | 73 | 63 | 86 | 84 | #N/A | #N/A
2022-05-29 18:00 | 5 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 74 | 63 | 76 | 62 | 71 | 60 | 83 | 79 | #N/A | #N/A
2022-05-29 19:00 | 5 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 70 | 62 | 71 | 60 | 70 | 58 | 78 | 72 | #N/A | #N/A
2022-05-29 20:00 | 5 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 69 | 60 | 69 | 57 | 68 | 55 | 77 | 69 | #N/A | #N/A
2022-05-29 21:00 | 5 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 71 | 59 | 66 | 55 | 66 | 54 | 75 | 66 | #N/A | #N/A
2022-05-29 22:00 | 5 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 69 | 59 | 66 | 54 | 64 | 53 | 70 | 63 | #N/A | #N/A
2022-05-29 23:00 | 5 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 67 | 59 | 64 | 52 | 64 | 52 | 70 | 63 | #N/A | #N/A
2022-05-30 | 5 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 65 | 59 | 63 | 51 | 63 | 53 | 68 | 61 | #N/A | #N/A
2022-05-30 01:00 | 5 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 62 | 58 | 63 | 50 | 61 | 52 | 67 | 60 | #N/A | #N/A
2022-05-30 02:00 | 5 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 61 | 58 | 62 | 50 | 60 | 52 | 67 | 59 | #N/A | #N/A
2022-05-30 03:00 | 5 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 59 | 57 | 62 | 49 | 59 | 52 | 64 | 57 | #N/A | #N/A
2022-05-30 04:00 | 5 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 58 | 58 | 62 | 49 | 59 | 51 | 63 | 57 | #N/A | #N/A
2022-05-30 05:00 | 5 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 61 | 59 | 66 | 52 | 59 | 51 | 66 | 59 | #N/A | #N/A
2022-05-30 06:00 | 5 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 63 | 60 | 68 | 55 | 59 | 55 | 68 | 62 | #N/A | #N/A
2022-05-30 07:00 | 5 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 66 | 63 | 73 | 58 | 60 | 60 | 73 | 65 | #N/A | #N/A
2022-05-30 08:00 | 5 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 69 | 67 | 74 | 61 | 60 | 63 | 78 | 66 | #N/A | #N/A
2022-05-30 09:00 | 5 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 73 | 70 | 76 | 63 | 62 | 64 | 81 | 69 | #N/A | #N/A
2022-05-30 10:00 | 5 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 90 | 74 | 67 | 79 | 66 | 62 | 65 | 84 | 74 | #N/A | #N/A
2022-05-30 11:00 | 5 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 92 | 79 | 65 | 79 | 68 | 66 | 68 | 86 | 80 | #N/A | #N/A
2022-05-30 12:00 | 5 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 92 | 82 | 62 | 76 | 69 | 66 | 70 | 88 | 84 | #N/A | #N/A
2022-05-30 13:00 | 5 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 92 | 84 | 65 | 76 | 69 | 66 | 71 | 89 | 86 | #N/A | #N/A
2022-05-30 14:00 | 5 | 1 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 93 | 85 | 67 | 77 | 70 | 67 | 69 | 90 | 90 | #N/A | #N/A
2022-05-30 15:00 | 5 | 1 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 92 | 86 | 70 | 78 | 69 | 68 | 69 | 91 | 90 | #N/A | #N/A
2022-05-30 16:00 | 5 | 1 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 92 | 84 | 69 | 77 | 68 | 68 | 65 | 88 | 87 | #N/A | #N/A
2022-05-30 17:00 | 5 | 1 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 81 | 67 | 76 | 67 | 67 | 64 | 87 | 87 | #N/A | #N/A
2022-05-30 18:00 | 5 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 78 | 66 | 75 | 66 | 66 | 63 | 84 | 81 | #N/A | #N/A
2022-05-30 19:00 | 5 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 73 | 65 | 73 | 65 | 64 | 62 | 81 | 71 | #N/A | #N/A
2022-05-30 20:00 | 5 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 72 | 64 | 72 | 64 | 62 | 59 | 79 | 70 | #N/A | #N/A
2022-05-30 21:00 | 5 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 71 | 63 | 71 | 64 | 60 | 59 | 78 | 66 | #N/A | #N/A
2022-05-30 22:00 | 5 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 70 | 62 | 70 | 63 | 58 | 57 | 75 | 64 | #N/A | #N/A
2022-05-30 23:00 | 5 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 68 | 61 | 69 | 62 | 57 | 58 | 73 | 62 | #N/A | #N/A
2022-05-31 | 5 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 67 | 60 | 68 | 62 | 56 | 57 | 71 | 60 | #N/A | #N/A
2022-05-31 01:00 | 5 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 65 | 60 | 68 | 59 | 55 | 56 | 70 | 58 | #N/A | #N/A
2022-05-31 02:00 | 5 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 63 | 60 | 67 | 58 | 53 | 57 | 68 | 59 | #N/A | #N/A
2022-05-31 03:00 | 5 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 64 | 60 | 66 | 58 | 52 | 56 | 66 | 57 | #N/A | #N/A
2022-05-31 04:00 | 5 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 61 | 65 | 58 | 52 | 54 | 67 | 55 | #N/A | #N/A
2022-05-31 05:00 | 5 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 61 | 66 | 59 | 50 | 56 | 67 | 58 | #N/A | #N/A
2022-05-31 06:00 | 5 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 66 | 62 | 68 | 60 | 53 | 59 | 70 | 63 | #N/A | #N/A
2022-05-31 07:00 | 5 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 70 | 63 | 72 | 61 | 56 | 59 | 73 | 73 | #N/A | #N/A
2022-05-31 08:00 | 5 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 73 | 64 | 73 | 62 | 57 | 61 | 76 | 77 | #N/A | #N/A
2022-05-31 09:00 | 5 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 74 | 65 | 74 | 63 | 60 | 65 | 80 | 81 | #N/A | #N/A
2022-05-31 10:00 | 5 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 75 | 67 | 75 | 65 | 62 | 68 | 79 | 86 | #N/A | #N/A
2022-05-31 11:00 | 5 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 76 | 68 | 74 | 65 | 64 | 70 | 75 | 90 | #N/A | #N/A
2022-05-31 12:00 | 5 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 78 | 70 | 75 | 69 | 66 | 74 | 71 | 88 | #N/A | #N/A
2022-05-31 13:00 | 5 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 79 | 66 | 75 | 69 | 67 | 74 | 76 | 89 | #N/A | #N/A
2022-05-31 14:00 | 5 | 2 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 80 | 63 | 77 | 70 | 68 | 72 | 78 | 87 | #N/A | #N/A
2022-05-31 15:00 | 5 | 2 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 79 | 59 | 79 | 71 | 70 | 72 | 79 | 88 | #N/A | #N/A
2022-05-31 16:00 | 5 | 2 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 78 | 60 | 80 | 71 | 69 | 72 | 79 | 87 | #N/A | #N/A
2022-05-31 17:00 | 5 | 2 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 77 | 61 | 81 | 70 | 69 | 71 | 78 | 86 | #N/A | #N/A
2022-05-31 18:00 | 5 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 74 | 62 | 80 | 70 | 68 | 70 | 76 | 83 | #N/A | #N/A
2022-05-31 19:00 | 5 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 70 | 60 | 79 | 70 | 67 | 70 | 75 | 78 | #N/A | #N/A
2022-05-31 20:00 | 5 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 68 | 57 | 76 | 70 | 63 | 68 | 74 | 72 | #N/A | #N/A
2022-05-31 21:00 | 5 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 67 | 53 | 73 | 67 | 62 | 66 | 73 | 70 | #N/A | #N/A
2022-05-31 22:00 | 5 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 66 | 49 | 71 | 65 | 61 | 64 | 72 | 69 | #N/A | #N/A
2022-05-31 23:00 | 5 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 65 | 45 | 68 | 62 | 60 | 61 | 71 | 67 | #N/A | #N/A
2022-06-01 | 6 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 41 | 66 | 60 | 60 | 59 | 69 | 66 | #N/A | #N/A
2022-06-01 01:00 | 6 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 63 | 37 | 63 | 57 | 59 | 56 | 68 | 64 | #N/A | #N/A
2022-06-01 02:00 | 6 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 62 | 33 | 60 | 55 | 58 | 54 | 67 | 63 | #N/A | #N/A
2022-06-01 03:00 | 6 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 61 | 29 | 58 | 52 | 57 | 52 | 66 | 61 | #N/A | #N/A
2022-06-01 04:00 | 6 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 60 | 33 | 60 | 53 | 56 | 55 | 66 | 59 | #N/A | #N/A
2022-06-01 05:00 | 6 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 60 | 37 | 62 | 54 | 59 | 55 | 67 | 63 | #N/A | #N/A
2022-06-01 06:00 | 6 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 61 | 41 | 64 | 61 | 62 | 53 | 70 | 66 | #N/A | #N/A
2022-06-01 07:00 | 6 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 64 | 46 | 65 | 64 | 67 | 54 | 72 | 72 | #N/A | #N/A
2022-06-01 08:00 | 6 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 67 | 50 | 66 | 65 | 67 | 57 | 75 | 75 | #N/A | #N/A
2022-06-01 09:00 | 6 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 69 | 55 | 67 | 67 | 70 | 61 | 78 | 77 | #N/A | #N/A
2022-06-01 10:00 | 6 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 69 | 58 | 68 | 68 | 70 | 65 | 80 | 79 | #N/A | #N/A
2022-06-01 11:00 | 6 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 66 | 60 | 69 | 68 | 74 | 69 | 81 | 80 | #N/A | #N/A
2022-06-01 12:00 | 6 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 66 | 63 | 70 | 70 | 75 | 73 | 83 | 80 | #N/A | #N/A
2022-06-01 13:00 | 6 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 57 | 65 | 70 | 72 | 74 | 75 | 83 | 81 | #N/A | #N/A
2022-06-01 14:00 | 6 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 56 | 67 | 70 | 71 | 74 | 73 | 82 | 80 | #N/A | #N/A
2022-06-01 15:00 | 6 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 56 | 69 | 70 | 72 | 73 | 63 | 79 | 80 | #N/A | #N/A
2022-06-01 16:00 | 6 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 58 | 68 | 68 | 67 | 71 | 63 | 82 | 78 | #N/A | #N/A
2022-06-01 17:00 | 6 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 55 | 66 | 65 | 65 | 69 | 63 | 78 | 77 | #N/A | #N/A
2022-06-01 18:00 | 6 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 53 | 65 | 63 | 62 | 68 | 63 | 77 | 74 | #N/A | #N/A
2022-06-01 19:00 | 6 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 49 | 62 | 61 | 61 | 67 | 63 | 74 | 75 | #N/A | #N/A
2022-06-01 20:00 | 6 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 48 | 59 | 58 | 61 | 66 | 62 | 72 | 74 | #N/A | #N/A
2022-06-01 21:00 | 6 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 47 | 56 | 56 | 60 | 65 | 59 | 72 | 73 | #N/A | #N/A
2022-06-01 22:00 | 6 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 45 | 55 | 56 | 60 | 64 | 57 | 71 | 71 | #N/A | #N/A
2022-06-01 23:00 | 6 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 43 | 54 | 57 | 60 | 63 | 56 | 71 | 69 | #N/A | #N/A
2022-06-02 | 6 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 43 | 53 | 57 | 59 | 62 | 55 | 68 | 67 | #N/A | #N/A
2022-06-02 01:00 | 6 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 42 | 52 | 57 | 59 | 61 | 55 | 67 | 66 | #N/A | #N/A
2022-06-02 02:00 | 6 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 41 | 52 | 57 | 59 | 60 | 55 | 65 | 65 | #N/A | #N/A
2022-06-02 03:00 | 6 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 39 | 51 | 57 | 59 | 59 | 54 | 65 | 66 | #N/A | #N/A
2022-06-02 04:00 | 6 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 39 | 51 | 56 | 59 | 59 | 54 | 64 | 65 | #N/A | #N/A
2022-06-02 05:00 | 6 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 41 | 52 | 56 | 59 | 59 | 53 | 64 | 66 | #N/A | #N/A
2022-06-02 06:00 | 6 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 44 | 52 | 55 | 59 | 60 | 54 | 65 | 68 | #N/A | #N/A
2022-06-02 07:00 | 6 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 49 | 53 | 57 | 59 | 60 | 55 | 66 | 72 | #N/A | #N/A
2022-06-02 08:00 | 6 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 52 | 53 | 59 | 61 | 60 | 57 | 70 | 74 | #N/A | #N/A
2022-06-02 09:00 | 6 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 55 | 54 | 61 | 61 | 60 | 58 | 70 | 76 | #N/A | #N/A
2022-06-02 10:00 | 6 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 53 | 54 | 61 | 61 | 60 | 59 | 73 | 80 | #N/A | #N/A
2022-06-02 11:00 | 6 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 50 | 55 | 61 | 62 | 61 | 59 | 77 | 82 | #N/A | #N/A
2022-06-02 12:00 | 6 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 49 | 55 | 61 | 63 | 61 | 57 | 77 | 84 | #N/A | #N/A
2022-06-02 13:00 | 6 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 49 | 56 | 61 | 64 | 62 | 59 | 78 | 83 | #N/A | #N/A
2022-06-02 14:00 | 6 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 49 | 56 | 60 | 64 | 62 | 61 | 79 | 82 | #N/A | #N/A
2022-06-02 15:00 | 6 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 52 | 57 | 60 | 63 | 62 | 57 | 79 | 80 | #N/A | #N/A
2022-06-02 16:00 | 6 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 53 | 57 | 59 | 64 | 61 | 57 | 80 | 79 | #N/A | #N/A
2022-06-02 17:00 | 6 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 53 | 57 | 59 | 63 | 61 | 57 | 79 | 70 | #N/A | #N/A
2022-06-02 18:00 | 6 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 52 | 57 | 58 | 64 | 61 | 57 | 74 | 68 | #N/A | #N/A
2022-06-02 19:00 | 6 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 49 | 56 | 57 | 62 | 59 | 55 | 71 | 67 | #N/A | #N/A
2022-06-02 20:00 | 6 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 47 | 56 | 56 | 62 | 59 | 53 | 70 | 66 | #N/A | #N/A
2022-06-02 21:00 | 6 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 46 | 55 | 55 | 62 | 59 | 52 | 69 | 66 | #N/A | #N/A
2022-06-02 22:00 | 6 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 46 | 55 | 55 | 62 | 59 | 53 | 69 | 65 | #N/A | #N/A
2022-06-02 23:00 | 6 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 45 | 54 | 54 | 62 | 59 | 54 | 69 | 64 | #N/A | #N/A
2022-06-03 | 6 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 43 | 54 | 54 | 62 | 59 | 53 | 69 | 65 | #N/A | #N/A
2022-06-03 01:00 | 6 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 45 | 54 | 54 | 62 | 59 | 52 | 69 | 65 | #N/A | #N/A
2022-06-03 02:00 | 6 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 44 | 55 | 54 | 61 | 59 | 52 | 69 | 64 | #N/A | #N/A
2022-06-03 03:00 | 6 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 43 | 55 | 54 | 61 | 59 | 52 | 68 | 65 | #N/A | #N/A
2022-06-03 04:00 | 6 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 43 | 55 | 55 | 61 | 60 | 51 | 67 | 64 | #N/A | #N/A
2022-06-03 05:00 | 6 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 44 | 56 | 57 | 61 | 61 | 51 | 67 | 66 | #N/A | #N/A
2022-06-03 06:00 | 6 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 48 | 56 | 58 | 61 | 62 | 51 | 67 | 67 | #N/A | #N/A
2022-06-03 07:00 | 6 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 52 | 57 | 62 | 61 | 61 | 51 | 68 | 68 | #N/A | #N/A
2022-06-03 08:00 | 6 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 56 | 58 | 66 | 62 | 62 | 51 | 69 | 70 | #N/A | #N/A
2022-06-03 09:00 | 6 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 59 | 59 | 70 | 62 | 62 | 52 | 70 | 71 | #N/A | #N/A
2022-06-03 10:00 | 6 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 61 | 60 | 71 | 63 | 63 | 55 | 68 | 72 | #N/A | #N/A
2022-06-03 11:00 | 6 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 65 | 60 | 73 | 63 | 64 | 56 | 68 | 71 | #N/A | #N/A
2022-06-03 12:00 | 6 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 65 | 61 | 74 | 64 | 65 | 56 | 70 | 72 | #N/A | #N/A
2022-06-03 13:00 | 6 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 67 | 62 | 73 | 64 | 66 | 56 | 66 | 72 | #N/A | #N/A
2022-06-03 14:00 | 6 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 67 | 62 | 73 | 65 | 66 | 59 | 66 | 70 | #N/A | #N/A
2022-06-03 15:00 | 6 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 68 | 63 | 72 | 66 | 67 | 60 | 66 | 70 | #N/A | #N/A
2022-06-03 16:00 | 6 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 67 | 63 | 71 | 67 | 70 | 61 | 65 | 71 | #N/A | #N/A
2022-06-03 17:00 | 6 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 66 | 63 | 70 | 68 | 69 | 59 | 64 | 70 | #N/A | #N/A
2022-06-03 18:00 | 6 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 64 | 63 | 69 | 68 | 69 | 58 | 64 | 67 | #N/A | #N/A
2022-06-03 19:00 | 6 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 60 | 63 | 65 | 67 | 69 | 57 | 63 | 66 | #N/A | #N/A
2022-06-03 20:00 | 6 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 59 | 63 | 62 | 67 | 69 | 53 | 63 | 64 | #N/A | #N/A
2022-06-03 21:00 | 6 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 58 | 63 | 58 | 68 | 68 | 51 | 63 | 64 | #N/A | #N/A
2022-06-03 22:00 | 6 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 56 | 65 | 58 | 68 | 67 | 52 | 63 | 62 | #N/A | #N/A
2022-06-03 23:00 | 6 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 56 | 67 | 59 | 68 | 67 | 50 | 63 | 61 | #N/A | #N/A
2022-06-04 | 6 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 55 | 69 | 59 | 68 | 67 | 48 | 63 | 59 | #N/A | #N/A
2022-06-04 01:00 | 6 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 53 | 66 | 58 | 68 | 67 | 49 | 62 | 57 | #N/A | #N/A
2022-06-04 02:00 | 6 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 46 | 63 | 58 | 67 | 67 | 48 | 63 | 56 | #N/A | #N/A
2022-06-04 03:00 | 6 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 47 | 60 | 57 | 67 | 67 | 47 | 63 | 54 | #N/A | #N/A
2022-06-04 04:00 | 6 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 46 | 60 | 59 | 66 | 68 | 46 | 63 | 52 | #N/A | #N/A
2022-06-04 05:00 | 6 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 50 | 61 | 61 | 67 | 68 | 46 | 63 | 56 | #N/A | #N/A
2022-06-04 06:00 | 6 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 52 | 61 | 63 | 68 | 68 | 51 | 63 | 58 | #N/A | #N/A
2022-06-04 07:00 | 6 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 58 | 63 | 67 | 70 | 70 | 56 | 62 | 62 | #N/A | #N/A
2022-06-04 08:00 | 6 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 62 | 66 | 70 | 72 | 72 | 57 | 63 | 65 | #N/A | #N/A
2022-06-04 09:00 | 6 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 65 | 68 | 74 | 77 | 75 | 59 | 64 | 68 | #N/A | #N/A
2022-06-04 10:00 | 6 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 69 | 69 | 73 | 79 | 79 | 62 | 64 | 70 | #N/A | #N/A
2022-06-04 11:00 | 6 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 71 | 69 | 73 | 77 | 83 | 63 | 65 | 71 | #N/A | #N/A
2022-06-04 12:00 | 6 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 72 | 70 | 72 | 74 | 85 | 64 | 67 | 73 | #N/A | #N/A
2022-06-04 13:00 | 6 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 74 | 70 | 73 | 72 | 82 | 66 | 68 | 74 | #N/A | #N/A
2022-06-04 14:00 | 6 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 73 | 69 | 74 | 72 | 81 | 66 | 68 | 75 | #N/A | #N/A
2022-06-04 15:00 | 6 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 73 | 69 | 75 | 74 | 81 | 66 | 68 | 76 | #N/A | #N/A
2022-06-04 16:00 | 6 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 74 | 68 | 74 | 76 | 75 | 65 | 68 | 75 | #N/A | #N/A
2022-06-04 17:00 | 6 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 71 | 66 | 73 | 75 | 76 | 65 | 67 | 74 | #N/A | #N/A
2022-06-04 18:00 | 6 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 70 | 65 | 72 | 72 | 75 | 62 | 66 | 72 | #N/A | #N/A
2022-06-04 19:00 | 6 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 69 | 61 | 69 | 71 | 72 | 60 | 66 | 65 | #N/A | #N/A
2022-06-04 20:00 | 6 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 67 | 58 | 67 | 69 | 71 | 59 | 64 | 58 | #N/A | #N/A
2022-06-04 21:00 | 6 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 62 | 54 | 64 | 69 | 70 | 59 | 64 | 58 | #N/A | #N/A
2022-06-04 22:00 | 6 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 60 | 53 | 65 | 69 | 69 | 58 | 61 | 54 | #N/A | #N/A
2022-06-04 23:00 | 6 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 58 | 53 | 67 | 68 | 68 | 57 | 59 | 52 | #N/A | #N/A
2022-06-05 | 6 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 58 | 52 | 68 | 67 | 66 | 55 | 59 | 50 | #N/A | #N/A
2022-06-05 01:00 | 6 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 54 | 51 | 67 | 66 | 66 | 54 | 57 | 48 | #N/A | #N/A
2022-06-05 02:00 | 6 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 52 | 49 | 65 | 66 | 66 | 52 | 57 | 48 | #N/A | #N/A
2022-06-05 03:00 | 6 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 52 | 48 | 64 | 67 | 65 | 51 | 55 | 47 | #N/A | #N/A
2022-06-05 04:00 | 6 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 52 | 50 | 64 | 67 | 64 | 50 | 54 | 47 | #N/A | #N/A
2022-06-05 05:00 | 6 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 55 | 52 | 64 | 64 | 66 | 51 | 59 | 48 | #N/A | #N/A
2022-06-05 06:00 | 6 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 60 | 54 | 64 | 69 | 70 | 55 | 60 | 52 | #N/A | #N/A
2022-06-05 07:00 | 6 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 64 | 58 | 63 | 70 | 73 | 58 | 61 | 57 | #N/A | #N/A
2022-06-05 08:00 | 6 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 68 | 62 | 63 | 73 | 75 | 61 | 64 | 61 | #N/A | #N/A
2022-06-05 09:00 | 6 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 71 | 66 | 62 | 76 | 78 | 64 | 65 | 69 | #N/A | #N/A
2022-06-05 10:00 | 6 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 71 | 68 | 61 | 76 | 79 | 67 | 68 | 72 | #N/A | #N/A
2022-06-05 11:00 | 6 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 73 | 70 | 61 | 79 | 78 | 69 | 69 | 75 | #N/A | #N/A
2022-06-05 12:00 | 6 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 72 | 72 | 60 | 80 | 81 | 69 | 71 | 77 | #N/A | #N/A
2022-06-05 13:00 | 6 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 73 | 73 | 63 | 82 | 80 | 70 | 72 | 77 | #N/A | #N/A
2022-06-05 14:00 | 6 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 71 | 74 | 65 | 83 | 82 | 72 | 72 | 78 | #N/A | #N/A
2022-06-05 15:00 | 6 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 72 | 75 | 68 | 84 | 82 | 72 | 73 | 78 | #N/A | #N/A
2022-06-05 16:00 | 6 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 70 | 73 | 67 | 83 | 81 | 73 | 73 | 77 | #N/A | #N/A
2022-06-05 17:00 | 6 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 69 | 72 | 65 | 80 | 80 | 72 | 72 | 76 | #N/A | #N/A
2022-06-05 18:00 | 6 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 68 | 70 | 64 | 79 | 74 | 70 | 69 | 75 | #N/A | #N/A
2022-06-05 19:00 | 6 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 66 | 68 | 61 | 78 | 73 | 69 | 67 | 72 | #N/A | #N/A
2022-06-05 20:00 | 6 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 64 | 67 | 58 | 76 | 72 | 67 | 64 | 72 | #N/A | #N/A
2022-06-05 21:00 | 6 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 63 | 65 | 55 | 75 | 71 | 66 | 62 | 71 | #N/A | #N/A
2022-06-05 22:00 | 6 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 62 | 65 | 54 | 73 | 70 | 65 | 62 | 69 | #N/A | #N/A
2022-06-05 23:00 | 6 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 60 | 65 | 54 | 73 | 70 | 64 | 59 | 67 | #N/A | #N/A
2022-06-06 | 6 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 62 | 65 | 53 | 72 | 69 | 63 | 58 | 65 | #N/A | #N/A
2022-06-06 01:00 | 6 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 60 | 65 | 54 | 74 | 70 | 61 | 55 | 63 | #N/A | #N/A
2022-06-06 02:00 | 6 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 59 | 64 | 54 | 71 | 70 | 60 | 57 | 63 | #N/A | #N/A
2022-06-06 03:00 | 6 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 57 | 64 | 55 | 70 | 70 | 61 | 57 | 62 | #N/A | #N/A
2022-06-06 04:00 | 6 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 56 | 64 | 56 | 70 | 70 | 58 | 55 | 60 | #N/A | #N/A
2022-06-06 05:00 | 6 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 58 | 64 | 57 | 70 | 71 | 57 | 56 | 61 | #N/A | #N/A
2022-06-06 06:00 | 6 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 60 | 64 | 58 | 71 | 71 | 57 | 56 | 63 | #N/A | #N/A
2022-06-06 07:00 | 6 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 62 | 66 | 60 | 74 | 73 | 59 | 58 | 66 | #N/A | #N/A
2022-06-06 08:00 | 6 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 63 | 69 | 61 | 76 | 77 | 61 | 59 | 69 | #N/A | #N/A
2022-06-06 09:00 | 6 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 67 | 71 | 63 | 79 | 81 | 62 | 62 | 71 | #N/A | #N/A
2022-06-06 10:00 | 6 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 70 | 72 | 66 | 80 | 81 | 64 | 64 | 74 | #N/A | #N/A
2022-06-06 11:00 | 6 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 66 | 72 | 68 | 80 | 82 | 65 | 67 | 78 | #N/A | #N/A
2022-06-06 12:00 | 6 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 66 | 73 | 71 | 81 | 82 | 65 | 67 | 81 | #N/A | #N/A
2022-06-06 13:00 | 6 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 71 | 72 | 71 | 81 | 83 | 64 | 67 | 83 | #N/A | #N/A
2022-06-06 14:00 | 6 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 73 | 72 | 70 | 81 | 82 | 65 | 68 | 85 | #N/A | #N/A
2022-06-06 15:00 | 6 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 72 | 71 | 70 | 80 | 81 | 64 | 68 | 85 | #N/A | #N/A
2022-06-06 16:00 | 6 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 75 | 69 | 69 | 79 | 79 | 64 | 67 | 85 | #N/A | #N/A
2022-06-06 17:00 | 6 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 72 | 68 | 67 | 78 | 78 | 63 | 66 | 83 | #N/A | #N/A
2022-06-06 18:00 | 6 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 71 | 66 | 66 | 76 | 77 | 63 | 65 | 82 | #N/A | #N/A
2022-06-06 19:00 | 6 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 69 | 62 | 65 | 74 | 76 | 63 | 59 | 81 | #N/A | #N/A
2022-06-06 20:00 | 6 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 68 | 59 | 63 | 73 | 75 | 63 | 57 | 78 | #N/A | #N/A
2022-06-06 21:00 | 6 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 68 | 55 | 62 | 74 | 74 | 62 | 56 | 76 | #N/A | #N/A
2022-06-06 22:00 | 6 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 66 | 54 | 63 | 71 | 73 | 61 | 55 | 72 | #N/A | #N/A
2022-06-06 23:00 | 6 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 66 | 54 | 64 | 73 | 72 | 60 | 55 | 69 | #N/A | #N/A
2022-06-07 | 6 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 66 | 53 | 65 | 68 | 72 | 60 | 55 | 67 | #N/A | #N/A
2022-06-07 01:00 | 6 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 65 | 51 | 65 | 65 | 72 | 59 | 55 | 66 | #N/A | #N/A
2022-06-07 02:00 | 6 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 65 | 49 | 65 | 63 | 69 | 59 | 56 | 65 | #N/A | #N/A
2022-06-07 03:00 | 6 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 65 | 47 | 65 | 63 | 64 | 59 | 54 | 64 | #N/A | #N/A
2022-06-07 04:00 | 6 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 63 | 48 | 66 | 62 | 61 | 58 | 54 | 64 | #N/A | #N/A
2022-06-07 05:00 | 6 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 62 | 50 | 67 | 65 | 67 | 59 | 52 | 66 | #N/A | #N/A
2022-06-07 06:00 | 6 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 60 | 51 | 68 | 69 | 70 | 61 | 53 | 69 | #N/A | #N/A
2022-06-07 07:00 | 6 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 60 | 53 | 70 | 71 | 72 | 61 | 53 | 75 | #N/A | #N/A
2022-06-07 08:00 | 6 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 61 | 55 | 73 | 72 | 74 | 64 | 52 | 79 | #N/A | #N/A
2022-06-07 09:00 | 6 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 60 | 57 | 75 | 74 | 75 | 65 | 54 | 84 | #N/A | #N/A
2022-06-07 10:00 | 6 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 61 | 59 | 77 | 75 | 76 | 66 | 59 | 87 | #N/A | #N/A
2022-06-07 11:00 | 6 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 63 | 61 | 80 | 77 | 76 | 68 | 64 | 92 | #N/A | #N/A
2022-06-07 12:00 | 6 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 65 | 63 | 82 | 78 | 77 | 68 | 67 | 92 | #N/A | #N/A
2022-06-07 13:00 | 6 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 68 | 64 | 82 | 79 | 78 | 68 | 69 | 93 | #N/A | #N/A
2022-06-07 14:00 | 6 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 70 | 64 | 82 | 80 | 78 | 69 | 71 | 89 | #N/A | #N/A
2022-06-07 15:00 | 6 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 71 | 65 | 82 | 80 | 80 | 69 | 73 | 88 | #N/A | #N/A
2022-06-07 16:00 | 6 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 71 | 64 | 80 | 80 | 79 | 68 | 73 | 87 | #N/A | #N/A
2022-06-07 17:00 | 6 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 71 | 62 | 78 | 79 | 78 | 70 | 73 | 86 | #N/A | #N/A
2022-06-07 18:00 | 6 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 69 | 61 | 76 | 77 | 76 | 67 | 72 | 82 | #N/A | #N/A
2022-06-07 19:00 | 6 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 67 | 56 | 75 | 72 | 72 | 65 | 71 | 78 | #N/A | #N/A
2022-06-07 20:00 | 6 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 67 | 52 | 73 | 69 | 71 | 64 | 71 | 75 | #N/A | #N/A
2022-06-07 21:00 | 6 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 66 | 47 | 72 | 66 | 68 | 64 | 70 | 73 | #N/A | #N/A
2022-06-07 22:00 | 6 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 62 | 46 | 72 | 65 | 66 | 61 | 68 | 71 | #N/A | #N/A
2022-06-07 23:00 | 6 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 61 | 45 | 73 | 65 | 63 | 61 | 66 | 69 | #N/A | #N/A
2022-06-08 | 6 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 59 | 44 | 73 | 61 | 60 | 61 | 65 | 68 | #N/A | #N/A
2022-06-08 01:00 | 6 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 58 | 43 | 71 | 58 | 58 | 60 | 66 | 68 | #N/A | #N/A
2022-06-08 02:00 | 6 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 58 | 43 | 69 | 55 | 58 | 57 | 68 | 67 | #N/A | #N/A
2022-06-08 03:00 | 6 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 55 | 42 | 67 | 55 | 60 | 57 | 67 | 65 | #N/A | #N/A
2022-06-08 04:00 | 6 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 53 | 45 | 68 | 54 | 57 | 54 | 67 | 65 | #N/A | #N/A
2022-06-08 05:00 | 6 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 51 | 47 | 68 | 58 | 59 | 52 | 67 | 68 | #N/A | #N/A
2022-06-08 06:00 | 6 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 51 | 50 | 69 | 62 | 65 | 59 | 70 | 73 | #N/A | #N/A
2022-06-08 07:00 | 6 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 50 | 56 | 70 | 66 | 69 | 63 | 73 | 79 | #N/A | #N/A
2022-06-08 08:00 | 6 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 51 | 61 | 72 | 70 | 71 | 66 | 76 | 82 | #N/A | #N/A
2022-06-08 09:00 | 6 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 54 | 67 | 73 | 73 | 73 | 69 | 78 | 86 | #N/A | #N/A
2022-06-08 10:00 | 6 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 55 | 67 | 74 | 72 | 76 | 71 | 79 | 88 | #N/A | #N/A
2022-06-08 11:00 | 6 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 60 | 68 | 75 | 79 | 78 | 72 | 79 | 89 | #N/A | #N/A
2022-06-08 12:00 | 6 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 63 | 68 | 76 | 82 | 81 | 73 | 79 | 90 | #N/A | #N/A
2022-06-08 13:00 | 6 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 63 | 69 | 75 | 81 | 82 | 74 | 79 | 91 | #N/A | #N/A
2022-06-08 14:00 | 6 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 63 | 70 | 74 | 82 | 82 | 73 | 80 | 92 | #N/A | #N/A
2022-06-08 15:00 | 6 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 63 | 71 | 73 | 81 | 82 | 75 | 79 | 92 | #N/A | #N/A
2022-06-08 16:00 | 6 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 63 | 69 | 72 | 81 | 80 | 75 | 77 | 90 | #N/A | #N/A
2022-06-08 17:00 | 6 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 60 | 66 | 72 | 80 | 79 | 74 | 71 | 89 | #N/A | #N/A
2022-06-08 18:00 | 6 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 57 | 64 | 71 | 78 | 77 | 72 | 71 | 86 | #N/A | #N/A
2022-06-08 19:00 | 6 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 53 | 63 | 69 | 77 | 73 | 69 | 69 | 80 | #N/A | #N/A
2022-06-08 20:00 | 6 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 51 | 63 | 68 | 77 | 72 | 66 | 68 | 75 | #N/A | #N/A
2022-06-08 21:00 | 6 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 50 | 62 | 66 | 76 | 72 | 65 | 66 | 73 | #N/A | #N/A
2022-06-08 22:00 | 6 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 49 | 62 | 65 | 76 | 72 | 64 | 66 | 70 | #N/A | #N/A
2022-06-08 23:00 | 6 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 49 | 63 | 65 | 76 | 72 | 61 | 66 | 67 | #N/A | #N/A
2022-06-09 | 6 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 49 | 63 | 64 | 75 | 72 | 56 | 65 | 65 | #N/A | #N/A
2022-06-09 01:00 | 6 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 48 | 62 | 65 | 74 | 72 | 53 | 65 | 64 | #N/A | #N/A
2022-06-09 02:00 | 6 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 45 | 62 | 65 | 73 | 72 | 51 | 64 | 62 | #N/A | #N/A
2022-06-09 03:00 | 6 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 47 | 61 | 66 | 70 | 73 | 51 | 63 | 61 | #N/A | #N/A
2022-06-09 04:00 | 6 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 44 | 60 | 67 | 70 | 73 | 50 | 63 | 61 | #N/A | #N/A
2022-06-09 05:00 | 6 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 43 | 59 | 67 | 70 | 73 | 52 | 63 | 64 | #N/A | #N/A
2022-06-09 06:00 | 6 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 46 | 58 | 68 | 71 | 73 | 59 | 64 | 69 | #N/A | #N/A
2022-06-09 07:00 | 6 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 52 | 59 | 71 | 71 | 74 | 63 | 66 | 73 | #N/A | #N/A
2022-06-09 08:00 | 6 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 54 | 57 | 60 | 74 | 72 | 74 | 66 | 69 | 76 | #N/A | #N/A
2022-06-09 09:00 | 6 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 61 | 61 | 77 | 75 | 76 | 70 | 70 | 80 | #N/A | #N/A
2022-06-09 10:00 | 6 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 64 | 62 | 78 | 76 | 80 | 72 | 72 | 83 | #N/A | #N/A
2022-06-09 11:00 | 6 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 67 | 64 | 79 | 81 | 83 | 74 | 68 | 84 | #N/A | #N/A
2022-06-09 12:00 | 6 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 70 | 65 | 80 | 82 | 86 | 75 | 69 | 86 | #N/A | #N/A
2022-06-09 13:00 | 6 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 72 | 65 | 78 | 82 | 86 | 73 | 72 | 88 | #N/A | #N/A
2022-06-09 14:00 | 6 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 73 | 64 | 75 | 82 | 86 | 75 | 75 | 90 | #N/A | #N/A
2022-06-09 15:00 | 6 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 58 | 74 | 64 | 73 | 82 | 85 | 74 | 72 | 89 | #N/A | #N/A
2022-06-09 16:00 | 6 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 73 | 63 | 74 | 81 | 84 | 74 | 70 | 88 | #N/A | #N/A
2022-06-09 17:00 | 6 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 72 | 62 | 75 | 80 | 82 | 72 | 67 | 86 | #N/A | #N/A
2022-06-09 18:00 | 6 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 70 | 61 | 76 | 78 | 79 | 71 | 64 | 84 | #N/A | #N/A
2022-06-09 19:00 | 6 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 67 | 59 | 75 | 74 | 75 | 68 | 62 | 77 | #N/A | #N/A
2022-06-09 20:00 | 6 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 65 | 56 | 74 | 71 | 76 | 65 | 59 | 74 | #N/A | #N/A
2022-06-09 21:00 | 6 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 63 | 54 | 73 | 68 | 73 | 63 | 57 | 70 | #N/A | #N/A
2022-06-09 22:00 | 6 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 62 | 54 | 72 | 67 | 71 | 62 | 55 | 69 | #N/A | #N/A
2022-06-09 23:00 | 6 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 61 | 54 | 71 | 67 | 67 | 60 | 53 | 66 | #N/A | #N/A
2022-06-10 | 6 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 58 | 54 | 70 | 66 | 67 | 58 | 52 | 65 | #N/A | #N/A
2022-06-10 01:00 | 6 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 57 | 53 | 70 | 65 | 67 | 57 | 52 | 65 | #N/A | #N/A
2022-06-10 02:00 | 6 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 55 | 52 | 71 | 65 | 65 | 56 | 51 | 67 | #N/A | #N/A
2022-06-10 03:00 | 6 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 53 | 51 | 71 | 66 | 65 | 56 | 51 | 66 | #N/A | #N/A
2022-06-10 04:00 | 6 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 51 | 52 | 72 | 63 | 66 | 57 | 51 | 66 | #N/A | #N/A
2022-06-10 05:00 | 6 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 53 | 52 | 72 | 64 | 65 | 57 | 50 | 65 | #N/A | #N/A
2022-06-10 06:00 | 6 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 59 | 53 | 73 | 66 | 65 | 61 | 50 | 65 | #N/A | #N/A
2022-06-10 07:00 | 6 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 52 | 64 | 55 | 75 | 66 | 67 | 66 | 54 | 65 | #N/A | #N/A
2022-06-10 08:00 | 6 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 54 | 67 | 56 | 77 | 67 | 67 | 70 | 58 | 65 | #N/A | #N/A
2022-06-10 09:00 | 6 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 70 | 58 | 79 | 67 | 68 | 73 | 62 | 64 | #N/A | #N/A
2022-06-10 10:00 | 6 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 58 | 72 | 59 | 81 | 68 | 68 | 76 | 63 | 65 | #N/A | #N/A
2022-06-10 11:00 | 6 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 74 | 59 | 82 | 68 | 68 | 77 | 66 | 66 | #N/A | #N/A
2022-06-10 12:00 | 6 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 72 | 60 | 84 | 68 | 68 | 77 | 66 | 65 | #N/A | #N/A
2022-06-10 13:00 | 6 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 58 | 75 | 61 | 81 | 68 | 68 | 77 | 68 | 65 | #N/A | #N/A
2022-06-10 14:00 | 6 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 75 | 63 | 77 | 68 | 68 | 78 | 69 | 66 | #N/A | #N/A
2022-06-10 15:00 | 6 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 75 | 64 | 74 | 69 | 67 | 76 | 67 | 67 | #N/A | #N/A
2022-06-10 16:00 | 6 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 75 | 63 | 72 | 70 | 67 | 78 | 68 | 67 | #N/A | #N/A
2022-06-10 17:00 | 6 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 73 | 63 | 70 | 72 | 68 | 77 | 67 | 67 | #N/A | #N/A
2022-06-10 18:00 | 6 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 69 | 62 | 68 | 72 | 68 | 76 | 65 | 67 | #N/A | #N/A
2022-06-10 19:00 | 6 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 65 | 60 | 65 | 69 | 66 | 73 | 61 | 66 | #N/A | #N/A
2022-06-10 20:00 | 6 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 62 | 58 | 63 | 67 | 67 | 72 | 57 | 66 | #N/A | #N/A
2022-06-10 21:00 | 6 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 62 | 56 | 60 | 66 | 67 | 68 | 54 | 66 | #N/A | #N/A
2022-06-10 22:00 | 6 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 61 | 54 | 59 | 66 | 66 | 66 | 53 | 66 | #N/A | #N/A
2022-06-10 23:00 | 6 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 59 | 53 | 58 | 64 | 65 | 65 | 50 | 65 | #N/A | #N/A
2022-06-11 | 6 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 58 | 51 | 57 | 64 | 65 | 64 | 49 | 64 | #N/A | #N/A
2022-06-11 01:00 | 6 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 58 | 49 | 56 | 63 | 64 | 63 | 46 | 65 | #N/A | #N/A
2022-06-11 02:00 | 6 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 44 | 55 | 46 | 56 | 65 | 64 | 62 | 45 | 65 | #N/A | #N/A
2022-06-11 03:00 | 6 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 43 | 54 | 44 | 55 | 64 | 61 | 61 | 43 | 64 | #N/A | #N/A
2022-06-11 04:00 | 6 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 53 | 46 | 55 | 65 | 60 | 60 | 43 | 63 | #N/A | #N/A
2022-06-11 05:00 | 6 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 43 | 56 | 48 | 55 | 66 | 64 | 61 | 45 | 62 | #N/A | #N/A
2022-06-11 06:00 | 6 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 59 | 50 | 55 | 67 | 67 | 64 | 52 | 63 | #N/A | #N/A
2022-06-11 07:00 | 6 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 64 | 54 | 55 | 69 | 70 | 64 | 56 | 64 | #N/A | #N/A
2022-06-11 08:00 | 6 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 65 | 58 | 55 | 71 | 71 | 62 | 61 | 65 | #N/A | #N/A
2022-06-11 09:00 | 6 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 66 | 62 | 55 | 72 | 73 | 65 | 65 | 67 | #N/A | #N/A
2022-06-11 10:00 | 6 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 64 | 63 | 56 | 74 | 74 | 74 | 69 | 69 | #N/A | #N/A
2022-06-11 11:00 | 6 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 57 | 64 | 57 | 75 | 76 | 76 | 70 | 71 | #N/A | #N/A
2022-06-11 12:00 | 6 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 58 | 65 | 58 | 78 | 77 | 77 | 71 | 74 | #N/A | #N/A
2022-06-11 13:00 | 6 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 58 | 65 | 59 | 78 | 78 | 80 | 73 | 77 | #N/A | #N/A
2022-06-11 14:00 | 6 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 63 | 66 | 59 | 79 | 80 | 80 | 72 | 79 | #N/A | #N/A
2022-06-11 15:00 | 6 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 63 | 66 | 60 | 80 | 79 | 79 | 74 | 81 | #N/A | #N/A
2022-06-11 16:00 | 6 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 62 | 64 | 59 | 79 | 79 | 80 | 73 | 80 | #N/A | #N/A
2022-06-11 17:00 | 6 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 61 | 63 | 57 | 78 | 77 | 78 | 72 | 79 | #N/A | #N/A
2022-06-11 18:00 | 6 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 60 | 61 | 56 | 76 | 74 | 78 | 71 | 76 | #N/A | #N/A
2022-06-11 19:00 | 6 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 60 | 59 | 55 | 70 | 69 | 75 | 67 | 69 | #N/A | #N/A
2022-06-11 20:00 | 6 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 58 | 57 | 55 | 69 | 69 | 73 | 68 | 64 | #N/A | #N/A
2022-06-11 21:00 | 6 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 57 | 55 | 54 | 69 | 67 | 70 | 67 | 63 | #N/A | #N/A
2022-06-11 22:00 | 6 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 57 | 54 | 53 | 69 | 68 | 68 | 66 | 59 | #N/A | #N/A
2022-06-11 23:00 | 6 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 57 | 54 | 51 | 68 | 67 | 67 | 66 | 56 | #N/A | #N/A
2022-06-12 | 6 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 57 | 53 | 50 | 67 | 67 | 66 | 64 | 56 | #N/A | #N/A
2022-06-12 01:00 | 6 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 57 | 52 | 49 | 67 | 68 | 65 | 66 | 55 | #N/A | #N/A
2022-06-12 02:00 | 6 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 56 | 51 | 47 | 67 | 68 | 62 | 65 | 54 | #N/A | #N/A
2022-06-12 03:00 | 6 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 55 | 50 | 46 | 66 | 65 | 62 | 65 | 51 | #N/A | #N/A
2022-06-12 04:00 | 6 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 55 | 53 | 48 | 66 | 65 | 61 | 64 | 50 | #N/A | #N/A
2022-06-12 05:00 | 6 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 57 | 55 | 51 | 67 | 68 | 63 | 65 | 53 | #N/A | #N/A
2022-06-12 06:00 | 6 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 60 | 58 | 53 | 70 | 70 | 65 | 63 | 57 | #N/A | #N/A
2022-06-12 07:00 | 6 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 63 | 61 | 54 | 73 | 74 | 69 | 61 | 63 | #N/A | #N/A
2022-06-12 08:00 | 6 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 64 | 63 | 55 | 74 | 76 | 74 | 61 | 68 | #N/A | #N/A
2022-06-12 09:00 | 6 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 67 | 66 | 56 | 78 | 78 | 77 | 62 | 72 | #N/A | #N/A
2022-06-12 10:00 | 6 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 70 | 67 | 57 | 80 | 80 | 78 | 64 | 76 | #N/A | #N/A
2022-06-12 11:00 | 6 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 73 | 69 | 57 | 80 | 82 | 80 | 64 | 79 | #N/A | #N/A
2022-06-12 12:00 | 6 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 76 | 70 | 58 | 80 | 84 | 83 | 65 | 81 | #N/A | #N/A
2022-06-12 13:00 | 6 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 75 | 69 | 59 | 81 | 84 | 84 | 65 | 82 | #N/A | #N/A
2022-06-12 14:00 | 6 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 70 | 68 | 59 | 82 | 82 | 86 | 67 | 84 | #N/A | #N/A
2022-06-12 15:00 | 6 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 72 | 67 | 60 | 82 | 82 | 85 | 68 | 85 | #N/A | #N/A
2022-06-12 16:00 | 6 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 73 | 66 | 59 | 81 | 81 | 85 | 68 | 84 | #N/A | #N/A
2022-06-12 17:00 | 6 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 70 | 66 | 58 | 80 | 79 | 83 | 70 | 82 | #N/A | #N/A
2022-06-12 18:00 | 6 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 69 | 65 | 57 | 78 | 76 | 81 | 71 | 79 | #N/A | #N/A
2022-06-12 19:00 | 6 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 68 | 63 | 56 | 76 | 75 | 79 | 70 | 76 | #N/A | #N/A
2022-06-12 20:00 | 6 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 67 | 62 | 55 | 76 | 74 | 77 | 70 | 75 | #N/A | #N/A
2022-06-12 21:00 | 6 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 67 | 60 | 54 | 74 | 72 | 76 | 69 | 74 | #N/A | #N/A
2022-06-12 22:00 | 6 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 66 | 59 | 51 | 72 | 71 | 71 | 69 | 72 | #N/A | #N/A
2022-06-12 23:00 | 6 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 64 | 57 | 49 | 70 | 70 | 73 | 68 | 71 | #N/A | #N/A
2022-06-13 | 6 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 63 | 56 | 46 | 68 | 70 | 68 | 67 | 68 | #N/A | #N/A
2022-06-13 01:00 | 6 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 64 | 55 | 45 | 67 | 67 | 68 | 67 | 69 | #N/A | #N/A
2022-06-13 02:00 | 6 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 63 | 54 | 43 | 67 | 69 | 68 | 66 | 67 | #N/A | #N/A
2022-06-13 03:00 | 6 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 63 | 53 | 42 | 68 | 69 | 67 | 67 | 68 | #N/A | #N/A
2022-06-13 04:00 | 6 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 63 | 55 | 45 | 67 | 68 | 66 | 68 | 68 | #N/A | #N/A
2022-06-13 05:00 | 6 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 64 | 57 | 48 | 68 | 68 | 67 | 67 | 68 | #N/A | #N/A
2022-06-13 06:00 | 6 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 67 | 59 | 51 | 68 | 71 | 71 | 70 | 69 | #N/A | #N/A
2022-06-13 07:00 | 6 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 58 | 70 | 62 | 54 | 71 | 73 | 74 | 70 | 71 | #N/A | #N/A
2022-06-13 08:00 | 6 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 73 | 64 | 58 | 71 | 76 | 78 | 72 | 73 | #N/A | #N/A
2022-06-13 09:00 | 6 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 76 | 67 | 61 | 75 | 79 | 80 | 73 | 74 | #N/A | #N/A
2022-06-13 10:00 | 6 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 78 | 69 | 62 | 77 | 81 | 82 | 75 | 74 | #N/A | #N/A
2022-06-13 11:00 | 6 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 78 | 70 | 63 | 80 | 82 | 83 | 75 | 77 | #N/A | #N/A
2022-06-13 12:00 | 6 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 80 | 72 | 64 | 82 | 83 | 84 | 79 | 79 | #N/A | #N/A
2022-06-13 13:00 | 6 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 79 | 72 | 65 | 80 | 84 | 85 | 82 | 78 | #N/A | #N/A
2022-06-13 14:00 | 6 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 79 | 71 | 66 | 83 | 82 | 87 | 83 | 81 | #N/A | #N/A
2022-06-13 15:00 | 6 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 64 | 71 | 67 | 82 | 82 | 87 | 76 | 82 | #N/A | #N/A
2022-06-13 16:00 | 6 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 66 | 69 | 66 | 81 | 79 | 88 | 64 | 71 | #N/A | #N/A
2022-06-13 17:00 | 6 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 67 | 66 | 66 | 79 | 78 | 88 | 63 | 71 | #N/A | #N/A
2022-06-13 18:00 | 6 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 66 | 64 | 65 | 78 | 74 | 85 | 63 | 71 | #N/A | #N/A
2022-06-13 19:00 | 6 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 67 | 64 | 60 | 75 | 72 | 80 | 63 | 71 | #N/A | #N/A
2022-06-13 20:00 | 6 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 63 | 55 | 74 | 70 | 76 | 62 | 67 | #N/A | #N/A
2022-06-13 21:00 | 6 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 62 | 63 | 50 | 71 | 69 | 76 | 61 | 66 | #N/A | #N/A
2022-06-13 22:00 | 6 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 63 | 64 | 49 | 69 | 69 | 72 | 61 | 67 | #N/A | #N/A
2022-06-13 23:00 | 6 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 62 | 65 | 47 | 67 | 67 | 71 | 58 | 67 | #N/A | #N/A
2022-06-14 | 6 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 62 | 66 | 46 | 68 | 66 | 72 | 58 | 66 | #N/A | #N/A
2022-06-14 01:00 | 6 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 61 | 65 | 47 | 67 | 64 | 69 | 56 | 66 | #N/A | #N/A
2022-06-14 02:00 | 6 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 62 | 65 | 48 | 67 | 63 | 67 | 56 | 65 | #N/A | #N/A
2022-06-14 03:00 | 6 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 62 | 64 | 49 | 67 | 62 | 67 | 56 | 66 | #N/A | #N/A
2022-06-14 04:00 | 6 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 62 | 64 | 51 | 66 | 62 | 67 | 55 | 66 | #N/A | #N/A
2022-06-14 05:00 | 6 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 61 | 65 | 53 | 67 | 62 | 68 | 56 | 66 | #N/A | #N/A
2022-06-14 06:00 | 6 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 63 | 65 | 55 | 65 | 62 | 71 | 59 | 68 | #N/A | #N/A
2022-06-14 07:00 | 6 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 66 | 65 | 60 | 66 | 63 | 74 | 62 | 70 | #N/A | #N/A
2022-06-14 08:00 | 6 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 70 | 66 | 64 | 67 | 64 | 78 | 67 | 73 | #N/A | #N/A
2022-06-14 09:00 | 6 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 74 | 66 | 69 | 68 | 65 | 81 | 68 | 73 | #N/A | #N/A
2022-06-14 10:00 | 6 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 77 | 68 | 71 | 68 | 65 | 83 | 74 | 75 | #N/A | #N/A
2022-06-14 11:00 | 6 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 80 | 70 | 74 | 69 | 66 | 85 | 78 | 76 | #N/A | #N/A
2022-06-14 12:00 | 6 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 82 | 72 | 76 | 71 | 67 | 86 | 81 | 77 | #N/A | #N/A
2022-06-14 13:00 | 6 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 84 | 70 | 76 | 70 | 67 | 87 | 83 | 77 | #N/A | #N/A
2022-06-14 14:00 | 6 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 84 | 68 | 77 | 70 | 66 | 87 | 84 | 76 | #N/A | #N/A
2022-06-14 15:00 | 6 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 85 | 66 | 77 | 71 | 65 | 88 | 83 | 75 | #N/A | #N/A
2022-06-14 16:00 | 6 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 84 | 67 | 76 | 71 | 64 | 87 | 83 | 74 | #N/A | #N/A
2022-06-14 17:00 | 6 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 82 | 68 | 75 | 70 | 64 | 86 | 83 | 73 | #N/A | #N/A
2022-06-14 18:00 | 6 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 78 | 69 | 74 | 69 | 63 | 85 | 81 | 72 | #N/A | #N/A
2022-06-14 19:00 | 6 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 75 | 69 | 72 | 68 | 63 | 83 | 78 | 71 | #N/A | #N/A
2022-06-14 20:00 | 6 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 72 | 69 | 69 | 67 | 63 | 81 | 76 | 70 | #N/A | #N/A
2022-06-14 21:00 | 6 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 71 | 69 | 67 | 67 | 62 | 79 | 75 | 69 | #N/A | #N/A
2022-06-14 22:00 | 6 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 71 | 70 | 68 | 67 | 62 | 78 | 76 | 66 | #N/A | #N/A
2022-06-14 23:00 | 6 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 70 | 70 | 68 | 66 | 62 | 77 | 75 | 63 | #N/A | #N/A
2022-06-15 | 6 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 69 | 71 | 69 | 66 | 62 | 75 | 72 | 61 | #N/A | #N/A
2022-06-15 01:00 | 6 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 68 | 71 | 68 | 66 | 63 | 74 | 74 | 59 | #N/A | #N/A
2022-06-15 02:00 | 6 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 68 | 71 | 67 | 66 | 63 | 73 | 70 | 58 | #N/A | #N/A
2022-06-15 03:00 | 6 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 68 | 71 | 66 | 66 | 63 | 71 | 69 | 57 | #N/A | #N/A
2022-06-15 04:00 | 6 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 68 | 71 | 67 | 66 | 63 | 72 | 70 | 57 | #N/A | #N/A
2022-06-15 05:00 | 6 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 65 | 71 | 69 | 66 | 63 | 72 | 72 | 59 | #N/A | #N/A
2022-06-15 06:00 | 6 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 67 | 71 | 70 | 66 | 64 | 73 | 73 | 61 | #N/A | #N/A
2022-06-15 07:00 | 6 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 70 | 72 | 73 | 66 | 66 | 75 | 76 | 63 | #N/A | #N/A
2022-06-15 08:00 | 6 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 76 | 72 | 75 | 69 | 67 | 77 | 79 | 67 | #N/A | #N/A
2022-06-15 09:00 | 6 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 80 | 73 | 78 | 70 | 69 | 80 | 81 | 69 | #N/A | #N/A
2022-06-15 10:00 | 6 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 83 | 76 | 79 | 76 | 71 | 82 | 82 | 71 | #N/A | #N/A
2022-06-15 11:00 | 6 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 83 | 78 | 79 | 81 | 74 | 84 | 84 | 71 | #N/A | #N/A
2022-06-15 12:00 | 6 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 85 | 81 | 80 | 85 | 78 | 84 | 86 | 74 | #N/A | #N/A
2022-06-15 13:00 | 6 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 86 | 82 | 79 | 90 | 80 | 85 | 87 | 74 | #N/A | #N/A
2022-06-15 14:00 | 6 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 87 | 82 | 78 | 92 | 82 | 86 | 87 | 73 | #N/A | #N/A
2022-06-15 15:00 | 6 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 86 | 83 | 77 | 91 | 83 | 86 | 86 | 75 | #N/A | #N/A
2022-06-15 16:00 | 6 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 86 | 81 | 77 | 89 | 83 | 86 | 83 | 73 | #N/A | #N/A
2022-06-15 17:00 | 6 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 84 | 80 | 76 | 89 | 83 | 85 | 81 | 73 | #N/A | #N/A
2022-06-15 18:00 | 6 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 82 | 78 | 76 | 87 | 82 | 84 | 79 | 69 | #N/A | #N/A
2022-06-15 19:00 | 6 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 79 | 76 | 75 | 84 | 78 | 82 | 75 | 65 | #N/A | #N/A
2022-06-15 20:00 | 6 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 77 | 74 | 73 | 80 | 78 | 79 | 72 | 60 | #N/A | #N/A
2022-06-15 21:00 | 6 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 75 | 72 | 72 | 78 | 76 | 77 | 68 | 61 | #N/A | #N/A
2022-06-15 22:00 | 6 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 75 | 72 | 71 | 78 | 75 | 76 | 68 | 58 | #N/A | #N/A
2022-06-15 23:00 | 6 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 73 | 71 | 70 | 75 | 73 | 75 | 63 | 57 | #N/A | #N/A
2022-06-16 | 6 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 73 | 71 | 69 | 75 | 72 | 74 | 63 | 56 | #N/A | #N/A
2022-06-16 01:00 | 6 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 70 | 71 | 69 | 74 | 71 | 73 | 60 | 54 | #N/A | #N/A
2022-06-16 02:00 | 6 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 69 | 70 | 68 | 75 | 71 | 70 | 59 | 50 | #N/A | #N/A
2022-06-16 03:00 | 6 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 69 | 70 | 68 | 74 | 71 | 72 | 58 | 48 | #N/A | #N/A
2022-06-16 04:00 | 6 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 68 | 70 | 69 | 72 | 71 | 69 | 56 | 47 | #N/A | #N/A
2022-06-16 05:00 | 6 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 70 | 70 | 69 | 74 | 72 | 72 | 58 | 50 | #N/A | #N/A
2022-06-16 06:00 | 6 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 73 | 70 | 70 | 78 | 72 | 72 | 62 | 53 | #N/A | #N/A
2022-06-16 07:00 | 6 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 74 | 72 | 72 | 82 | 74 | 72 | 66 | 56 | #N/A | #N/A
2022-06-16 08:00 | 6 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 80 | 74 | 74 | 84 | 79 | 66 | 72 | 59 | #N/A | #N/A
2022-06-16 09:00 | 6 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 85 | 76 | 76 | 88 | 85 | 67 | 75 | 61 | #N/A | #N/A
2022-06-16 10:00 | 6 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 84 | 78 | 77 | 89 | 88 | 66 | 78 | 65 | #N/A | #N/A
2022-06-16 11:00 | 6 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 86 | 79 | 77 | 91 | 90 | 67 | 81 | 68 | #N/A | #N/A
2022-06-16 12:00 | 6 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 87 | 81 | 78 | 93 | 92 | 67 | 82 | 69 | #N/A | #N/A
2022-06-16 13:00 | 6 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 89 | 80 | 78 | 93 | 92 | 69 | 83 | 71 | #N/A | #N/A
2022-06-16 14:00 | 6 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 89 | 78 | 78 | 94 | 92 | 72 | 83 | 70 | #N/A | #N/A
2022-06-16 15:00 | 6 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 88 | 77 | 78 | 94 | 91 | 74 | 83 | 69 | #N/A | #N/A
2022-06-16 16:00 | 6 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 87 | 73 | 76 | 91 | 91 | 77 | 83 | 69 | #N/A | #N/A
2022-06-16 17:00 | 6 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 83 | 70 | 75 | 89 | 88 | 77 | 82 | 68 | #N/A | #N/A
2022-06-16 18:00 | 6 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 83 | 66 | 73 | 88 | 84 | 75 | 80 | 67 | #N/A | #N/A
2022-06-16 19:00 | 6 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 79 | 66 | 70 | 85 | 82 | 72 | 76 | 65 | #N/A | #N/A
2022-06-16 20:00 | 6 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 77 | 66 | 68 | 84 | 81 | 69 | 73 | 63 | #N/A | #N/A
2022-06-16 21:00 | 6 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 75 | 66 | 65 | 83 | 79 | 64 | 69 | 63 | #N/A | #N/A
2022-06-16 22:00 | 6 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 73 | 64 | 64 | 80 | 78 | 63 | 68 | 60 | #N/A | #N/A
2022-06-16 23:00 | 6 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 72 | 61 | 64 | 78 | 78 | 62 | 68 | 59 | #N/A | #N/A
2022-06-17 | 6 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 71 | 59 | 63 | 77 | 76 | 59 | 65 | 58 | #N/A | #N/A
2022-06-17 01:00 | 6 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 71 | 58 | 63 | 75 | 76 | 57 | 63 | 57 | #N/A | #N/A
2022-06-17 02:00 | 6 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 69 | 58 | 64 | 75 | 74 | 57 | 62 | 57 | #N/A | #N/A
2022-06-17 03:00 | 6 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 69 | 57 | 64 | 74 | 73 | 56 | 60 | 56 | #N/A | #N/A
2022-06-17 04:00 | 6 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 69 | 57 | 65 | 75 | 72 | 57 | 57 | 55 | #N/A | #N/A
2022-06-17 05:00 | 6 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 70 | 57 | 66 | 73 | 73 | 58 | 60 | 54 | #N/A | #N/A
2022-06-17 06:00 | 6 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 70 | 57 | 67 | 71 | 77 | 62 | 62 | 54 | #N/A | #N/A
2022-06-17 07:00 | 6 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 72 | 58 | 69 | 69 | 80 | 68 | 64 | 54 | #N/A | #N/A
2022-06-17 08:00 | 6 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 79 | 60 | 72 | 71 | 80 | 72 | 66 | 54 | #N/A | #N/A
2022-06-17 09:00 | 6 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 82 | 61 | 74 | 73 | 78 | 74 | 69 | 55 | #N/A | #N/A
2022-06-17 10:00 | 6 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 83 | 62 | 76 | 74 | 81 | 78 | 72 | 56 | #N/A | #N/A
2022-06-17 11:00 | 6 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 86 | 64 | 77 | 75 | 81 | 78 | 72 | 56 | #N/A | #N/A
2022-06-17 12:00 | 6 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 87 | 65 | 79 | 79 | 80 | 80 | 75 | 55 | #N/A | #N/A
2022-06-17 13:00 | 6 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 88 | 65 | 79 | 80 | 81 | 82 | 76 | 55 | #N/A | #N/A
2022-06-17 14:00 | 6 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 89 | 65 | 80 | 80 | 80 | 80 | 76 | 55 | #N/A | #N/A
2022-06-17 15:00 | 6 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 89 | 65 | 80 | 80 | 80 | 79 | 78 | 54 | #N/A | #N/A
2022-06-17 16:00 | 6 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 87 | 64 | 79 | 79 | 80 | 78 | 76 | 54 | #N/A | #N/A
2022-06-17 17:00 | 6 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 86 | 64 | 77 | 78 | 79 | 77 | 75 | 52 | #N/A | #N/A
2022-06-17 18:00 | 6 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 83 | 63 | 76 | 76 | 78 | 75 | 73 | 53 | #N/A | #N/A
2022-06-17 19:00 | 6 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 80 | 59 | 74 | 72 | 73 | 71 | 69 | 52 | #N/A | #N/A
2022-06-17 20:00 | 6 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 79 | 55 | 71 | 67 | 72 | 70 | 64 | 53 | #N/A | #N/A
2022-06-17 21:00 | 6 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 77 | 51 | 69 | 65 | 72 | 67 | 62 | 53 | #N/A | #N/A
2022-06-17 22:00 | 6 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 77 | 48 | 65 | 64 | 69 | 63 | 59 | 52 | #N/A | #N/A
2022-06-17 23:00 | 6 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 75 | 46 | 62 | 61 | 67 | 59 | 57 | 52 | #N/A | #N/A
2022-06-18 | 6 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 77 | 43 | 58 | 59 | 68 | 57 | 55 | 51 | #N/A | #N/A
2022-06-18 01:00 | 6 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 76 | 42 | 57 | 58 | 67 | 56 | 54 | 50 | #N/A | #N/A
2022-06-18 02:00 | 6 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 73 | 40 | 55 | 58 | 64 | 54 | 53 | 50 | #N/A | #N/A
2022-06-18 03:00 | 6 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 71 | 39 | 54 | 57 | 63 | 54 | 52 | 48 | #N/A | #N/A
2022-06-18 04:00 | 6 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 71 | 44 | 54 | 56 | 63 | 54 | 52 | 48 | #N/A | #N/A
2022-06-18 05:00 | 6 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 72 | 50 | 55 | 59 | 65 | 56 | 53 | 49 | #N/A | #N/A
2022-06-18 06:00 | 6 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 76 | 55 | 55 | 66 | 69 | 60 | 56 | 52 | #N/A | #N/A
2022-06-18 07:00 | 6 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 78 | 59 | 55 | 70 | 73 | 66 | 61 | 54 | #N/A | #N/A
2022-06-18 08:00 | 6 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 83 | 62 | 54 | 71 | 75 | 71 | 67 | 58 | #N/A | #N/A
2022-06-18 09:00 | 6 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 84 | 66 | 54 | 75 | 77 | 74 | 74 | 63 | #N/A | #N/A
2022-06-18 10:00 | 6 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 85 | 68 | 54 | 76 | 78 | 75 | 77 | 67 | #N/A | #N/A
2022-06-18 11:00 | 6 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 88 | 71 | 55 | 78 | 80 | 78 | 77 | 70 | #N/A | #N/A
2022-06-18 12:00 | 6 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 88 | 73 | 55 | 80 | 81 | 79 | 80 | 72 | #N/A | #N/A
2022-06-18 13:00 | 6 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 89 | 73 | 56 | 80 | 81 | 80 | 82 | 71 | #N/A | #N/A
2022-06-18 14:00 | 6 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 88 | 74 | 57 | 82 | 82 | 81 | 83 | 73 | #N/A | #N/A
2022-06-18 15:00 | 6 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 88 | 74 | 58 | 81 | 81 | 82 | 83 | 73 | #N/A | #N/A
2022-06-18 16:00 | 6 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 88 | 73 | 58 | 81 | 79 | 82 | 85 | 73 | #N/A | #N/A
2022-06-18 17:00 | 6 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 86 | 73 | 59 | 79 | 79 | 81 | 82 | 72 | #N/A | #N/A
2022-06-18 18:00 | 6 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 84 | 72 | 59 | 78 | 77 | 80 | 80 | 68 | #N/A | #N/A
2022-06-18 19:00 | 6 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 81 | 68 | 56 | 75 | 74 | 75 | 74 | 62 | #N/A | #N/A
2022-06-18 20:00 | 6 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 80 | 65 | 53 | 74 | 70 | 72 | 71 | 58 | #N/A | #N/A
2022-06-18 21:00 | 6 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 80 | 61 | 50 | 73 | 68 | 72 | 66 | 55 | #N/A | #N/A
2022-06-18 22:00 | 6 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 76 | 61 | 49 | 72 | 68 | 67 | 67 | 54 | #N/A | #N/A
2022-06-18 23:00 | 6 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 74 | 61 | 49 | 70 | 67 | 68 | 66 | 51 | #N/A | #N/A
2022-06-19 | 6 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 75 | 61 | 48 | 69 | 66 | 66 | 65 | 51 | #N/A | #N/A
2022-06-19 01:00 | 6 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 72 | 59 | 47 | 68 | 64 | 63 | 64 | 50 | #N/A | #N/A
2022-06-19 02:00 | 6 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 72 | 58 | 47 | 68 | 62 | 65 | 63 | 48 | #N/A | #N/A
2022-06-19 03:00 | 6 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 70 | 56 | 46 | 66 | 64 | 60 | 60 | 48 | #N/A | #N/A
2022-06-19 04:00 | 6 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 70 | 57 | 49 | 65 | 64 | 61 | 62 | 47 | #N/A | #N/A
2022-06-19 05:00 | 6 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 72 | 59 | 52 | 66 | 66 | 64 | 63 | 49 | #N/A | #N/A
2022-06-19 06:00 | 6 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 74 | 60 | 55 | 69 | 69 | 70 | 66 | 51 | #N/A | #N/A
2022-06-19 07:00 | 6 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 76 | 64 | 58 | 71 | 72 | 74 | 70 | 57 | #N/A | #N/A
2022-06-19 08:00 | 6 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 77 | 67 | 61 | 71 | 75 | 77 | 75 | 61 | #N/A | #N/A
2022-06-19 09:00 | 6 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 79 | 71 | 64 | 74 | 79 | 80 | 78 | 68 | #N/A | #N/A
2022-06-19 10:00 | 6 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 80 | 73 | 65 | 77 | 78 | 82 | 82 | 72 | #N/A | #N/A
2022-06-19 11:00 | 6 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 81 | 75 | 66 | 79 | 72 | 85 | 84 | 73 | #N/A | #N/A
2022-06-19 12:00 | 6 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 82 | 77 | 67 | 80 | 76 | 87 | 86 | 74 | #N/A | #N/A
2022-06-19 13:00 | 6 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 82 | 78 | 69 | 81 | 74 | 86 | 87 | 74 | #N/A | #N/A
2022-06-19 14:00 | 6 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 80 | 78 | 70 | 82 | 71 | 87 | 87 | 75 | #N/A | #N/A
2022-06-19 15:00 | 6 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 81 | 79 | 72 | 82 | 71 | 87 | 88 | 75 | #N/A | #N/A
2022-06-19 16:00 | 6 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 79 | 76 | 71 | 80 | 72 | 87 | 87 | 74 | #N/A | #N/A
2022-06-19 17:00 | 6 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 77 | 74 | 71 | 78 | 71 | 86 | 86 | 74 | #N/A | #N/A
2022-06-19 18:00 | 6 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 74 | 71 | 70 | 76 | 70 | 84 | 83 | 69 | #N/A | #N/A
2022-06-19 19:00 | 6 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 71 | 68 | 67 | 74 | 71 | 82 | 78 | 66 | #N/A | #N/A
2022-06-19 20:00 | 6 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 68 | 66 | 63 | 72 | 69 | 78 | 76 | 61 | #N/A | #N/A
2022-06-19 21:00 | 6 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 67 | 63 | 60 | 72 | 69 | 74 | 76 | 62 | #N/A | #N/A
2022-06-19 22:00 | 6 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 65 | 63 | 60 | 72 | 69 | 73 | 73 | 59 | #N/A | #N/A
2022-06-19 23:00 | 6 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 64 | 62 | 59 | 71 | 69 | 72 | 72 | 57 | #N/A | #N/A
2022-06-20 | 6 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 62 | 62 | 59 | 70 | 69 | 70 | 70 | 57 | #N/A | #N/A
2022-06-20 01:00 | 6 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 60 | 61 | 58 | 68 | 69 | 73 | 68 | 57 | #N/A | #N/A
2022-06-20 02:00 | 6 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 59 | 61 | 57 | 69 | 70 | 71 | 67 | 58 | #N/A | #N/A
2022-06-20 03:00 | 6 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 58 | 60 | 56 | 68 | 71 | 71 | 65 | 57 | #N/A | #N/A
2022-06-20 04:00 | 6 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 59 | 60 | 57 | 68 | 70 | 68 | 65 | 56 | #N/A | #N/A
2022-06-20 05:00 | 6 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 60 | 59 | 59 | 68 | 70 | 68 | 66 | 56 | #N/A | #N/A
2022-06-20 06:00 | 6 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 62 | 59 | 60 | 70 | 69 | 71 | 68 | 60 | #N/A | #N/A
2022-06-20 07:00 | 6 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 68 | 61 | 64 | 71 | 74 | 71 | 74 | 63 | #N/A | #N/A
2022-06-20 08:00 | 6 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 71 | 63 | 69 | 73 | 75 | 71 | 79 | 69 | #N/A | #N/A
2022-06-20 09:00 | 6 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 73 | 65 | 73 | 74 | 76 | 73 | 81 | 71 | #N/A | #N/A
2022-06-20 10:00 | 6 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 77 | 67 | 74 | 74 | 78 | 79 | 84 | 72 | #N/A | #N/A
2022-06-20 11:00 | 6 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 78 | 69 | 76 | 72 | 79 | 82 | 86 | 73 | #N/A | #N/A
2022-06-20 12:00 | 6 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 80 | 71 | 77 | 72 | 80 | 83 | 87 | 73 | #N/A | #N/A
2022-06-20 13:00 | 6 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 81 | 71 | 78 | 74 | 83 | 84 | 85 | 73 | #N/A | #N/A
2022-06-20 14:00 | 6 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 81 | 71 | 80 | 74 | 81 | 83 | 85 | 73 | #N/A | #N/A
2022-06-20 15:00 | 6 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 80 | 71 | 81 | 75 | 74 | 82 | 84 | 72 | #N/A | #N/A
2022-06-20 16:00 | 6 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 80 | 70 | 80 | 75 | 75 | 73 | 83 | 71 | #N/A | #N/A
2022-06-20 17:00 | 6 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 80 | 69 | 78 | 74 | 75 | 72 | 82 | 70 | #N/A | #N/A
2022-06-20 18:00 | 6 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 76 | 68 | 77 | 73 | 74 | 71 | 80 | 67 | #N/A | #N/A
2022-06-20 19:00 | 6 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 74 | 65 | 75 | 70 | 73 | 69 | 78 | 66 | #N/A | #N/A
2022-06-20 20:00 | 6 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 72 | 62 | 73 | 68 | 72 | 68 | 78 | 64 | #N/A | #N/A
2022-06-20 21:00 | 6 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 71 | 59 | 71 | 68 | 72 | 68 | 77 | 62 | #N/A | #N/A
2022-06-20 22:00 | 6 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 70 | 58 | 69 | 66 | 70 | 67 | 76 | 60 | #N/A | #N/A
2022-06-20 23:00 | 6 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 69 | 58 | 68 | 64 | 69 | 66 | 73 | 59 | #N/A | #N/A
2022-06-21 | 6 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 69 | 57 | 66 | 65 | 68 | 65 | 73 | 60 | #N/A | #N/A
2022-06-21 01:00 | 6 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 69 | 57 | 66 | 64 | 67 | 65 | 71 | 59 | #N/A | #N/A
2022-06-21 02:00 | 6 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 65 | 58 | 65 | 63 | 66 | 64 | 69 | 59 | #N/A | #N/A
2022-06-21 03:00 | 6 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 64 | 58 | 65 | 62 | 66 | 64 | 68 | 59 | #N/A | #N/A
2022-06-21 04:00 | 6 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 64 | 60 | 65 | 62 | 64 | 64 | 68 | 59 | #N/A | #N/A
2022-06-21 05:00 | 6 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 64 | 62 | 64 | 64 | 66 | 65 | 68 | 59 | #N/A | #N/A
2022-06-21 06:00 | 6 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 62 | 64 | 64 | 67 | 70 | 66 | 68 | 61 | #N/A | #N/A
2022-06-21 07:00 | 6 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 64 | 66 | 66 | 71 | 73 | 69 | 69 | 64 | #N/A | #N/A
2022-06-21 08:00 | 6 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 68 | 68 | 68 | 76 | 76 | 70 | 71 | 67 | #N/A | #N/A
2022-06-21 09:00 | 6 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 66 | 70 | 70 | 77 | 78 | 73 | 72 | 71 | #N/A | #N/A
2022-06-21 10:00 | 6 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 67 | 72 | 72 | 80 | 81 | 76 | 72 | 73 | #N/A | #N/A
2022-06-21 11:00 | 6 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 70 | 73 | 75 | 82 | 83 | 78 | 71 | 76 | #N/A | #N/A
2022-06-21 12:00 | 6 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 74 | 75 | 77 | 83 | 84 | 80 | 71 | 77 | #N/A | #N/A
2022-06-21 13:00 | 6 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 79 | 74 | 76 | 83 | 85 | 81 | 71 | 77 | #N/A | #N/A
2022-06-21 14:00 | 6 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 78 | 74 | 75 | 85 | 85 | 81 | 73 | 79 | #N/A | #N/A
2022-06-21 15:00 | 6 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 82 | 73 | 74 | 87 | 85 | 81 | 74 | 78 | #N/A | #N/A
2022-06-21 16:00 | 6 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 82 | 71 | 73 | 84 | 84 | 80 | 71 | 78 | #N/A | #N/A
2022-06-21 17:00 | 6 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 79 | 68 | 73 | 82 | 82 | 79 | 71 | 78 | #N/A | #N/A
2022-06-21 18:00 | 6 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 78 | 66 | 72 | 74 | 81 | 77 | 72 | 75 | #N/A | #N/A
2022-06-21 19:00 | 6 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 75 | 65 | 71 | 74 | 79 | 65 | 71 | 73 | #N/A | #N/A
2022-06-21 20:00 | 6 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 74 | 64 | 69 | 73 | 77 | 65 | 71 | 70 | #N/A | #N/A
2022-06-21 21:00 | 6 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 72 | 63 | 68 | 71 | 76 | 64 | 71 | 65 | #N/A | #N/A
2022-06-21 22:00 | 6 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 69 | 63 | 68 | 70 | 75 | 65 | 70 | 60 | #N/A | #N/A
2022-06-21 23:00 | 6 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 65 | 63 | 67 | 69 | 76 | 65 | 70 | 60 | #N/A | #N/A
2022-06-22 | 6 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 64 | 63 | 67 | 69 | 74 | 65 | 70 | 59 | #N/A | #N/A
2022-06-22 01:00 | 6 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 63 | 63 | 66 | 69 | 71 | 65 | 70 | 57 | #N/A | #N/A
2022-06-22 02:00 | 6 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 62 | 64 | 65 | 69 | 71 | 65 | 69 | 55 | #N/A | #N/A
2022-06-22 03:00 | 6 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 60 | 64 | 64 | 69 | 71 | 64 | 69 | 54 | #N/A | #N/A
2022-06-22 04:00 | 6 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 57 | 64 | 65 | 69 | 70 | 65 | 68 | 55 | #N/A | #N/A
2022-06-22 05:00 | 6 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 59 | 64 | 65 | 69 | 71 | 66 | 68 | 56 | #N/A | #N/A
2022-06-22 06:00 | 6 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 61 | 64 | 66 | 70 | 73 | 67 | 70 | 59 | #N/A | #N/A
2022-06-22 07:00 | 6 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 65 | 66 | 67 | 72 | 77 | 66 | 70 | 63 | #N/A | #N/A
2022-06-22 08:00 | 6 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 67 | 69 | 68 | 77 | 82 | 68 | 73 | 68 | #N/A | #N/A
2022-06-22 09:00 | 6 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 69 | 71 | 69 | 80 | 84 | 69 | 77 | 72 | #N/A | #N/A
2022-06-22 10:00 | 6 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 70 | 70 | 70 | 80 | 86 | 70 | 75 | 77 | #N/A | #N/A
2022-06-22 11:00 | 6 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 71 | 70 | 70 | 83 | 89 | 68 | 74 | 80 | #N/A | #N/A
2022-06-22 12:00 | 6 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 74 | 69 | 71 | 82 | 91 | 71 | 75 | 81 | #N/A | #N/A
2022-06-22 13:00 | 6 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 74 | 66 | 69 | 81 | 91 | 71 | 71 | 82 | #N/A | #N/A
2022-06-22 14:00 | 6 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 74 | 64 | 68 | 81 | 90 | 71 | 72 | 83 | #N/A | #N/A
2022-06-22 15:00 | 6 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 74 | 61 | 66 | 84 | 80 | 73 | 76 | 82 | #N/A | #N/A
2022-06-22 16:00 | 6 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 74 | 61 | 65 | 83 | 78 | 72 | 73 | 82 | #N/A | #N/A
2022-06-22 17:00 | 6 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 73 | 60 | 63 | 80 | 82 | 70 | 73 | 81 | #N/A | #N/A
2022-06-22 18:00 | 6 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 71 | 60 | 62 | 79 | 80 | 68 | 72 | 78 | #N/A | #N/A
2022-06-22 19:00 | 6 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 67 | 58 | 59 | 75 | 76 | 67 | 72 | 72 | #N/A | #N/A
2022-06-22 20:00 | 6 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 65 | 57 | 56 | 73 | 73 | 65 | 71 | 68 | #N/A | #N/A
2022-06-22 21:00 | 6 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 64 | 55 | 53 | 71 | 71 | 64 | 70 | 65 | #N/A | #N/A
2022-06-22 22:00 | 6 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 62 | 54 | 54 | 72 | 70 | 63 | 70 | 63 | #N/A | #N/A
2022-06-22 23:00 | 6 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 62 | 52 | 55 | 71 | 70 | 62 | 70 | 61 | #N/A | #N/A
2022-06-23 | 6 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 61 | 51 | 56 | 69 | 69 | 62 | 70 | 59 | #N/A | #N/A
2022-06-23 01:00 | 6 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 60 | 51 | 55 | 67 | 69 | 61 | 70 | 58 | #N/A | #N/A
2022-06-23 02:00 | 6 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 59 | 50 | 53 | 63 | 67 | 60 | 70 | 57 | #N/A | #N/A
2022-06-23 03:00 | 6 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 58 | 50 | 52 | 62 | 65 | 59 | 70 | 56 | #N/A | #N/A
2022-06-23 04:00 | 6 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 58 | 51 | 52 | 60 | 65 | 59 | 70 | 55 | #N/A | #N/A
2022-06-23 05:00 | 6 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 60 | 52 | 52 | 63 | 67 | 59 | 69 | 58 | #N/A | #N/A
2022-06-23 06:00 | 6 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 62 | 53 | 52 | 68 | 69 | 59 | 68 | 61 | #N/A | #N/A
2022-06-23 07:00 | 6 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 68 | 55 | 52 | 71 | 71 | 60 | 70 | 64 | #N/A | #N/A
2022-06-23 08:00 | 6 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 70 | 58 | 52 | 72 | 73 | 61 | 69 | 70 | #N/A | #N/A
2022-06-23 09:00 | 6 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 72 | 60 | 52 | 73 | 75 | 61 | 70 | 77 | #N/A | #N/A
2022-06-23 10:00 | 6 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 75 | 62 | 52 | 76 | 76 | 64 | 69 | 80 | #N/A | #N/A
2022-06-23 11:00 | 6 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 75 | 64 | 51 | 75 | 78 | 64 | 69 | 81 | #N/A | #N/A
2022-06-23 12:00 | 6 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 78 | 66 | 51 | 78 | 79 | 65 | 68 | 83 | #N/A | #N/A
2022-06-23 13:00 | 6 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 77 | 66 | 51 | 79 | 80 | 64 | 70 | 84 | #N/A | #N/A
2022-06-23 14:00 | 6 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 78 | 65 | 51 | 79 | 77 | 65 | 70 | 84 | #N/A | #N/A
2022-06-23 15:00 | 6 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 77 | 65 | 51 | 78 | 79 | 66 | 70 | 82 | #N/A | #N/A
2022-06-23 16:00 | 6 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 77 | 64 | 50 | 80 | 79 | 65 | 68 | 83 | #N/A | #N/A
2022-06-23 17:00 | 6 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 74 | 64 | 50 | 79 | 78 | 64 | 68 | 81 | #N/A | #N/A
2022-06-23 18:00 | 6 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 72 | 63 | 49 | 77 | 75 | 65 | 67 | 77 | #N/A | #N/A
2022-06-23 19:00 | 6 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 71 | 59 | 49 | 71 | 73 | 64 | 67 | 70 | #N/A | #N/A
2022-06-23 20:00 | 6 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 70 | 56 | 49 | 68 | 73 | 62 | 66 | 69 | #N/A | #N/A
2022-06-23 21:00 | 6 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 52 | 49 | 68 | 71 | 60 | 65 | 66 | #N/A | #N/A
2022-06-23 22:00 | 6 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 68 | 50 | 49 | 64 | 67 | 58 | 63 | 65 | #N/A | #N/A
2022-06-23 23:00 | 6 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 67 | 48 | 48 | 64 | 65 | 57 | 62 | 63 | #N/A | #N/A
2022-06-24 | 6 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 65 | 46 | 48 | 61 | 67 | 56 | 61 | 61 | #N/A | #N/A
2022-06-24 01:00 | 6 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 63 | 47 | 48 | 62 | 65 | 55 | 60 | 58 | #N/A | #N/A
2022-06-24 02:00 | 6 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 63 | 48 | 48 | 59 | 64 | 54 | 58 | 57 | #N/A | #N/A
2022-06-24 03:00 | 6 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 62 | 49 | 48 | 58 | 64 | 53 | 59 | 57 | #N/A | #N/A
2022-06-24 04:00 | 6 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 60 | 50 | 49 | 58 | 63 | 52 | 57 | 57 | #N/A | #N/A
2022-06-24 05:00 | 6 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 60 | 52 | 49 | 60 | 66 | 52 | 58 | 59 | #N/A | #N/A
2022-06-24 06:00 | 6 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 60 | 53 | 50 | 67 | 69 | 53 | 59 | 63 | #N/A | #N/A
2022-06-24 07:00 | 6 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 60 | 58 | 52 | 69 | 71 | 57 | 62 | 70 | #N/A | #N/A
2022-06-24 08:00 | 6 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 61 | 62 | 54 | 72 | 74 | 64 | 65 | 72 | #N/A | #N/A
2022-06-24 09:00 | 6 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 61 | 67 | 56 | 75 | 77 | 65 | 69 | 76 | #N/A | #N/A
2022-06-24 10:00 | 6 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 62 | 69 | 57 | 78 | 80 | 66 | 75 | 78 | #N/A | #N/A
2022-06-24 11:00 | 6 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 63 | 70 | 57 | 80 | 81 | 69 | 79 | 79 | #N/A | #N/A
2022-06-24 12:00 | 6 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 63 | 72 | 58 | 81 | 83 | 70 | 81 | 81 | #N/A | #N/A
2022-06-24 13:00 | 6 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 64 | 71 | 59 | 82 | 85 | 73 | 82 | 83 | #N/A | #N/A
2022-06-24 14:00 | 6 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 65 | 70 | 59 | 82 | 84 | 73 | 82 | 82 | #N/A | #N/A
2022-06-24 15:00 | 6 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 65 | 69 | 60 | 83 | 83 | 74 | 84 | 84 | #N/A | #N/A
2022-06-24 16:00 | 6 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 66 | 69 | 59 | 83 | 82 | 76 | 83 | 82 | #N/A | #N/A
2022-06-24 17:00 | 6 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 66 | 69 | 59 | 81 | 80 | 76 | 82 | 81 | #N/A | #N/A
2022-06-24 18:00 | 6 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 65 | 69 | 58 | 80 | 79 | 74 | 80 | 79 | #N/A | #N/A
2022-06-24 19:00 | 6 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 63 | 68 | 57 | 79 | 76 | 70 | 74 | 77 | #N/A | #N/A
2022-06-24 20:00 | 6 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 63 | 66 | 56 | 77 | 75 | 72 | 70 | 72 | #N/A | #N/A
2022-06-24 21:00 | 6 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 64 | 65 | 55 | 76 | 74 | 67 | 69 | 70 | #N/A | #N/A
2022-06-24 22:00 | 6 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 64 | 65 | 52 | 75 | 74 | 67 | 68 | 67 | #N/A | #N/A
2022-06-24 23:00 | 6 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 64 | 65 | 48 | 73 | 73 | 62 | 66 | 63 | #N/A | #N/A
2022-06-25 | 6 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 64 | 65 | 45 | 71 | 73 | 63 | 65 | 64 | #N/A | #N/A
2022-06-25 01:00 | 6 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 63 | 65 | 43 | 71 | 74 | 61 | 64 | 63 | #N/A | #N/A
2022-06-25 02:00 | 6 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 66 | 42 | 70 | 71 | 60 | 63 | 63 | #N/A | #N/A
2022-06-25 03:00 | 6 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 64 | 66 | 40 | 69 | 73 | 59 | 61 | 62 | #N/A | #N/A
2022-06-25 04:00 | 6 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 64 | 65 | 45 | 70 | 72 | 58 | 61 | 63 | #N/A | #N/A
2022-06-25 05:00 | 6 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 65 | 65 | 49 | 71 | 73 | 59 | 63 | 65 | #N/A | #N/A
2022-06-25 06:00 | 6 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 66 | 64 | 54 | 74 | 75 | 61 | 65 | 66 | #N/A | #N/A
2022-06-25 07:00 | 6 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 69 | 65 | 56 | 75 | 77 | 63 | 71 | 68 | #N/A | #N/A
2022-06-25 08:00 | 6 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 70 | 66 | 59 | 77 | 79 | 68 | 74 | 70 | #N/A | #N/A
2022-06-25 09:00 | 6 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 71 | 67 | 61 | 78 | 81 | 72 | 79 | 71 | #N/A | #N/A
2022-06-25 10:00 | 6 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 73 | 67 | 62 | 80 | 84 | 75 | 81 | 73 | #N/A | #N/A
2022-06-25 11:00 | 6 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 70 | 68 | 63 | 84 | 85 | 76 | 84 | 77 | #N/A | #N/A
2022-06-25 12:00 | 6 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 88 | 73 | 68 | 64 | 87 | 87 | 77 | 84 | 80 | #N/A | #N/A
2022-06-25 13:00 | 6 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 88 | 70 | 70 | 65 | 87 | 88 | 78 | 86 | 83 | #N/A | #N/A
2022-06-25 14:00 | 6 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 88 | 75 | 71 | 66 | 88 | 89 | 77 | 87 | 83 | #N/A | #N/A
2022-06-25 15:00 | 6 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 76 | 73 | 67 | 85 | 89 | 77 | 83 | 84 | #N/A | #N/A
2022-06-25 16:00 | 6 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 75 | 71 | 66 | 68 | 88 | 78 | 81 | 84 | #N/A | #N/A
2022-06-25 17:00 | 6 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 72 | 68 | 65 | 64 | 85 | 77 | 80 | 83 | #N/A | #N/A
2022-06-25 18:00 | 6 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 68 | 66 | 64 | 66 | 67 | 77 | 80 | 81 | #N/A | #N/A
2022-06-25 19:00 | 6 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 66 | 63 | 60 | 67 | 68 | 74 | 78 | 80 | #N/A | #N/A
2022-06-25 20:00 | 6 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 64 | 59 | 56 | 66 | 68 | 70 | 76 | 78 | #N/A | #N/A
2022-06-25 21:00 | 6 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 63 | 56 | 52 | 66 | 68 | 68 | 74 | 75 | #N/A | #N/A
2022-06-25 22:00 | 6 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 63 | 54 | 51 | 65 | 67 | 66 | 71 | 75 | #N/A | #N/A
2022-06-25 23:00 | 6 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 62 | 52 | 50 | 65 | 64 | 64 | 70 | 72 | #N/A | #N/A
2022-06-26 | 6 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 61 | 50 | 49 | 65 | 64 | 62 | 67 | 70 | #N/A | #N/A
2022-06-26 01:00 | 6 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 59 | 48 | 50 | 65 | 64 | 62 | 64 | 70 | #N/A | #N/A
2022-06-26 02:00 | 6 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 59 | 47 | 52 | 65 | 65 | 60 | 62 | 70 | #N/A | #N/A
2022-06-26 03:00 | 6 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 59 | 45 | 53 | 62 | 64 | 60 | 62 | 68 | #N/A | #N/A
2022-06-26 04:00 | 6 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 59 | 46 | 54 | 61 | 64 | 60 | 62 | 69 | #N/A | #N/A
2022-06-26 05:00 | 6 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 60 | 48 | 56 | 61 | 65 | 61 | 64 | 69 | #N/A | #N/A
2022-06-26 06:00 | 6 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 49 | 57 | 62 | 65 | 65 | 66 | 72 | #N/A | #N/A
2022-06-26 07:00 | 6 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 67 | 52 | 61 | 64 | 64 | 69 | 68 | 75 | #N/A | #N/A
2022-06-26 08:00 | 6 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 54 | 66 | 66 | 66 | 73 | 67 | 80 | #N/A | #N/A
2022-06-26 09:00 | 6 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 73 | 57 | 70 | 69 | 66 | 76 | 67 | 84 | #N/A | #N/A
2022-06-26 10:00 | 6 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 75 | 58 | 71 | 68 | 70 | 78 | 66 | 86 | #N/A | #N/A
2022-06-26 11:00 | 6 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 76 | 60 | 72 | 71 | 70 | 80 | 67 | 87 | #N/A | #N/A
2022-06-26 12:00 | 6 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 78 | 61 | 73 | 72 | 72 | 80 | 67 | 89 | #N/A | #N/A
2022-06-26 13:00 | 6 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 77 | 61 | 72 | 72 | 71 | 83 | 68 | 91 | #N/A | #N/A
2022-06-26 14:00 | 6 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 88 | 80 | 61 | 72 | 73 | 70 | 82 | 68 | 90 | #N/A | #N/A
2022-06-26 15:00 | 6 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 79 | 61 | 71 | 72 | 71 | 83 | 68 | 91 | #N/A | #N/A
2022-06-26 16:00 | 6 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 79 | 60 | 70 | 70 | 71 | 83 | 69 | 90 | #N/A | #N/A
2022-06-26 17:00 | 6 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 77 | 59 | 69 | 69 | 70 | 83 | 68 | 89 | #N/A | #N/A
2022-06-26 18:00 | 6 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 73 | 58 | 68 | 70 | 69 | 82 | 68 | 84 | #N/A | #N/A
2022-06-26 19:00 | 6 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 71 | 55 | 64 | 66 | 68 | 78 | 67 | 80 | #N/A | #N/A
2022-06-26 20:00 | 6 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 70 | 53 | 60 | 63 | 67 | 79 | 67 | 76 | #N/A | #N/A
2022-06-26 21:00 | 6 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 70 | 50 | 56 | 58 | 66 | 75 | 66 | 75 | #N/A | #N/A
2022-06-26 22:00 | 6 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 68 | 47 | 57 | 59 | 61 | 73 | 66 | 71 | #N/A | #N/A
2022-06-26 23:00 | 6 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 68 | 45 | 58 | 57 | 61 | 71 | 66 | 70 | #N/A | #N/A
2022-06-27 | 6 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 68 | 42 | 59 | 59 | 58 | 68 | 66 | 69 | #N/A | #N/A
2022-06-27 01:00 | 6 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 67 | 43 | 59 | 55 | 58 | 68 | 66 | 67 | #N/A | #N/A
2022-06-27 02:00 | 6 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 67 | 43 | 59 | 55 | 56 | 66 | 66 | 66 | #N/A | #N/A
2022-06-27 03:00 | 6 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 67 | 44 | 59 | 54 | 54 | 65 | 65 | 66 | #N/A | #N/A
2022-06-27 04:00 | 6 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 67 | 47 | 60 | 55 | 54 | 63 | 65 | 66 | #N/A | #N/A
2022-06-27 05:00 | 6 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 67 | 49 | 61 | 58 | 59 | 64 | 66 | 67 | #N/A | #N/A
2022-06-27 06:00 | 6 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 67 | 52 | 62 | 62 | 63 | 67 | 67 | 72 | #N/A | #N/A
2022-06-27 07:00 | 6 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 66 | 56 | 66 | 66 | 67 | 73 | 68 | 78 | #N/A | #N/A
2022-06-27 08:00 | 6 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 69 | 60 | 69 | 69 | 70 | 77 | 70 | 81 | #N/A | #N/A
2022-06-27 09:00 | 6 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 69 | 64 | 73 | 71 | 72 | 79 | 74 | 83 | #N/A | #N/A
2022-06-27 10:00 | 6 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 71 | 65 | 74 | 74 | 75 | 81 | 76 | 86 | #N/A | #N/A
2022-06-27 11:00 | 6 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 74 | 67 | 74 | 76 | 75 | 84 | 79 | 86 | #N/A | #N/A
2022-06-27 12:00 | 6 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 91 | 72 | 68 | 75 | 75 | 76 | 85 | 80 | 87 | #N/A | #N/A
2022-06-27 13:00 | 6 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 92 | 70 | 68 | 75 | 75 | 78 | 86 | 81 | 89 | #N/A | #N/A
2022-06-27 14:00 | 6 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 90 | 65 | 68 | 75 | 77 | 78 | 85 | 78 | 87 | #N/A | #N/A
2022-06-27 15:00 | 6 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 66 | 68 | 75 | 77 | 78 | 85 | 79 | 86 | #N/A | #N/A
2022-06-27 16:00 | 6 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 90 | 65 | 67 | 72 | 77 | 76 | 84 | 79 | 86 | #N/A | #N/A
2022-06-27 17:00 | 6 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 64 | 67 | 69 | 77 | 77 | 84 | 78 | 85 | #N/A | #N/A
2022-06-27 18:00 | 6 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 64 | 66 | 66 | 74 | 75 | 82 | 76 | 84 | #N/A | #N/A
2022-06-27 19:00 | 6 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 64 | 61 | 65 | 67 | 71 | 80 | 68 | 83 | #N/A | #N/A
2022-06-27 20:00 | 6 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 65 | 57 | 65 | 66 | 67 | 76 | 62 | 81 | #N/A | #N/A
2022-06-27 21:00 | 6 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 65 | 52 | 64 | 66 | 65 | 74 | 61 | 79 | #N/A | #N/A
2022-06-27 22:00 | 6 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 65 | 51 | 63 | 60 | 64 | 74 | 59 | 74 | #N/A | #N/A
2022-06-27 23:00 | 6 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 64 | 50 | 63 | 59 | 62 | 73 | 59 | 73 | #N/A | #N/A
2022-06-28 | 6 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 49 | 62 | 60 | 64 | 69 | 58 | 73 | #N/A | #N/A
2022-06-28 01:00 | 6 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 63 | 49 | 62 | 57 | 60 | 68 | 57 | 73 | #N/A | #N/A
2022-06-28 02:00 | 6 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 62 | 49 | 61 | 56 | 60 | 68 | 56 | 73 | #N/A | #N/A
2022-06-28 03:00 | 6 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 60 | 49 | 61 | 54 | 58 | 67 | 55 | 73 | #N/A | #N/A
2022-06-28 04:00 | 6 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 60 | 51 | 61 | 54 | 58 | 67 | 54 | 73 | #N/A | #N/A
2022-06-28 05:00 | 6 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 60 | 53 | 61 | 56 | 62 | 67 | 55 | 74 | #N/A | #N/A
2022-06-28 06:00 | 6 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 60 | 55 | 61 | 60 | 67 | 71 | 58 | 78 | #N/A | #N/A
2022-06-28 07:00 | 6 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 60 | 59 | 64 | 65 | 71 | 76 | 61 | 79 | #N/A | #N/A
2022-06-28 08:00 | 6 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 61 | 64 | 67 | 71 | 75 | 78 | 63 | 77 | #N/A | #N/A
2022-06-28 09:00 | 6 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 63 | 68 | 70 | 74 | 77 | 81 | 65 | 80 | #N/A | #N/A
2022-06-28 10:00 | 6 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 64 | 70 | 69 | 76 | 79 | 83 | 66 | 82 | #N/A | #N/A
2022-06-28 11:00 | 6 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 66 | 71 | 69 | 77 | 80 | 84 | 69 | 82 | #N/A | #N/A
2022-06-28 12:00 | 6 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 69 | 73 | 68 | 77 | 81 | 85 | 70 | 81 | #N/A | #N/A
2022-06-28 13:00 | 6 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 70 | 74 | 69 | 79 | 82 | 86 | 72 | 81 | #N/A | #N/A
2022-06-28 14:00 | 6 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 70 | 74 | 71 | 79 | 82 | 87 | 69 | 77 | #N/A | #N/A
2022-06-28 15:00 | 6 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 71 | 75 | 72 | 80 | 82 | 86 | 72 | 75 | #N/A | #N/A
2022-06-28 16:00 | 6 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 72 | 74 | 70 | 80 | 81 | 86 | 71 | 75 | #N/A | #N/A
2022-06-28 17:00 | 6 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 71 | 72 | 69 | 80 | 80 | 85 | 72 | 76 | #N/A | #N/A
2022-06-28 18:00 | 6 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 69 | 71 | 67 | 76 | 76 | 82 | 70 | 74 | #N/A | #N/A
2022-06-28 19:00 | 6 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 67 | 66 | 64 | 70 | 72 | 79 | 68 | 73 | #N/A | #N/A
2022-06-28 20:00 | 6 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 65 | 62 | 62 | 70 | 69 | 76 | 63 | 73 | #N/A | #N/A
2022-06-28 21:00 | 6 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 64 | 57 | 59 | 66 | 66 | 74 | 64 | 73 | #N/A | #N/A
2022-06-28 22:00 | 6 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 64 | 57 | 58 | 62 | 68 | 74 | 63 | 73 | #N/A | #N/A
2022-06-28 23:00 | 6 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 57 | 57 | 60 | 63 | 72 | 62 | 73 | #N/A | #N/A
2022-06-29 | 6 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 63 | 57 | 56 | 60 | 63 | 70 | 61 | 73 | #N/A | #N/A
2022-06-29 01:00 | 6 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 62 | 57 | 56 | 59 | 58 | 68 | 61 | 72 | #N/A | #N/A
2022-06-29 02:00 | 6 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 63 | 58 | 57 | 57 | 61 | 67 | 59 | 73 | #N/A | #N/A
2022-06-29 03:00 | 6 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 63 | 58 | 57 | 56 | 57 | 66 | 57 | 72 | #N/A | #N/A
2022-06-29 04:00 | 6 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 64 | 59 | 59 | 56 | 60 | 64 | 58 | 72 | #N/A | #N/A
2022-06-29 05:00 | 6 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 65 | 61 | 62 | 58 | 64 | 65 | 63 | 73 | #N/A | #N/A
2022-06-29 06:00 | 6 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 68 | 62 | 64 | 66 | 68 | 70 | 64 | 74 | #N/A | #N/A
2022-06-29 07:00 | 6 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 71 | 65 | 66 | 70 | 72 | 74 | 68 | 74 | #N/A | #N/A
2022-06-29 08:00 | 6 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 72 | 67 | 69 | 71 | 76 | 79 | 73 | 74 | #N/A | #N/A
2022-06-29 09:00 | 6 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 75 | 70 | 71 | 78 | 79 | 83 | 75 | 76 | #N/A | #N/A
2022-06-29 10:00 | 6 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 75 | 73 | 68 | 78 | 82 | 84 | 78 | 78 | #N/A | #N/A
2022-06-29 11:00 | 6 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 76 | 76 | 65 | 80 | 83 | 85 | 81 | 82 | #N/A | #N/A
2022-06-29 12:00 | 6 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 76 | 79 | 62 | 82 | 84 | 86 | 82 | 84 | #N/A | #N/A
2022-06-29 13:00 | 6 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 80 | 80 | 64 | 83 | 84 | 86 | 84 | 74 | #N/A | #N/A
2022-06-29 14:00 | 6 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 75 | 80 | 67 | 82 | 84 | 87 | 83 | 76 | #N/A | #N/A
2022-06-29 15:00 | 6 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 76 | 81 | 69 | 83 | 84 | 86 | 82 | 79 | #N/A | #N/A
2022-06-29 16:00 | 6 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 77 | 79 | 68 | 83 | 82 | 86 | 80 | 80 | #N/A | #N/A
2022-06-29 17:00 | 6 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 77 | 76 | 66 | 81 | 78 | 85 | 80 | 79 | #N/A | #N/A
2022-06-29 18:00 | 6 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 75 | 74 | 65 | 78 | 76 | 83 | 77 | 77 | #N/A | #N/A
2022-06-29 19:00 | 6 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 74 | 71 | 65 | 75 | 74 | 81 | 75 | 72 | #N/A | #N/A
2022-06-29 20:00 | 6 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 67 | 69 | 65 | 74 | 72 | 79 | 75 | 69 | #N/A | #N/A
2022-06-29 21:00 | 6 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 64 | 66 | 65 | 74 | 70 | 77 | 75 | 66 | #N/A | #N/A
2022-06-29 22:00 | 6 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 63 | 65 | 65 | 72 | 67 | 76 | 75 | 64 | #N/A | #N/A
2022-06-29 23:00 | 6 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 65 | 64 | 70 | 67 | 76 | 74 | 63 | #N/A | #N/A
2022-06-30 | 6 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 64 | 64 | 70 | 66 | 75 | 73 | 61 | #N/A | #N/A
2022-06-30 01:00 | 6 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 63 | 64 | 68 | 64 | 73 | 73 | 58 | #N/A | #N/A
2022-06-30 02:00 | 6 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 63 | 64 | 68 | 64 | 71 | 73 | 56 | #N/A | #N/A
2022-06-30 03:00 | 6 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 62 | 62 | 64 | 67 | 64 | 72 | 71 | 54 | #N/A | #N/A
2022-06-30 04:00 | 6 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 61 | 64 | 64 | 68 | 61 | 71 | 70 | 55 | #N/A | #N/A
2022-06-30 05:00 | 6 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 61 | 65 | 65 | 69 | 65 | 70 | 71 | 57 | #N/A | #N/A
2022-06-30 06:00 | 6 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 67 | 65 | 71 | 66 | 72 | 73 | 60 | #N/A | #N/A
2022-06-30 07:00 | 6 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 66 | 70 | 67 | 71 | 71 | 70 | 74 | 64 | #N/A | #N/A
2022-06-30 08:00 | 6 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 67 | 74 | 69 | 73 | 74 | 70 | 75 | 66 | #N/A | #N/A
2022-06-30 09:00 | 6 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 69 | 77 | 71 | 76 | 74 | 75 | 78 | 68 | #N/A | #N/A
2022-06-30 10:00 | 6 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 68 | 79 | 71 | 78 | 78 | 75 | 79 | 72 | #N/A | #N/A
2022-06-30 11:00 | 6 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 67 | 81 | 71 | 81 | 80 | 80 | 79 | 75 | #N/A | #N/A
2022-06-30 12:00 | 6 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 66 | 83 | 71 | 82 | 84 | 81 | 82 | 75 | #N/A | #N/A
2022-06-30 13:00 | 6 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 68 | 80 | 69 | 84 | 81 | 82 | 80 | 76 | #N/A | #N/A
2022-06-30 14:00 | 6 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 69 | 77 | 68 | 82 | 78 | 76 | 81 | 77 | #N/A | #N/A
2022-06-30 15:00 | 6 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 68 | 74 | 66 | 81 | 79 | 80 | 81 | 77 | #N/A | #N/A
2022-06-30 16:00 | 6 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 70 | 72 | 66 | 79 | 77 | 76 | 80 | 77 | #N/A | #N/A
2022-06-30 17:00 | 6 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 68 | 69 | 67 | 80 | 76 | 79 | 80 | 77 | #N/A | #N/A
2022-06-30 18:00 | 6 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 67 | 67 | 67 | 77 | 72 | 79 | 79 | 75 | #N/A | #N/A
2022-06-30 19:00 | 6 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 66 | 66 | 65 | 73 | 69 | 76 | 77 | 72 | #N/A | #N/A
2022-06-30 20:00 | 6 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 65 | 64 | 63 | 72 | 69 | 73 | 74 | 72 | #N/A | #N/A
2022-06-30 21:00 | 6 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 64 | 64 | 72 | 68 | 71 | 72 | 69 | #N/A | #N/A
2022-06-30 22:00 | 6 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 62 | 63 | 64 | 71 | 66 | 68 | 70 | 67 | #N/A | #N/A
2022-06-30 23:00 | 6 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 60 | 62 | 65 | 71 | 65 | 65 | 67 | 64 | #N/A | #N/A
2022-07-01 | 7 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 59 | 61 | 65 | 71 | 63 | 63 | 65 | 62 | #N/A | #N/A
2022-07-01 01:00 | 7 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 57 | 60 | 66 | 71 | 62 | 60 | 63 | 59 | #N/A | #N/A
2022-07-01 02:00 | 7 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 56 | 60 | 66 | 70 | 60 | 58 | 61 | 56 | #N/A | #N/A
2022-07-01 03:00 | 7 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 54 | 59 | 67 | 70 | 59 | 55 | 59 | 54 | #N/A | #N/A
2022-07-01 04:00 | 7 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 51 | 59 | 69 | 69 | 59 | 55 | 56 | 53 | #N/A | #N/A
2022-07-01 05:00 | 7 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 54 | 60 | 70 | 69 | 61 | 56 | 58 | 54 | #N/A | #N/A
2022-07-01 06:00 | 7 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 56 | 60 | 70 | 70 | 68 | 58 | 62 | 59 | #N/A | #N/A
2022-07-01 07:00 | 7 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 59 | 61 | 73 | 75 | 72 | 61 | 65 | 64 | #N/A | #N/A
2022-07-01 08:00 | 7 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 64 | 62 | 75 | 79 | 74 | 63 | 69 | 68 | #N/A | #N/A
2022-07-01 09:00 | 7 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 66 | 63 | 78 | 81 | 78 | 64 | 72 | 73 | #N/A | #N/A
2022-07-01 10:00 | 7 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 67 | 66 | 78 | 84 | 81 | 68 | 74 | 74 | #N/A | #N/A
2022-07-01 11:00 | 7 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 69 | 69 | 80 | 83 | 81 | 74 | 76 | 75 | #N/A | #N/A
2022-07-01 12:00 | 7 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 70 | 72 | 81 | 84 | 77 | 74 | 78 | 76 | #N/A | #N/A
2022-07-01 13:00 | 7 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 71 | 68 | 82 | 84 | 79 | 77 | 80 | 76 | #N/A | #N/A
2022-07-01 14:00 | 7 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 71 | 65 | 85 | 83 | 75 | 76 | 80 | 77 | #N/A | #N/A
2022-07-01 15:00 | 7 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 69 | 61 | 81 | 79 | 75 | 76 | 81 | 76 | #N/A | #N/A
2022-07-01 16:00 | 7 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 68 | 61 | 81 | 78 | 74 | 76 | 81 | 75 | #N/A | #N/A
2022-07-01 17:00 | 7 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 66 | 61 | 80 | 76 | 72 | 75 | 80 | 73 | #N/A | #N/A
2022-07-01 18:00 | 7 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 64 | 61 | 79 | 74 | 72 | 73 | 78 | 71 | #N/A | #N/A
2022-07-01 19:00 | 7 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 60 | 75 | 70 | 71 | 71 | 74 | 67 | #N/A | #N/A
2022-07-01 20:00 | 7 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 61 | 60 | 74 | 70 | 71 | 70 | 72 | 65 | #N/A | #N/A
2022-07-01 21:00 | 7 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 60 | 59 | 73 | 69 | 70 | 70 | 68 | 62 | #N/A | #N/A
2022-07-01 22:00 | 7 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 59 | 59 | 73 | 67 | 69 | 69 | 64 | 59 | #N/A | #N/A
2022-07-01 23:00 | 7 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 58 | 58 | 72 | 66 | 67 | 69 | 63 | 56 | #N/A | #N/A
2022-07-02 | 7 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 57 | 58 | 72 | 67 | 67 | 68 | 64 | 56 | #N/A | #N/A
2022-07-02 01:00 | 7 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 50 | 58 | 71 | 66 | 66 | 69 | 62 | 55 | #N/A | #N/A
2022-07-02 02:00 | 7 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 49 | 58 | 70 | 66 | 66 | 67 | 63 | 54 | #N/A | #N/A
2022-07-02 03:00 | 7 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 51 | 58 | 70 | 64 | 67 | 67 | 64 | 53 | #N/A | #N/A
2022-07-02 04:00 | 7 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 49 | 59 | 67 | 64 | 67 | 67 | 63 | 54 | #N/A | #N/A
2022-07-02 05:00 | 7 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 52 | 59 | 67 | 66 | 68 | 67 | 65 | 55 | #N/A | #N/A
2022-07-02 06:00 | 7 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 56 | 60 | 70 | 68 | 69 | 66 | 67 | 57 | #N/A | #N/A
2022-07-02 07:00 | 7 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 60 | 60 | 73 | 70 | 70 | 69 | 69 | 61 | #N/A | #N/A
2022-07-02 08:00 | 7 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 64 | 59 | 76 | 73 | 71 | 70 | 70 | 64 | #N/A | #N/A
2022-07-02 09:00 | 7 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 67 | 59 | 76 | 76 | 73 | 71 | 69 | 68 | #N/A | #N/A
2022-07-02 10:00 | 7 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 68 | 59 | 78 | 79 | 73 | 70 | 70 | 70 | #N/A | #N/A
2022-07-02 11:00 | 7 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 69 | 58 | 79 | 79 | 77 | 71 | 65 | 71 | #N/A | #N/A
2022-07-02 12:00 | 7 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 70 | 58 | 77 | 79 | 79 | 74 | 64 | 71 | #N/A | #N/A
2022-07-02 13:00 | 7 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 71 | 58 | 76 | 79 | 80 | 74 | 65 | 70 | #N/A | #N/A
2022-07-02 14:00 | 7 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 71 | 59 | 74 | 83 | 81 | 74 | 66 | 69 | #N/A | #N/A
2022-07-02 15:00 | 7 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 71 | 59 | 76 | 83 | 82 | 74 | 68 | 68 | #N/A | #N/A
2022-07-02 16:00 | 7 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 70 | 58 | 76 | 83 | 82 | 74 | 67 | 67 | #N/A | #N/A
2022-07-02 17:00 | 7 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 68 | 58 | 74 | 82 | 81 | 72 | 67 | 66 | #N/A | #N/A
2022-07-02 18:00 | 7 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 66 | 57 | 75 | 80 | 80 | 71 | 68 | 65 | #N/A | #N/A
2022-07-02 19:00 | 7 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 66 | 57 | 72 | 76 | 77 | 71 | 68 | 64 | #N/A | #N/A
2022-07-02 20:00 | 7 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 65 | 57 | 71 | 70 | 76 | 69 | 68 | 64 | #N/A | #N/A
2022-07-02 21:00 | 7 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 62 | 57 | 71 | 66 | 74 | 67 | 67 | 62 | #N/A | #N/A
2022-07-02 22:00 | 7 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 60 | 57 | 70 | 64 | 72 | 65 | 67 | 61 | #N/A | #N/A
2022-07-02 23:00 | 7 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 58 | 58 | 70 | 63 | 71 | 63 | 67 | 61 | #N/A | #N/A
2022-07-03 | 7 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 56 | 58 | 68 | 62 | 70 | 61 | 66 | 61 | #N/A | #N/A
2022-07-03 01:00 | 7 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 54 | 56 | 68 | 61 | 67 | 61 | 66 | 62 | #N/A | #N/A
2022-07-03 02:00 | 7 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 53 | 53 | 66 | 59 | 65 | 59 | 65 | 63 | #N/A | #N/A
2022-07-03 03:00 | 7 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 53 | 51 | 66 | 57 | 63 | 60 | 65 | 63 | #N/A | #N/A
2022-07-03 04:00 | 7 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 53 | 53 | 65 | 57 | 63 | 58 | 65 | 62 | #N/A | #N/A
2022-07-03 05:00 | 7 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 53 | 55 | 67 | 61 | 65 | 59 | 65 | 62 | #N/A | #N/A
2022-07-03 06:00 | 7 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 58 | 57 | 70 | 66 | 71 | 59 | 65 | 60 | #N/A | #N/A
2022-07-03 07:00 | 7 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 60 | 60 | 73 | 71 | 71 | 61 | 67 | 61 | #N/A | #N/A
2022-07-03 08:00 | 7 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 63 | 63 | 75 | 74 | 71 | 64 | 66 | 61 | #N/A | #N/A
2022-07-03 09:00 | 7 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 62 | 66 | 77 | 77 | 77 | 66 | 67 | 62 | #N/A | #N/A
2022-07-03 10:00 | 7 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 56 | 68 | 79 | 82 | 78 | 66 | 68 | 62 | #N/A | #N/A
2022-07-03 11:00 | 7 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 56 | 69 | 79 | 84 | 78 | 70 | 68 | 61 | #N/A | #N/A
2022-07-03 12:00 | 7 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 57 | 71 | 81 | 86 | 80 | 70 | 68 | 61 | #N/A | #N/A
2022-07-03 13:00 | 7 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 59 | 71 | 79 | 87 | 81 | 70 | 70 | 61 | #N/A | #N/A
2022-07-03 14:00 | 7 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 59 | 72 | 77 | 88 | 80 | 72 | 71 | 62 | #N/A | #N/A
2022-07-03 15:00 | 7 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 60 | 72 | 77 | 87 | 80 | 72 | 72 | 61 | #N/A | #N/A
2022-07-03 16:00 | 7 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 60 | 70 | 80 | 87 | 79 | 70 | 72 | 61 | #N/A | #N/A
2022-07-03 17:00 | 7 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 59 | 67 | 79 | 85 | 76 | 70 | 71 | 62 | #N/A | #N/A
2022-07-03 18:00 | 7 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 58 | 65 | 77 | 83 | 74 | 68 | 70 | 61 | #N/A | #N/A
2022-07-03 19:00 | 7 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 57 | 61 | 75 | 81 | 70 | 68 | 69 | 61 | #N/A | #N/A
2022-07-03 20:00 | 7 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 55 | 56 | 72 | 80 | 68 | 66 | 68 | 62 | #N/A | #N/A
2022-07-03 21:00 | 7 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 54 | 52 | 73 | 79 | 67 | 63 | 67 | 62 | #N/A | #N/A
2022-07-03 22:00 | 7 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 52 | 51 | 72 | 77 | 65 | 57 | 67 | 62 | #N/A | #N/A
2022-07-03 23:00 | 7 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 50 | 51 | 72 | 71 | 64 | 55 | 66 | 60 | #N/A | #N/A
2022-07-04 | 7 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 50 | 50 | 70 | 70 | 61 | 54 | 65 | 58 | #N/A | #N/A
2022-07-04 01:00 | 7 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 48 | 49 | 69 | 68 | 59 | 54 | 64 | 56 | #N/A | #N/A
2022-07-04 02:00 | 7 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 49 | 49 | 69 | 65 | 57 | 50 | 64 | 56 | #N/A | #N/A
2022-07-04 03:00 | 7 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 49 | 48 | 68 | 64 | 55 | 51 | 64 | 56 | #N/A | #N/A
2022-07-04 04:00 | 7 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 49 | 49 | 68 | 63 | 55 | 49 | 65 | 56 | #N/A | #N/A
2022-07-04 05:00 | 7 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 48 | 50 | 67 | 67 | 59 | 50 | 66 | 56 | #N/A | #N/A
2022-07-04 06:00 | 7 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 49 | 51 | 69 | 71 | 65 | 55 | 67 | 57 | #N/A | #N/A
2022-07-04 07:00 | 7 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 51 | 52 | 68 | 76 | 69 | 62 | 72 | 58 | #N/A | #N/A
2022-07-04 08:00 | 7 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 54 | 52 | 76 | 80 | 70 | 68 | 73 | 58 | #N/A | #N/A
2022-07-04 09:00 | 7 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 54 | 53 | 79 | 85 | 74 | 71 | 73 | 60 | #N/A | #N/A
2022-07-04 10:00 | 7 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 56 | 56 | 77 | 90 | 75 | 72 | 76 | 62 | #N/A | #N/A
2022-07-04 11:00 | 7 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 57 | 59 | 75 | 91 | 77 | 75 | 77 | 63 | #N/A | #N/A
2022-07-04 12:00 | 7 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 59 | 62 | 78 | 96 | 79 | 77 | 77 | 64 | #N/A | #N/A
2022-07-04 13:00 | 7 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 92 | 63 | 64 | 80 | 98 | 79 | 78 | 76 | 66 | #N/A | #N/A
2022-07-04 14:00 | 7 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 93 | 63 | 65 | 81 | 99 | 80 | 79 | 74 | 68 | #N/A | #N/A
2022-07-04 15:00 | 7 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 95 | 64 | 67 | 80 | 99 | 81 | 80 | 73 | 67 | #N/A | #N/A
2022-07-04 16:00 | 7 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 95 | 64 | 65 | 74 | 98 | 80 | 80 | 72 | 67 | #N/A | #N/A
2022-07-04 17:00 | 7 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 95 | 64 | 62 | 76 | 96 | 78 | 79 | 72 | 67 | #N/A | #N/A
2022-07-04 18:00 | 7 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 92 | 63 | 60 | 74 | 94 | 75 | 77 | 72 | 66 | #N/A | #N/A
2022-07-04 19:00 | 7 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 89 | 61 | 57 | 72 | 91 | 72 | 73 | 71 | 66 | #N/A | #N/A
2022-07-04 20:00 | 7 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 88 | 59 | 53 | 70 | 88 | 70 | 70 | 69 | 64 | #N/A | #N/A
2022-07-04 21:00 | 7 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 58 | 50 | 69 | 85 | 70 | 68 | 68 | 61 | #N/A | #N/A
2022-07-04 22:00 | 7 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 58 | 50 | 69 | 84 | 68 | 65 | 67 | 59 | #N/A | #N/A
2022-07-04 23:00 | 7 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 58 | 49 | 68 | 84 | 68 | 65 | 67 | 59 | #N/A | #N/A
2022-07-05 | 7 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 58 | 49 | 68 | 84 | 68 | 61 | 67 | 59 | #N/A | #N/A
2022-07-05 01:00 | 7 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 57 | 47 | 68 | 82 | 67 | 61 | 65 | 59 | #N/A | #N/A
2022-07-05 02:00 | 7 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 57 | 46 | 68 | 83 | 67 | 63 | 65 | 59 | #N/A | #N/A
2022-07-05 03:00 | 7 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 55 | 44 | 68 | 82 | 67 | 62 | 64 | 58 | #N/A | #N/A
2022-07-05 04:00 | 7 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 55 | 46 | 68 | 82 | 68 | 60 | 63 | 58 | #N/A | #N/A
2022-07-05 05:00 | 7 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 58 | 47 | 68 | 82 | 69 | 60 | 63 | 57 | #N/A | #N/A
2022-07-05 06:00 | 7 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 65 | 49 | 67 | 85 | 72 | 69 | 64 | 58 | #N/A | #N/A
2022-07-05 07:00 | 7 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 68 | 50 | 69 | 88 | 77 | 72 | 65 | 60 | #N/A | #N/A
2022-07-05 08:00 | 7 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 70 | 51 | 73 | 90 | 80 | 76 | 66 | 62 | #N/A | #N/A
2022-07-05 09:00 | 7 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 90 | 72 | 52 | 75 | 92 | 83 | 79 | 68 | 66 | #N/A | #N/A
2022-07-05 10:00 | 7 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 74 | 52 | 77 | 94 | 86 | 82 | 68 | 72 | #N/A | #N/A
2022-07-05 11:00 | 7 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 93 | 76 | 53 | 78 | 95 | 89 | 83 | 69 | 77 | #N/A | #N/A
2022-07-05 12:00 | 7 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 77 | 53 | 79 | 96 | 91 | 85 | 69 | 78 | #N/A | #N/A
2022-07-05 13:00 | 7 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 79 | 54 | 78 | 87 | 92 | 87 | 70 | 79 | #N/A | #N/A
2022-07-05 14:00 | 7 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 80 | 55 | 75 | 74 | 91 | 87 | 71 | 80 | #N/A | #N/A
2022-07-05 15:00 | 7 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 82 | 56 | 77 | 77 | 90 | 87 | 71 | 80 | #N/A | #N/A
2022-07-05 16:00 | 7 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 81 | 56 | 75 | 80 | 89 | 86 | 71 | 82 | #N/A | #N/A
2022-07-05 17:00 | 7 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 79 | 57 | 77 | 81 | 87 | 85 | 69 | 82 | #N/A | #N/A
2022-07-05 18:00 | 7 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 75 | 57 | 73 | 79 | 84 | 83 | 68 | 79 | #N/A | #N/A
2022-07-05 19:00 | 7 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 72 | 52 | 71 | 78 | 81 | 80 | 68 | 73 | #N/A | #N/A
2022-07-05 20:00 | 7 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 70 | 48 | 70 | 78 | 78 | 77 | 67 | 70 | #N/A | #N/A
2022-07-05 21:00 | 7 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 68 | 43 | 70 | 76 | 76 | 74 | 67 | 67 | #N/A | #N/A
2022-07-05 22:00 | 7 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 69 | 42 | 69 | 74 | 76 | 72 | 66 | 65 | #N/A | #N/A
2022-07-05 23:00 | 7 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 66 | 42 | 68 | 71 | 75 | 72 | 67 | 63 | #N/A | #N/A
2022-07-06 | 7 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 41 | 66 | 70 | 74 | 72 | 66 | 63 | #N/A | #N/A
2022-07-06 01:00 | 7 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 41 | 65 | 68 | 73 | 71 | 66 | 61 | #N/A | #N/A
2022-07-06 02:00 | 7 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 62 | 42 | 65 | 67 | 72 | 69 | 66 | 60 | #N/A | #N/A
2022-07-06 03:00 | 7 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 60 | 42 | 63 | 66 | 70 | 69 | 65 | 61 | #N/A | #N/A
2022-07-06 04:00 | 7 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 62 | 45 | 65 | 65 | 70 | 67 | 66 | 59 | #N/A | #N/A
2022-07-06 05:00 | 7 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 61 | 49 | 65 | 67 | 72 | 66 | 67 | 60 | #N/A | #N/A
2022-07-06 06:00 | 7 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 65 | 52 | 66 | 72 | 75 | 70 | 69 | 61 | #N/A | #N/A
2022-07-06 07:00 | 7 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 70 | 56 | 71 | 77 | 81 | 76 | 70 | 61 | #N/A | #N/A
2022-07-06 08:00 | 7 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 76 | 59 | 75 | 78 | 86 | 80 | 72 | 64 | #N/A | #N/A
2022-07-06 09:00 | 7 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 79 | 63 | 78 | 78 | 89 | 83 | 76 | 71 | #N/A | #N/A
2022-07-06 10:00 | 7 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 81 | 64 | 76 | 81 | 91 | 85 | 81 | 76 | #N/A | #N/A
2022-07-06 11:00 | 7 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 83 | 66 | 75 | 82 | 93 | 86 | 82 | 80 | #N/A | #N/A
2022-07-06 12:00 | 7 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 85 | 67 | 75 | 85 | 94 | 87 | 86 | 83 | #N/A | #N/A
2022-07-06 13:00 | 7 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 85 | 67 | 77 | 84 | 95 | 89 | 87 | 84 | #N/A | #N/A
2022-07-06 14:00 | 7 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 86 | 67 | 77 | 84 | 94 | 89 | 85 | 84 | #N/A | #N/A
2022-07-06 15:00 | 7 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 86 | 67 | 77 | 79 | 95 | 89 | 81 | 85 | #N/A | #N/A
2022-07-06 16:00 | 7 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 86 | 66 | 77 | 79 | 94 | 88 | 80 | 85 | #N/A | #N/A
2022-07-06 17:00 | 7 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 85 | 66 | 77 | 78 | 92 | 87 | 81 | 83 | #N/A | #N/A
2022-07-06 18:00 | 7 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 82 | 65 | 76 | 76 | 89 | 85 | 79 | 80 | #N/A | #N/A
2022-07-06 19:00 | 7 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 79 | 60 | 72 | 74 | 85 | 81 | 78 | 79 | #N/A | #N/A
2022-07-06 20:00 | 7 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 77 | 54 | 70 | 73 | 82 | 79 | 76 | 75 | #N/A | #N/A
2022-07-06 21:00 | 7 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 76 | 49 | 66 | 72 | 81 | 75 | 73 | 75 | #N/A | #N/A
2022-07-06 22:00 | 7 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 75 | 48 | 65 | 70 | 79 | 76 | 73 | 68 | #N/A | #N/A
2022-07-06 23:00 | 7 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 68 | 47 | 64 | 69 | 77 | 73 | 73 | 66 | #N/A | #N/A
2022-07-07 | 7 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 67 | 46 | 64 | 67 | 77 | 72 | 69 | 63 | #N/A | #N/A
2022-07-07 01:00 | 7 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 66 | 45 | 63 | 66 | 75 | 72 | 69 | 63 | #N/A | #N/A
2022-07-07 02:00 | 7 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 65 | 43 | 62 | 65 | 76 | 72 | 69 | 62 | #N/A | #N/A
2022-07-07 03:00 | 7 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 65 | 42 | 62 | 63 | 75 | 71 | 68 | 61 | #N/A | #N/A
2022-07-07 04:00 | 7 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 63 | 45 | 62 | 64 | 74 | 70 | 67 | 59 | #N/A | #N/A
2022-07-07 05:00 | 7 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 68 | 47 | 64 | 63 | 78 | 71 | 69 | 61 | #N/A | #N/A
2022-07-07 06:00 | 7 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 70 | 50 | 69 | 65 | 81 | 74 | 69 | 64 | #N/A | #N/A
2022-07-07 07:00 | 7 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 72 | 56 | 75 | 68 | 85 | 78 | 70 | 68 | #N/A | #N/A
2022-07-07 08:00 | 7 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 77 | 61 | 78 | 71 | 89 | 81 | 73 | 71 | #N/A | #N/A
2022-07-07 09:00 | 7 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 81 | 67 | 80 | 74 | 92 | 83 | 72 | 77 | #N/A | #N/A
2022-07-07 10:00 | 7 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 82 | 68 | 80 | 75 | 94 | 84 | 75 | 78 | #N/A | #N/A
2022-07-07 11:00 | 7 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 83 | 70 | 82 | 77 | 95 | 87 | 79 | 81 | #N/A | #N/A
2022-07-07 12:00 | 7 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 85 | 71 | 84 | 78 | 97 | 89 | 82 | 83 | #N/A | #N/A
2022-07-07 13:00 | 7 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 87 | 73 | 85 | 79 | 97 | 89 | 82 | 85 | #N/A | #N/A
2022-07-07 14:00 | 7 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 85 | 75 | 85 | 78 | 98 | 89 | 82 | 86 | #N/A | #N/A
2022-07-07 15:00 | 7 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 85 | 77 | 86 | 78 | 97 | 89 | 83 | 86 | #N/A | #N/A
2022-07-07 16:00 | 7 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 85 | 76 | 85 | 78 | 96 | 83 | 83 | 86 | #N/A | #N/A
2022-07-07 17:00 | 7 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 83 | 74 | 84 | 77 | 94 | 85 | 83 | 85 | #N/A | #N/A
2022-07-07 18:00 | 7 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 81 | 73 | 81 | 75 | 91 | 85 | 81 | 83 | #N/A | #N/A
2022-07-07 19:00 | 7 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 79 | 69 | 77 | 72 | 86 | 82 | 79 | 82 | #N/A | #N/A
2022-07-07 20:00 | 7 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 77 | 64 | 75 | 72 | 85 | 81 | 77 | 80 | #N/A | #N/A
2022-07-07 21:00 | 7 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 75 | 60 | 72 | 72 | 83 | 75 | 76 | 78 | #N/A | #N/A
2022-07-07 22:00 | 7 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 75 | 58 | 72 | 73 | 82 | 76 | 74 | 74 | #N/A | #N/A
2022-07-07 23:00 | 7 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 74 | 55 | 72 | 71 | 82 | 74 | 76 | 73 | #N/A | #N/A
2022-07-08 | 7 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 72 | 53 | 72 | 70 | 79 | 72 | 74 | 70 | #N/A | #N/A
2022-07-08 01:00 | 7 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 71 | 52 | 72 | 70 | 80 | 72 | 76 | 69 | #N/A | #N/A
2022-07-08 02:00 | 7 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 70 | 52 | 72 | 69 | 78 | 72 | 75 | 70 | #N/A | #N/A
2022-07-08 03:00 | 7 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 71 | 51 | 71 | 69 | 76 | 68 | 75 | 68 | #N/A | #N/A
2022-07-08 04:00 | 7 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 71 | 54 | 72 | 69 | 78 | 69 | 74 | 69 | #N/A | #N/A
2022-07-08 05:00 | 7 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 70 | 56 | 74 | 70 | 80 | 68 | 74 | 70 | #N/A | #N/A
2022-07-08 06:00 | 7 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 72 | 59 | 77 | 71 | 81 | 71 | 73 | 72 | #N/A | #N/A
2022-07-08 07:00 | 7 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 76 | 64 | 80 | 73 | 82 | 74 | 72 | 74 | #N/A | #N/A
2022-07-08 08:00 | 7 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 79 | 69 | 82 | 76 | 84 | 80 | 73 | 77 | #N/A | #N/A
2022-07-08 09:00 | 7 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 81 | 74 | 82 | 78 | 86 | 83 | 74 | 79 | #N/A | #N/A
2022-07-08 10:00 | 7 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 84 | 75 | 84 | 79 | 88 | 86 | 76 | 81 | #N/A | #N/A
2022-07-08 11:00 | 7 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 84 | 77 | 84 | 79 | 90 | 88 | 83 | 82 | #N/A | #N/A
2022-07-08 12:00 | 7 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 86 | 78 | 84 | 82 | 92 | 82 | 84 | 82 | #N/A | #N/A
2022-07-08 13:00 | 7 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 82 | 79 | 87 | 84 | 93 | 74 | 87 | 83 | #N/A | #N/A
2022-07-08 14:00 | 7 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 75 | 79 | 87 | 80 | 94 | 85 | 86 | 84 | #N/A | #N/A
2022-07-08 15:00 | 7 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 76 | 80 | 88 | 80 | 93 | 73 | 88 | 83 | #N/A | #N/A
2022-07-08 16:00 | 7 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 77 | 79 | 86 | 79 | 91 | 73 | 85 | 83 | #N/A | #N/A
2022-07-08 17:00 | 7 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 76 | 77 | 86 | 80 | 87 | 72 | 83 | 84 | #N/A | #N/A
2022-07-08 18:00 | 7 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 76 | 76 | 85 | 78 | 86 | 72 | 82 | 82 | #N/A | #N/A
2022-07-08 19:00 | 7 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 74 | 72 | 82 | 77 | 83 | 72 | 78 | 80 | #N/A | #N/A
2022-07-08 20:00 | 7 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 74 | 67 | 80 | 76 | 81 | 72 | 76 | 78 | #N/A | #N/A
2022-07-08 21:00 | 7 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 73 | 63 | 80 | 75 | 82 | 71 | 72 | 77 | #N/A | #N/A
2022-07-08 22:00 | 7 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 72 | 62 | 79 | 75 | 81 | 70 | 70 | 75 | #N/A | #N/A
2022-07-08 23:00 | 7 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 70 | 60 | 78 | 75 | 81 | 75 | 70 | 74 | #N/A | #N/A
2022-07-09 | 7 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 69 | 59 | 79 | 74 | 78 | 70 | 69 | 72 | #N/A | #N/A
2022-07-09 01:00 | 7 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 67 | 58 | 80 | 75 | 78 | 70 | 68 | 71 | #N/A | #N/A
2022-07-09 02:00 | 7 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 67 | 57 | 79 | 75 | 81 | 70 | 67 | 69 | #N/A | #N/A
2022-07-09 03:00 | 7 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 66 | 56 | 78 | 76 | 78 | 71 | 65 | 68 | #N/A | #N/A
2022-07-09 04:00 | 7 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 65 | 58 | 77 | 75 | 78 | 71 | 65 | 67 | #N/A | #N/A
2022-07-09 05:00 | 7 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 68 | 59 | 77 | 75 | 78 | 71 | 66 | 66 | #N/A | #N/A
2022-07-09 06:00 | 7 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 72 | 61 | 79 | 77 | 79 | 71 | 68 | 71 | #N/A | #N/A
2022-07-09 07:00 | 7 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 75 | 66 | 80 | 79 | 82 | 71 | 69 | 75 | #N/A | #N/A
2022-07-09 08:00 | 7 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 78 | 72 | 81 | 83 | 81 | 71 | 70 | 78 | #N/A | #N/A
2022-07-09 09:00 | 7 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 77 | 77 | 82 | 86 | 81 | 71 | 72 | 80 | #N/A | #N/A
2022-07-09 10:00 | 7 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 87 | 76 | 78 | 81 | 89 | 80 | 71 | 74 | 82 | #N/A | #N/A
2022-07-09 11:00 | 7 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 89 | 78 | 79 | 83 | 89 | 80 | 74 | 77 | 83 | #N/A | #N/A
2022-07-09 12:00 | 7 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 91 | 78 | 80 | 84 | 89 | 84 | 75 | 78 | 83 | #N/A | #N/A
2022-07-09 13:00 | 7 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 94 | 78 | 80 | 86 | 91 | 85 | 74 | 79 | 84 | #N/A | #N/A
2022-07-09 14:00 | 7 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 79 | 79 | 84 | 94 | 85 | 73 | 81 | 84 | #N/A | #N/A
2022-07-09 15:00 | 7 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 80 | 79 | 79 | 86 | 85 | 76 | 81 | 84 | #N/A | #N/A
2022-07-09 16:00 | 7 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 80 | 77 | 76 | 84 | 76 | 76 | 80 | 84 | #N/A | #N/A
2022-07-09 17:00 | 7 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 79 | 76 | 73 | 83 | 73 | 76 | 79 | 83 | #N/A | #N/A
2022-07-09 18:00 | 7 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 75 | 74 | 73 | 81 | 73 | 75 | 77 | 81 | #N/A | #N/A
2022-07-09 19:00 | 7 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 73 | 72 | 74 | 79 | 72 | 72 | 72 | 77 | #N/A | #N/A
2022-07-09 20:00 | 7 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 72 | 70 | 75 | 78 | 72 | 70 | 70 | 75 | #N/A | #N/A
2022-07-09 21:00 | 7 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 71 | 68 | 74 | 77 | 71 | 68 | 66 | 73 | #N/A | #N/A
2022-07-09 22:00 | 7 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 67 | 74 | 76 | 71 | 66 | 63 | 72 | #N/A | #N/A
2022-07-09 23:00 | 7 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 69 | 66 | 73 | 74 | 71 | 64 | 62 | 71 | #N/A | #N/A
2022-07-10 | 7 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 67 | 65 | 72 | 73 | 72 | 61 | 60 | 70 | #N/A | #N/A
2022-07-10 01:00 | 7 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 66 | 65 | 68 | 73 | 71 | 61 | 57 | 68 | #N/A | #N/A
2022-07-10 02:00 | 7 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 66 | 65 | 62 | 72 | 70 | 60 | 56 | 67 | #N/A | #N/A
2022-07-10 03:00 | 7 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 66 | 65 | 60 | 73 | 68 | 56 | 54 | 67 | #N/A | #N/A
2022-07-10 04:00 | 7 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 66 | 65 | 57 | 74 | 66 | 58 | 54 | 66 | #N/A | #N/A
2022-07-10 05:00 | 7 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 67 | 65 | 60 | 75 | 67 | 59 | 56 | 66 | #N/A | #N/A
2022-07-10 06:00 | 7 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 68 | 65 | 67 | 77 | 69 | 62 | 61 | 68 | #N/A | #N/A
2022-07-10 07:00 | 7 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 74 | 65 | 72 | 79 | 72 | 66 | 69 | 69 | #N/A | #N/A
2022-07-10 08:00 | 7 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 78 | 65 | 73 | 80 | 75 | 69 | 71 | 73 | #N/A | #N/A
2022-07-10 09:00 | 7 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 82 | 65 | 74 | 84 | 78 | 70 | 76 | 77 | #N/A | #N/A
2022-07-10 10:00 | 7 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 84 | 66 | 75 | 86 | 81 | 72 | 76 | 80 | #N/A | #N/A
2022-07-10 11:00 | 7 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 83 | 68 | 76 | 85 | 81 | 74 | 79 | 83 | #N/A | #N/A
2022-07-10 12:00 | 7 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 80 | 69 | 75 | 86 | 83 | 76 | 79 | 88 | #N/A | #N/A
2022-07-10 13:00 | 7 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 87 | 72 | 69 | 76 | 76 | 84 | 76 | 82 | 82 | #N/A | #N/A
2022-07-10 14:00 | 7 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 76 | 69 | 78 | 76 | 84 | 76 | 83 | 84 | #N/A | #N/A
2022-07-10 15:00 | 7 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 75 | 69 | 80 | 74 | 84 | 77 | 82 | 85 | #N/A | #N/A
2022-07-10 16:00 | 7 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 74 | 69 | 78 | 77 | 83 | 76 | 79 | 85 | #N/A | #N/A
2022-07-10 17:00 | 7 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 70 | 68 | 78 | 77 | 82 | 73 | 79 | 84 | #N/A | #N/A
2022-07-10 18:00 | 7 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 68 | 68 | 77 | 77 | 80 | 72 | 78 | 80 | #N/A | #N/A
2022-07-10 19:00 | 7 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 64 | 68 | 71 | 74 | 76 | 72 | 73 | 77 | #N/A | #N/A
2022-07-10 20:00 | 7 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 61 | 67 | 67 | 73 | 75 | 69 | 69 | 74 | #N/A | #N/A
2022-07-10 21:00 | 7 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 59 | 67 | 65 | 72 | 72 | 67 | 66 | 72 | #N/A | #N/A
2022-07-10 22:00 | 7 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 56 | 66 | 63 | 71 | 73 | 66 | 64 | 68 | #N/A | #N/A
2022-07-10 23:00 | 7 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 55 | 66 | 62 | 70 | 69 | 63 | 62 | 65 | #N/A | #N/A
2022-07-11 | 7 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 54 | 65 | 60 | 70 | 68 | 63 | 60 | 63 | #N/A | #N/A
2022-07-11 01:00 | 7 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 54 | 65 | 60 | 70 | 69 | 65 | 59 | 59 | #N/A | #N/A
2022-07-11 02:00 | 7 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 52 | 66 | 60 | 70 | 70 | 64 | 57 | 58 | #N/A | #N/A
2022-07-11 03:00 | 7 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 51 | 66 | 59 | 70 | 67 | 64 | 56 | 55 | #N/A | #N/A
2022-07-11 04:00 | 7 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 50 | 66 | 59 | 70 | 64 | 65 | 55 | 56 | #N/A | #N/A
2022-07-11 05:00 | 7 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 53 | 67 | 61 | 69 | 68 | 63 | 58 | 58 | #N/A | #N/A
2022-07-11 06:00 | 7 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 56 | 67 | 64 | 65 | 72 | 63 | 62 | 60 | #N/A | #N/A
2022-07-11 07:00 | 7 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 58 | 69 | 70 | 64 | 75 | 64 | 67 | 64 | #N/A | #N/A
2022-07-11 08:00 | 7 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 61 | 71 | 76 | 64 | 77 | 63 | 72 | 67 | #N/A | #N/A
2022-07-11 09:00 | 7 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 60 | 73 | 78 | 64 | 76 | 65 | 75 | 68 | #N/A | #N/A
2022-07-11 10:00 | 7 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 62 | 75 | 79 | 64 | 74 | 66 | 76 | 70 | #N/A | #N/A
2022-07-11 11:00 | 7 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 63 | 76 | 80 | 64 | 76 | 70 | 77 | 72 | #N/A | #N/A
2022-07-11 12:00 | 7 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 64 | 78 | 80 | 64 | 77 | 72 | 81 | 73 | #N/A | #N/A
2022-07-11 13:00 | 7 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 65 | 79 | 82 | 66 | 76 | 76 | 82 | 73 | #N/A | #N/A
2022-07-11 14:00 | 7 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 65 | 79 | 81 | 66 | 75 | 78 | 81 | 74 | #N/A | #N/A
2022-07-11 15:00 | 7 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 65 | 80 | 80 | 66 | 73 | 79 | 81 | 75 | #N/A | #N/A
2022-07-11 16:00 | 7 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 64 | 79 | 79 | 67 | 70 | 81 | 82 | 75 | #N/A | #N/A
2022-07-11 17:00 | 7 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 63 | 77 | 80 | 67 | 71 | 76 | 80 | 74 | #N/A | #N/A
2022-07-11 18:00 | 7 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 62 | 76 | 75 | 67 | 70 | 75 | 78 | 72 | #N/A | #N/A
2022-07-11 19:00 | 7 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 58 | 73 | 72 | 66 | 69 | 70 | 74 | 68 | #N/A | #N/A
2022-07-11 20:00 | 7 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 57 | 71 | 70 | 65 | 67 | 70 | 69 | 61 | #N/A | #N/A
2022-07-11 21:00 | 7 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 56 | 68 | 70 | 65 | 68 | 70 | 69 | 59 | #N/A | #N/A
2022-07-11 22:00 | 7 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 55 | 67 | 70 | 65 | 68 | 68 | 66 | 57 | #N/A | #N/A
2022-07-11 23:00 | 7 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 52 | 67 | 69 | 65 | 68 | 68 | 63 | 56 | #N/A | #N/A
2022-07-12 | 7 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 51 | 66 | 69 | 65 | 69 | 68 | 60 | 53 | #N/A | #N/A
2022-07-12 01:00 | 7 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 50 | 66 | 69 | 64 | 69 | 70 | 58 | 52 | #N/A | #N/A
2022-07-12 02:00 | 7 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 51 | 65 | 67 | 64 | 70 | 70 | 58 | 52 | #N/A | #N/A
2022-07-12 03:00 | 7 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 50 | 65 | 70 | 63 | 71 | 70 | 56 | 51 | #N/A | #N/A
2022-07-12 04:00 | 7 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 50 | 66 | 66 | 63 | 70 | 70 | 54 | 51 | #N/A | #N/A
2022-07-12 05:00 | 7 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 49 | 67 | 68 | 63 | 70 | 70 | 57 | 53 | #N/A | #N/A
2022-07-12 06:00 | 7 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 54 | 68 | 71 | 63 | 70 | 70 | 62 | 56 | #N/A | #N/A
2022-07-12 07:00 | 7 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 59 | 72 | 78 | 63 | 72 | 71 | 67 | 60 | #N/A | #N/A
2022-07-12 08:00 | 7 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 63 | 75 | 82 | 64 | 74 | 74 | 72 | 65 | #N/A | #N/A
2022-07-12 09:00 | 7 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 69 | 79 | 84 | 64 | 78 | 75 | 78 | 69 | #N/A | #N/A
2022-07-12 10:00 | 7 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 70 | 81 | 85 | 65 | 82 | 76 | 81 | 72 | #N/A | #N/A
2022-07-12 11:00 | 7 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 72 | 82 | 83 | 65 | 87 | 74 | 83 | 75 | #N/A | #N/A
2022-07-12 12:00 | 7 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 73 | 84 | 83 | 66 | 87 | 77 | 81 | 77 | #N/A | #N/A
2022-07-12 13:00 | 7 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 74 | 84 | 84 | 66 | 85 | 76 | 82 | 78 | #N/A | #N/A
2022-07-12 14:00 | 7 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 75 | 84 | 80 | 65 | 84 | 79 | 83 | 79 | #N/A | #N/A
2022-07-12 15:00 | 7 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 75 | 84 | 81 | 64 | 89 | 79 | 83 | 80 | #N/A | #N/A
2022-07-12 16:00 | 7 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 74 | 83 | 81 | 62 | 89 | 81 | 83 | 80 | #N/A | #N/A
2022-07-12 17:00 | 7 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 74 | 81 | 81 | 62 | 87 | 80 | 82 | 80 | #N/A | #N/A
2022-07-12 18:00 | 7 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 71 | 80 | 78 | 61 | 86 | 78 | 79 | 77 | #N/A | #N/A
2022-07-12 19:00 | 7 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 68 | 76 | 77 | 60 | 80 | 77 | 78 | 73 | #N/A | #N/A
2022-07-12 20:00 | 7 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 68 | 71 | 75 | 60 | 77 | 74 | 77 | 69 | #N/A | #N/A
2022-07-12 21:00 | 7 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 66 | 67 | 74 | 60 | 76 | 72 | 76 | 63 | #N/A | #N/A
2022-07-12 22:00 | 7 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 65 | 66 | 74 | 60 | 74 | 70 | 72 | 61 | #N/A | #N/A
2022-07-12 23:00 | 7 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 62 | 64 | 74 | 60 | 73 | 70 | 73 | 59 | #N/A | #N/A
2022-07-13 | 7 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 59 | 63 | 75 | 61 | 73 | 67 | 72 | 58 | #N/A | #N/A
2022-07-13 01:00 | 7 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 58 | 63 | 75 | 61 | 72 | 70 | 71 | 56 | #N/A | #N/A
2022-07-13 02:00 | 7 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 57 | 62 | 75 | 60 | 72 | 70 | 70 | 55 | #N/A | #N/A
2022-07-13 03:00 | 7 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 56 | 62 | 74 | 60 | 72 | 71 | 71 | 54 | #N/A | #N/A
2022-07-13 04:00 | 7 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 56 | 64 | 74 | 59 | 71 | 71 | 70 | 53 | #N/A | #N/A
2022-07-13 05:00 | 7 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 58 | 66 | 74 | 59 | 70 | 71 | 68 | 55 | #N/A | #N/A
2022-07-13 06:00 | 7 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 60 | 68 | 76 | 59 | 72 | 72 | 67 | 55 | #N/A | #N/A
2022-07-13 07:00 | 7 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 64 | 72 | 77 | 59 | 74 | 74 | 68 | 60 | #N/A | #N/A
2022-07-13 08:00 | 7 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 68 | 77 | 77 | 60 | 75 | 76 | 69 | 69 | #N/A | #N/A
2022-07-13 09:00 | 7 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 71 | 81 | 80 | 61 | 81 | 75 | 70 | 72 | #N/A | #N/A
2022-07-13 10:00 | 7 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 73 | 82 | 81 | 63 | 85 | 74 | 71 | 76 | #N/A | #N/A
2022-07-13 11:00 | 7 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 75 | 84 | 80 | 63 | 93 | 75 | 73 | 79 | #N/A | #N/A
2022-07-13 12:00 | 7 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 77 | 85 | 81 | 63 | 92 | 73 | 74 | 81 | #N/A | #N/A
2022-07-13 13:00 | 7 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 70 | 84 | 82 | 63 | 91 | 74 | 75 | 82 | #N/A | #N/A
2022-07-13 14:00 | 7 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 78 | 84 | 82 | 63 | 83 | 76 | 79 | 83 | #N/A | #N/A
2022-07-13 15:00 | 7 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 78 | 83 | 82 | 64 | 89 | 77 | 79 | 83 | #N/A | #N/A
2022-07-13 16:00 | 7 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 75 | 81 | 81 | 64 | 90 | 80 | 76 | 82 | #N/A | #N/A
2022-07-13 17:00 | 7 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 74 | 80 | 80 | 64 | 78 | 79 | 74 | 80 | #N/A | #N/A
2022-07-13 18:00 | 7 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 73 | 78 | 78 | 62 | 80 | 78 | 73 | 79 | #N/A | #N/A
2022-07-13 19:00 | 7 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 72 | 77 | 77 | 62 | 78 | 74 | 73 | 79 | #N/A | #N/A
2022-07-13 20:00 | 7 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 71 | 76 | 76 | 61 | 78 | 71 | 72 | 78 | #N/A | #N/A
2022-07-13 21:00 | 7 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 70 | 75 | 75 | 61 | 79 | 68 | 71 | 78 | #N/A | #N/A
2022-07-13 22:00 | 7 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 70 | 75 | 74 | 61 | 79 | 68 | 71 | 78 | #N/A | #N/A
2022-07-13 23:00 | 7 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 69 | 74 | 73 | 61 | 79 | 69 | 70 | 76 | #N/A | #N/A
2022-07-14 | 7 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 69 | 74 | 73 | 62 | 78 | 69 | 69 | 74 | #N/A | #N/A
2022-07-14 01:00 | 7 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 68 | 72 | 72 | 62 | 76 | 70 | 68 | 73 | #N/A | #N/A
2022-07-14 02:00 | 7 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 68 | 71 | 71 | 62 | 73 | 68 | 68 | 72 | #N/A | #N/A
2022-07-14 03:00 | 7 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 67 | 69 | 69 | 62 | 70 | 67 | 67 | 71 | #N/A | #N/A
2022-07-14 04:00 | 7 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 66 | 70 | 68 | 62 | 70 | 65 | 66 | 69 | #N/A | #N/A
2022-07-14 05:00 | 7 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 66 | 71 | 69 | 62 | 74 | 64 | 66 | 70 | #N/A | #N/A
2022-07-14 06:00 | 7 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 68 | 72 | 72 | 62 | 77 | 69 | 65 | 71 | #N/A | #N/A
2022-07-14 07:00 | 7 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 69 | 75 | 72 | 63 | 80 | 72 | 68 | 71 | #N/A | #N/A
2022-07-14 08:00 | 7 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 70 | 79 | 73 | 64 | 81 | 74 | 73 | 75 | #N/A | #N/A
2022-07-14 09:00 | 7 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 72 | 82 | 74 | 65 | 84 | 76 | 74 | 76 | #N/A | #N/A
2022-07-14 10:00 | 7 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 74 | 84 | 75 | 66 | 85 | 75 | 76 | 78 | #N/A | #N/A
2022-07-14 11:00 | 7 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 75 | 85 | 76 | 67 | 86 | 77 | 78 | 79 | #N/A | #N/A
2022-07-14 12:00 | 7 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 77 | 87 | 76 | 68 | 89 | 75 | 78 | 80 | #N/A | #N/A
2022-07-14 13:00 | 7 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 78 | 87 | 77 | 70 | 89 | 77 | 82 | 82 | #N/A | #N/A
2022-07-14 14:00 | 7 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 78 | 87 | 77 | 72 | 87 | 78 | 80 | 82 | #N/A | #N/A
2022-07-14 15:00 | 7 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 76 | 87 | 76 | 71 | 86 | 79 | 81 | 82 | #N/A | #N/A
2022-07-14 16:00 | 7 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 75 | 85 | 77 | 70 | 85 | 78 | 82 | 80 | #N/A | #N/A
2022-07-14 17:00 | 7 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 74 | 83 | 76 | 71 | 84 | 77 | 80 | 79 | #N/A | #N/A
2022-07-14 18:00 | 7 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 74 | 81 | 75 | 71 | 82 | 74 | 77 | 79 | #N/A | #N/A
2022-07-14 19:00 | 7 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 72 | 79 | 71 | 72 | 80 | 73 | 73 | 71 | #N/A | #N/A
2022-07-14 20:00 | 7 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 70 | 78 | 70 | 72 | 78 | 68 | 70 | 67 | #N/A | #N/A
2022-07-14 21:00 | 7 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 69 | 76 | 70 | 73 | 76 | 67 | 69 | 67 | #N/A | #N/A
2022-07-14 22:00 | 7 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 69 | 75 | 68 | 73 | 75 | 65 | 64 | 67 | #N/A | #N/A
2022-07-14 23:00 | 7 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 68 | 75 | 67 | 73 | 72 | 63 | 62 | 67 | #N/A | #N/A
2022-07-15 | 7 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 67 | 74 | 62 | 74 | 70 | 63 | 58 | 68 | #N/A | #N/A
2022-07-15 01:00 | 7 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 66 | 73 | 60 | 73 | 67 | 63 | 58 | 67 | #N/A | #N/A
2022-07-15 02:00 | 7 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 66 | 71 | 58 | 72 | 66 | 63 | 56 | 66 | #N/A | #N/A
2022-07-15 03:00 | 7 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 66 | 70 | 56 | 73 | 65 | 62 | 55 | 64 | #N/A | #N/A
2022-07-15 04:00 | 7 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 66 | 71 | 55 | 73 | 65 | 61 | 54 | 64 | #N/A | #N/A
2022-07-15 05:00 | 7 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 66 | 72 | 59 | 74 | 67 | 59 | 56 | 65 | #N/A | #N/A
2022-07-15 06:00 | 7 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 67 | 73 | 66 | 75 | 71 | 61 | 62 | 65 | #N/A | #N/A
2022-07-15 07:00 | 7 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 69 | 76 | 72 | 76 | 75 | 66 | 68 | 66 | #N/A | #N/A
2022-07-15 08:00 | 7 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 70 | 80 | 73 | 78 | 78 | 69 | 72 | 67 | #N/A | #N/A
2022-07-15 09:00 | 7 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 72 | 83 | 75 | 81 | 80 | 72 | 76 | 71 | #N/A | #N/A
2022-07-15 10:00 | 7 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 76 | 84 | 75 | 82 | 83 | 74 | 81 | 75 | #N/A | #N/A
2022-07-15 11:00 | 7 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 76 | 86 | 75 | 85 | 84 | 76 | 81 | 78 | #N/A | #N/A
2022-07-15 12:00 | 7 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 78 | 87 | 76 | 83 | 86 | 78 | 83 | 80 | #N/A | #N/A
2022-07-15 13:00 | 7 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 80 | 87 | 77 | 80 | 84 | 79 | 86 | 83 | #N/A | #N/A
2022-07-15 14:00 | 7 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 81 | 88 | 77 | 84 | 86 | 79 | 85 | 84 | #N/A | #N/A
2022-07-15 15:00 | 7 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 81 | 88 | 79 | 79 | 84 | 81 | 85 | 84 | #N/A | #N/A
2022-07-15 16:00 | 7 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 80 | 85 | 77 | 80 | 87 | 80 | 85 | 84 | #N/A | #N/A
2022-07-15 17:00 | 7 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 79 | 82 | 75 | 80 | 84 | 79 | 84 | 84 | #N/A | #N/A
2022-07-15 18:00 | 7 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 77 | 79 | 73 | 79 | 81 | 79 | 82 | 81 | #N/A | #N/A
2022-07-15 19:00 | 7 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 74 | 77 | 71 | 75 | 77 | 78 | 77 | 78 | #N/A | #N/A
2022-07-15 20:00 | 7 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 72 | 76 | 70 | 73 | 75 | 74 | 74 | 74 | #N/A | #N/A
2022-07-15 21:00 | 7 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 71 | 74 | 69 | 73 | 74 | 70 | 69 | 71 | #N/A | #N/A
2022-07-15 22:00 | 7 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 70 | 72 | 67 | 72 | 72 | 68 | 67 | 71 | #N/A | #N/A
2022-07-15 23:00 | 7 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 69 | 69 | 67 | 72 | 72 | 67 | 65 | 68 | #N/A | #N/A
2022-07-16 | 7 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 69 | 67 | 66 | 70 | 71 | 66 | 64 | 67 | #N/A | #N/A
2022-07-16 01:00 | 7 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 67 | 66 | 66 | 68 | 73 | 66 | 61 | 67 | #N/A | #N/A
2022-07-16 02:00 | 7 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 66 | 66 | 66 | 66 | 72 | 69 | 60 | 67 | #N/A | #N/A
2022-07-16 03:00 | 7 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 66 | 65 | 66 | 66 | 68 | 68 | 58 | 66 | #N/A | #N/A
2022-07-16 04:00 | 7 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 65 | 66 | 66 | 65 | 68 | 68 | 59 | 66 | #N/A | #N/A
2022-07-16 05:00 | 7 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 65 | 67 | 66 | 66 | 68 | 71 | 60 | 66 | #N/A | #N/A
2022-07-16 06:00 | 7 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 69 | 68 | 68 | 69 | 71 | 71 | 63 | 67 | #N/A | #N/A
2022-07-16 07:00 | 7 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 72 | 71 | 68 | 72 | 77 | 70 | 70 | 70 | #N/A | #N/A
2022-07-16 08:00 | 7 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 74 | 75 | 69 | 75 | 80 | 72 | 75 | 72 | #N/A | #N/A
2022-07-16 09:00 | 7 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 77 | 78 | 71 | 76 | 81 | 72 | 80 | 75 | #N/A | #N/A
2022-07-16 10:00 | 7 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 78 | 79 | 75 | 77 | 82 | 76 | 84 | 77 | #N/A | #N/A
2022-07-16 11:00 | 7 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 79 | 79 | 76 | 80 | 84 | 75 | 87 | 80 | #N/A | #N/A
2022-07-16 12:00 | 7 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 80 | 80 | 75 | 81 | 84 | 77 | 87 | 82 | #N/A | #N/A
2022-07-16 13:00 | 7 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 81 | 81 | 74 | 83 | 82 | 77 | 88 | 82 | #N/A | #N/A
2022-07-16 14:00 | 7 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 77 | 81 | 74 | 84 | 80 | 77 | 89 | 83 | #N/A | #N/A
2022-07-16 15:00 | 7 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 76 | 82 | 74 | 83 | 80 | 79 | 89 | 82 | #N/A | #N/A
2022-07-16 16:00 | 7 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 69 | 81 | 73 | 83 | 78 | 81 | 88 | 74 | #N/A | #N/A
2022-07-16 17:00 | 7 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 67 | 79 | 73 | 82 | 75 | 79 | 87 | 69 | #N/A | #N/A
2022-07-16 18:00 | 7 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 65 | 78 | 73 | 80 | 72 | 75 | 86 | 70 | #N/A | #N/A
2022-07-16 19:00 | 7 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 65 | 75 | 69 | 76 | 71 | 77 | 80 | 68 | #N/A | #N/A
2022-07-16 20:00 | 7 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 64 | 73 | 64 | 74 | 71 | 75 | 77 | 67 | #N/A | #N/A
2022-07-16 21:00 | 7 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 64 | 70 | 63 | 68 | 71 | 74 | 75 | 67 | #N/A | #N/A
2022-07-16 22:00 | 7 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 63 | 67 | 62 | 69 | 71 | 72 | 74 | 66 | #N/A | #N/A
2022-07-16 23:00 | 7 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 63 | 64 | 61 | 68 | 71 | 72 | 71 | 66 | #N/A | #N/A
2022-07-17 | 7 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 63 | 61 | 60 | 66 | 72 | 71 | 71 | 66 | #N/A | #N/A
2022-07-17 01:00 | 7 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 64 | 60 | 60 | 66 | 72 | 70 | 69 | 66 | #N/A | #N/A
2022-07-17 02:00 | 7 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 63 | 58 | 60 | 65 | 72 | 70 | 65 | 66 | #N/A | #N/A
2022-07-17 03:00 | 7 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 63 | 57 | 59 | 64 | 71 | 71 | 65 | 66 | #N/A | #N/A
2022-07-17 04:00 | 7 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 62 | 59 | 59 | 63 | 71 | 70 | 65 | 66 | #N/A | #N/A
2022-07-17 05:00 | 7 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 62 | 61 | 61 | 64 | 71 | 71 | 66 | 65 | #N/A | #N/A
2022-07-17 06:00 | 7 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 62 | 63 | 66 | 69 | 72 | 72 | 69 | 66 | #N/A | #N/A
2022-07-17 07:00 | 7 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 63 | 66 | 72 | 73 | 73 | 76 | 75 | 68 | #N/A | #N/A
2022-07-17 08:00 | 7 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 63 | 68 | 75 | 76 | 75 | 80 | 79 | 71 | #N/A | #N/A
2022-07-17 09:00 | 7 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 65 | 71 | 76 | 81 | 77 | 83 | 84 | 71 | #N/A | #N/A
2022-07-17 10:00 | 7 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 66 | 72 | 78 | 83 | 80 | 85 | 87 | 73 | #N/A | #N/A
2022-07-17 11:00 | 7 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 68 | 74 | 77 | 84 | 83 | 87 | 88 | 76 | #N/A | #N/A
2022-07-17 12:00 | 7 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 69 | 75 | 79 | 87 | 81 | 89 | 89 | 78 | #N/A | #N/A
2022-07-17 13:00 | 7 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 71 | 76 | 80 | 87 | 83 | 90 | 90 | 77 | #N/A | #N/A
2022-07-17 14:00 | 7 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 87 | 73 | 76 | 80 | 87 | 84 | 91 | 91 | 79 | #N/A | #N/A
2022-07-17 15:00 | 7 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 74 | 77 | 81 | 87 | 85 | 91 | 91 | 80 | #N/A | #N/A
2022-07-17 16:00 | 7 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 74 | 75 | 80 | 87 | 84 | 90 | 91 | 81 | #N/A | #N/A
2022-07-17 17:00 | 7 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 72 | 72 | 80 | 86 | 84 | 88 | 89 | 79 | #N/A | #N/A
2022-07-17 18:00 | 7 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 70 | 70 | 78 | 83 | 81 | 87 | 87 | 78 | #N/A | #N/A
2022-07-17 19:00 | 7 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 67 | 68 | 72 | 79 | 79 | 83 | 84 | 76 | #N/A | #N/A
2022-07-17 20:00 | 7 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 66 | 67 | 67 | 78 | 79 | 82 | 82 | 72 | #N/A | #N/A
2022-07-17 21:00 | 7 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 65 | 65 | 66 | 76 | 77 | 79 | 80 | 70 | #N/A | #N/A
2022-07-17 22:00 | 7 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 64 | 63 | 66 | 72 | 77 | 78 | 79 | 68 | #N/A | #N/A
2022-07-17 23:00 | 7 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 62 | 62 | 66 | 70 | 75 | 76 | 75 | 68 | #N/A | #N/A
2022-07-18 | 7 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 61 | 60 | 69 | 69 | 74 | 76 | 76 | 68 | #N/A | #N/A
2022-07-18 01:00 | 7 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 61 | 59 | 68 | 68 | 74 | 76 | 74 | 67 | #N/A | #N/A
2022-07-18 02:00 | 7 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 58 | 59 | 65 | 66 | 74 | 73 | 70 | 67 | #N/A | #N/A
2022-07-18 03:00 | 7 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 58 | 65 | 66 | 73 | 74 | 68 | 65 | #N/A | #N/A
2022-07-18 04:00 | 7 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 58 | 59 | 65 | 65 | 73 | 74 | 66 | 65 | #N/A | #N/A
2022-07-18 05:00 | 7 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 60 | 66 | 66 | 74 | 74 | 70 | 64 | #N/A | #N/A
2022-07-18 06:00 | 7 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 61 | 61 | 70 | 70 | 77 | 76 | 74 | 64 | #N/A | #N/A
2022-07-18 07:00 | 7 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 65 | 64 | 74 | 75 | 81 | 80 | 79 | 66 | #N/A | #N/A
2022-07-18 08:00 | 7 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 67 | 67 | 78 | 79 | 83 | 84 | 82 | 68 | #N/A | #N/A
2022-07-18 09:00 | 7 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 71 | 70 | 80 | 82 | 84 | 84 | 85 | 73 | #N/A | #N/A
2022-07-18 10:00 | 7 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 72 | 70 | 82 | 84 | 87 | 87 | 88 | 78 | #N/A | #N/A
2022-07-18 11:00 | 7 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 74 | 70 | 82 | 89 | 88 | 89 | 90 | 80 | #N/A | #N/A
2022-07-18 12:00 | 7 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 76 | 70 | 82 | 88 | 88 | 89 | 92 | 80 | #N/A | #N/A
2022-07-18 13:00 | 7 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 90 | 77 | 72 | 83 | 89 | 91 | 90 | 92 | 82 | #N/A | #N/A
2022-07-18 14:00 | 7 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 78 | 74 | 83 | 90 | 90 | 90 | 93 | 84 | #N/A | #N/A
2022-07-18 15:00 | 7 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 78 | 76 | 85 | 89 | 91 | 90 | 93 | 84 | #N/A | #N/A
2022-07-18 16:00 | 7 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 78 | 74 | 85 | 89 | 89 | 90 | 93 | 84 | #N/A | #N/A
2022-07-18 17:00 | 7 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 77 | 72 | 83 | 87 | 87 | 88 | 91 | 83 | #N/A | #N/A
2022-07-18 18:00 | 7 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 73 | 70 | 81 | 85 | 84 | 87 | 90 | 79 | #N/A | #N/A
2022-07-18 19:00 | 7 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 73 | 66 | 77 | 83 | 81 | 83 | 86 | 76 | #N/A | #N/A
2022-07-18 20:00 | 7 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 72 | 63 | 75 | 81 | 79 | 79 | 83 | 72 | #N/A | #N/A
2022-07-18 21:00 | 7 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 70 | 59 | 74 | 80 | 78 | 79 | 80 | 70 | #N/A | #N/A
2022-07-18 22:00 | 7 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 68 | 57 | 74 | 76 | 77 | 79 | 77 | 67 | #N/A | #N/A
2022-07-18 23:00 | 7 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 67 | 55 | 74 | 75 | 77 | 79 | 76 | 66 | #N/A | #N/A
2022-07-19 | 7 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 67 | 53 | 74 | 75 | 76 | 78 | 74 | 64 | #N/A | #N/A
2022-07-19 01:00 | 7 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 65 | 53 | 73 | 72 | 73 | 78 | 73 | 63 | #N/A | #N/A
2022-07-19 02:00 | 7 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 64 | 53 | 74 | 72 | 73 | 75 | 71 | 63 | #N/A | #N/A
2022-07-19 03:00 | 7 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 61 | 53 | 73 | 71 | 74 | 74 | 70 | 62 | #N/A | #N/A
2022-07-19 04:00 | 7 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 63 | 55 | 74 | 69 | 74 | 74 | 69 | 61 | #N/A | #N/A
2022-07-19 05:00 | 7 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 64 | 57 | 74 | 71 | 73 | 72 | 70 | 62 | #N/A | #N/A
2022-07-19 06:00 | 7 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 66 | 59 | 75 | 73 | 73 | 76 | 73 | 62 | #N/A | #N/A
2022-07-19 07:00 | 7 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 71 | 63 | 80 | 79 | 74 | 77 | 80 | 65 | #N/A | #N/A
2022-07-19 08:00 | 7 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 74 | 68 | 81 | 82 | 75 | 82 | 84 | 69 | #N/A | #N/A
2022-07-19 09:00 | 7 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 77 | 72 | 81 | 84 | 77 | 83 | 89 | 74 | #N/A | #N/A
2022-07-19 10:00 | 7 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 80 | 74 | 83 | 86 | 77 | 82 | 91 | 80 | #N/A | #N/A
2022-07-19 11:00 | 7 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 81 | 75 | 84 | 87 | 79 | 85 | 93 | 84 | #N/A | #N/A
2022-07-19 12:00 | 7 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 82 | 77 | 86 | 90 | 76 | 82 | 92 | 85 | #N/A | #N/A
2022-07-19 13:00 | 7 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 90 | 84 | 77 | 91 | 90 | 81 | 81 | 92 | 86 | #N/A | #N/A
2022-07-19 14:00 | 7 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 90 | 83 | 78 | 86 | 89 | 78 | 77 | 91 | 87 | #N/A | #N/A
2022-07-19 15:00 | 7 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 90 | 83 | 78 | 84 | 89 | 75 | 81 | 83 | 87 | #N/A | #N/A
2022-07-19 16:00 | 7 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 82 | 76 | 83 | 89 | 74 | 82 | 82 | 87 | #N/A | #N/A
2022-07-19 17:00 | 7 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 80 | 75 | 81 | 87 | 75 | 81 | 81 | 86 | #N/A | #N/A
2022-07-19 18:00 | 7 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 78 | 73 | 79 | 84 | 74 | 80 | 82 | 84 | #N/A | #N/A
2022-07-19 19:00 | 7 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 76 | 69 | 76 | 82 | 74 | 78 | 81 | 82 | #N/A | #N/A
2022-07-19 20:00 | 7 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 75 | 64 | 74 | 81 | 74 | 76 | 78 | 80 | #N/A | #N/A
2022-07-19 21:00 | 7 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 74 | 60 | 72 | 80 | 73 | 75 | 77 | 76 | #N/A | #N/A
2022-07-19 22:00 | 7 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 73 | 59 | 72 | 76 | 72 | 75 | 75 | 75 | #N/A | #N/A
2022-07-19 23:00 | 7 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 72 | 58 | 72 | 75 | 72 | 76 | 73 | 73 | #N/A | #N/A
2022-07-20 | 7 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 70 | 57 | 71 | 72 | 71 | 72 | 72 | 70 | #N/A | #N/A
2022-07-20 01:00 | 7 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 70 | 56 | 72 | 70 | 71 | 70 | 70 | 70 | #N/A | #N/A
2022-07-20 02:00 | 7 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 70 | 54 | 73 | 70 | 70 | 70 | 69 | 70 | #N/A | #N/A
2022-07-20 03:00 | 7 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 68 | 53 | 73 | 69 | 70 | 71 | 68 | 69 | #N/A | #N/A
2022-07-20 04:00 | 7 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 68 | 55 | 74 | 68 | 68 | 70 | 67 | 69 | #N/A | #N/A
2022-07-20 05:00 | 7 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 68 | 57 | 74 | 70 | 71 | 72 | 68 | 71 | #N/A | #N/A
2022-07-20 06:00 | 7 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 69 | 59 | 74 | 73 | 73 | 76 | 72 | 75 | #N/A | #N/A
2022-07-20 07:00 | 7 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 73 | 64 | 75 | 76 | 74 | 79 | 75 | 76 | #N/A | #N/A
2022-07-20 08:00 | 7 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 76 | 69 | 75 | 79 | 74 | 81 | 80 | 77 | #N/A | #N/A
2022-07-20 09:00 | 7 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 79 | 74 | 74 | 83 | 75 | 85 | 85 | 79 | #N/A | #N/A
2022-07-20 10:00 | 7 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 80 | 75 | 77 | 85 | 80 | 87 | 89 | 81 | #N/A | #N/A
2022-07-20 11:00 | 7 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 82 | 77 | 78 | 87 | 80 | 89 | 90 | 84 | #N/A | #N/A
2022-07-20 12:00 | 7 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 82 | 78 | 80 | 88 | 80 | 91 | 93 | 85 | #N/A | #N/A
2022-07-20 13:00 | 7 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 85 | 79 | 80 | 89 | 79 | 90 | 95 | 87 | #N/A | #N/A
2022-07-20 14:00 | 7 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 86 | 80 | 83 | 88 | 80 | 76 | 94 | 88 | #N/A | #N/A
2022-07-20 15:00 | 7 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 84 | 81 | 74 | 88 | 83 | 78 | 94 | 88 | #N/A | #N/A
2022-07-20 16:00 | 7 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 84 | 80 | 75 | 86 | 81 | 76 | 95 | 88 | #N/A | #N/A
2022-07-20 17:00 | 7 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 82 | 78 | 76 | 81 | 80 | 76 | 93 | 87 | #N/A | #N/A
2022-07-20 18:00 | 7 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 80 | 77 | 75 | 70 | 79 | 79 | 91 | 86 | #N/A | #N/A
2022-07-20 19:00 | 7 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 78 | 73 | 75 | 70 | 77 | 78 | 89 | 84 | #N/A | #N/A
2022-07-20 20:00 | 7 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 77 | 70 | 74 | 70 | 76 | 76 | 85 | 84 | #N/A | #N/A
2022-07-20 21:00 | 7 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 75 | 66 | 74 | 70 | 74 | 74 | 84 | 81 | #N/A | #N/A
2022-07-20 22:00 | 7 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 75 | 64 | 73 | 69 | 73 | 72 | 82 | 79 | #N/A | #N/A
2022-07-20 23:00 | 7 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 74 | 61 | 72 | 69 | 73 | 70 | 82 | 76 | #N/A | #N/A
2022-07-21 | 7 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 73 | 59 | 72 | 69 | 72 | 69 | 79 | 75 | #N/A | #N/A
2022-07-21 01:00 | 7 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 73 | 59 | 72 | 69 | 71 | 68 | 75 | 75 | #N/A | #N/A
2022-07-21 02:00 | 7 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 72 | 58 | 72 | 69 | 71 | 67 | 75 | 74 | #N/A | #N/A
2022-07-21 03:00 | 7 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 71 | 58 | 71 | 68 | 71 | 67 | 74 | 72 | #N/A | #N/A
2022-07-21 04:00 | 7 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 71 | 59 | 70 | 68 | 70 | 67 | 73 | 72 | #N/A | #N/A
2022-07-21 05:00 | 7 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 72 | 61 | 70 | 69 | 71 | 67 | 74 | 72 | #N/A | #N/A
2022-07-21 06:00 | 7 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 74 | 62 | 71 | 72 | 74 | 66 | 78 | 73 | #N/A | #N/A
2022-07-21 07:00 | 7 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 75 | 66 | 72 | 75 | 76 | 68 | 80 | 74 | #N/A | #N/A
2022-07-21 08:00 | 7 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 77 | 70 | 73 | 76 | 79 | 71 | 83 | 78 | #N/A | #N/A
2022-07-21 09:00 | 7 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 82 | 74 | 72 | 80 | 80 | 73 | 88 | 81 | #N/A | #N/A
2022-07-21 10:00 | 7 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 83 | 76 | 74 | 82 | 82 | 75 | 86 | 83 | #N/A | #N/A
2022-07-21 11:00 | 7 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 84 | 79 | 72 | 81 | 86 | 77 | 86 | 86 | #N/A | #N/A
2022-07-21 12:00 | 7 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 87 | 81 | 74 | 83 | 87 | 79 | 90 | 88 | #N/A | #N/A
2022-07-21 13:00 | 7 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 89 | 81 | 74 | 86 | 90 | 80 | 84 | 90 | #N/A | #N/A
2022-07-21 14:00 | 7 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 87 | 82 | 76 | 86 | 89 | 83 | 75 | 91 | #N/A | #N/A
2022-07-21 15:00 | 7 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 85 | 82 | 76 | 82 | 88 | 82 | 83 | 91 | #N/A | #N/A
2022-07-21 16:00 | 7 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 77 | 79 | 76 | 81 | 87 | 81 | 82 | 90 | #N/A | #N/A
2022-07-21 17:00 | 7 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 72 | 77 | 74 | 82 | 86 | 82 | 80 | 89 | #N/A | #N/A
2022-07-21 18:00 | 7 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 74 | 77 | 79 | 84 | 81 | 78 | 82 | #N/A | #N/A
2022-07-21 19:00 | 7 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 70 | 72 | 76 | 81 | 78 | 76 | 79 | #N/A | #N/A
2022-07-21 20:00 | 7 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 65 | 70 | 75 | 79 | 76 | 76 | 79 | #N/A | #N/A
2022-07-21 21:00 | 7 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 70 | 61 | 68 | 73 | 77 | 72 | 74 | 78 | #N/A | #N/A
2022-07-21 22:00 | 7 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 70 | 59 | 65 | 73 | 76 | 71 | 73 | 77 | #N/A | #N/A
2022-07-21 23:00 | 7 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 69 | 58 | 65 | 72 | 74 | 66 | 72 | 75 | #N/A | #N/A
2022-07-22 | 7 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 69 | 56 | 65 | 71 | 72 | 68 | 71 | 74 | #N/A | #N/A
2022-07-22 01:00 | 7 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 70 | 56 | 65 | 71 | 70 | 66 | 70 | 75 | #N/A | #N/A
2022-07-22 02:00 | 7 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 70 | 55 | 64 | 70 | 69 | 64 | 69 | 74 | #N/A | #N/A
2022-07-22 03:00 | 7 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 69 | 55 | 64 | 70 | 70 | 65 | 69 | 74 | #N/A | #N/A
2022-07-22 04:00 | 7 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 69 | 56 | 64 | 69 | 69 | 63 | 69 | 74 | #N/A | #N/A
2022-07-22 05:00 | 7 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 70 | 57 | 63 | 71 | 70 | 63 | 69 | 74 | #N/A | #N/A
2022-07-22 06:00 | 7 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 70 | 58 | 65 | 73 | 73 | 64 | 70 | 75 | #N/A | #N/A
2022-07-22 07:00 | 7 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 72 | 63 | 67 | 76 | 78 | 69 | 72 | 76 | #N/A | #N/A
2022-07-22 08:00 | 7 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 76 | 69 | 69 | 79 | 80 | 73 | 78 | 80 | #N/A | #N/A
2022-07-22 09:00 | 7 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 78 | 74 | 70 | 79 | 82 | 76 | 82 | 84 | #N/A | #N/A
2022-07-22 10:00 | 7 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 80 | 75 | 70 | 80 | 84 | 77 | 85 | 86 | #N/A | #N/A
2022-07-22 11:00 | 7 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 81 | 77 | 71 | 80 | 87 | 80 | 85 | 87 | #N/A | #N/A
2022-07-22 12:00 | 7 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 82 | 78 | 71 | 83 | 86 | 82 | 86 | 91 | #N/A | #N/A
2022-07-22 13:00 | 7 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 84 | 79 | 71 | 85 | 86 | 83 | 87 | 92 | #N/A | #N/A
2022-07-22 14:00 | 7 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 86 | 79 | 72 | 84 | 85 | 82 | 88 | 94 | #N/A | #N/A
2022-07-22 15:00 | 7 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 85 | 80 | 72 | 84 | 87 | 83 | 89 | 94 | #N/A | #N/A
2022-07-22 16:00 | 7 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 85 | 78 | 72 | 83 | 87 | 83 | 85 | 93 | #N/A | #N/A
2022-07-22 17:00 | 7 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 83 | 77 | 71 | 82 | 86 | 81 | 84 | 91 | #N/A | #N/A
2022-07-22 18:00 | 7 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 81 | 75 | 70 | 81 | 81 | 79 | 82 | 88 | #N/A | #N/A
2022-07-22 19:00 | 7 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 80 | 71 | 65 | 78 | 78 | 79 | 79 | 88 | #N/A | #N/A
2022-07-22 20:00 | 7 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 79 | 68 | 59 | 77 | 76 | 76 | 79 | 85 | #N/A | #N/A
2022-07-22 21:00 | 7 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 76 | 64 | 56 | 77 | 75 | 73 | 78 | 84 | #N/A | #N/A
2022-07-22 22:00 | 7 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 76 | 63 | 55 | 77 | 74 | 70 | 78 | 83 | #N/A | #N/A
2022-07-22 23:00 | 7 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 76 | 63 | 56 | 78 | 73 | 66 | 78 | 81 | #N/A | #N/A
2022-07-23 | 7 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 76 | 62 | 54 | 75 | 73 | 66 | 79 | 80 | #N/A | #N/A
2022-07-23 01:00 | 7 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 75 | 62 | 54 | 73 | 73 | 67 | 78 | 78 | #N/A | #N/A
2022-07-23 02:00 | 7 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 75 | 62 | 54 | 72 | 73 | 65 | 78 | 77 | #N/A | #N/A
2022-07-23 03:00 | 7 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 74 | 62 | 54 | 70 | 73 | 63 | 77 | 76 | #N/A | #N/A
2022-07-23 04:00 | 7 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 74 | 63 | 53 | 71 | 73 | 61 | 78 | 75 | #N/A | #N/A
2022-07-23 05:00 | 7 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 74 | 64 | 54 | 73 | 72 | 61 | 79 | 75 | #N/A | #N/A
2022-07-23 06:00 | 7 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 76 | 65 | 59 | 76 | 76 | 64 | 80 | 77 | #N/A | #N/A
2022-07-23 07:00 | 7 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 80 | 69 | 65 | 78 | 79 | 67 | 82 | 80 | #N/A | #N/A
2022-07-23 08:00 | 7 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 82 | 73 | 69 | 81 | 79 | 71 | 83 | 83 | #N/A | #N/A
2022-07-23 09:00 | 7 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 83 | 77 | 70 | 83 | 83 | 75 | 88 | 89 | #N/A | #N/A
2022-07-23 10:00 | 7 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 86 | 78 | 72 | 86 | 85 | 78 | 88 | 91 | #N/A | #N/A
2022-07-23 11:00 | 7 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 86 | 78 | 73 | 85 | 85 | 81 | 91 | 92 | #N/A | #N/A
2022-07-23 12:00 | 7 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 88 | 79 | 73 | 88 | 87 | 83 | 93 | 93 | #N/A | #N/A
2022-07-23 13:00 | 7 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 87 | 91 | 75 | 73 | 86 | 86 | 83 | 93 | 95 | #N/A | #N/A
2022-07-23 14:00 | 7 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 86 | 85 | 70 | 73 | 85 | 87 | 85 | 71 | 95 | #N/A | #N/A
2022-07-23 15:00 | 7 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 87 | 77 | 66 | 73 | 83 | 87 | 85 | 71 | 95 | #N/A | #N/A
2022-07-23 16:00 | 7 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 85 | 77 | 66 | 72 | 81 | 84 | 84 | 71 | 93 | #N/A | #N/A
2022-07-23 17:00 | 7 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 78 | 66 | 72 | 77 | 78 | 83 | 72 | 76 | #N/A | #N/A
2022-07-23 18:00 | 7 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 77 | 66 | 70 | 76 | 79 | 83 | 72 | 75 | #N/A | #N/A
2022-07-23 19:00 | 7 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 75 | 65 | 67 | 74 | 77 | 82 | 72 | 74 | #N/A | #N/A
2022-07-23 20:00 | 7 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 72 | 65 | 65 | 72 | 77 | 79 | 72 | 73 | #N/A | #N/A
2022-07-23 21:00 | 7 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 69 | 64 | 64 | 71 | 74 | 77 | 72 | 73 | #N/A | #N/A
2022-07-23 22:00 | 7 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 68 | 63 | 64 | 68 | 73 | 75 | 71 | 73 | #N/A | #N/A
2022-07-23 23:00 | 7 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 67 | 62 | 65 | 67 | 72 | 72 | 71 | 74 | #N/A | #N/A
2022-07-24 | 7 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 65 | 61 | 64 | 66 | 72 | 72 | 71 | 74 | #N/A | #N/A
2022-07-24 01:00 | 7 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 64 | 60 | 64 | 65 | 71 | 70 | 70 | 73 | #N/A | #N/A
2022-07-24 02:00 | 7 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 62 | 60 | 63 | 64 | 70 | 69 | 68 | 71 | #N/A | #N/A
2022-07-24 03:00 | 7 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 61 | 59 | 63 | 64 | 70 | 69 | 67 | 69 | #N/A | #N/A
2022-07-24 04:00 | 7 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 61 | 63 | 63 | 69 | 69 | 64 | 67 | #N/A | #N/A
2022-07-24 05:00 | 7 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 61 | 63 | 63 | 65 | 70 | 68 | 62 | 67 | #N/A | #N/A
2022-07-24 06:00 | 7 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 62 | 65 | 66 | 69 | 74 | 70 | 64 | 70 | #N/A | #N/A
2022-07-24 07:00 | 7 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 63 | 67 | 69 | 72 | 79 | 72 | 68 | 72 | #N/A | #N/A
2022-07-24 08:00 | 7 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 66 | 70 | 72 | 74 | 81 | 76 | 70 | 74 | #N/A | #N/A
2022-07-24 09:00 | 7 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 68 | 72 | 74 | 77 | 84 | 80 | 73 | 75 | #N/A | #N/A
2022-07-24 10:00 | 7 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 70 | 74 | 77 | 77 | 86 | 83 | 77 | 76 | #N/A | #N/A
2022-07-24 11:00 | 7 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 72 | 75 | 77 | 78 | 88 | 85 | 79 | 78 | #N/A | #N/A
2022-07-24 12:00 | 7 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 74 | 77 | 79 | 79 | 88 | 85 | 80 | 79 | #N/A | #N/A
2022-07-24 13:00 | 7 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 75 | 76 | 77 | 81 | 90 | 86 | 81 | 80 | #N/A | #N/A
2022-07-24 14:00 | 7 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 75 | 76 | 79 | 82 | 86 | 86 | 82 | 80 | #N/A | #N/A
2022-07-24 15:00 | 7 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 74 | 75 | 80 | 82 | 88 | 87 | 83 | 81 | #N/A | #N/A
2022-07-24 16:00 | 7 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 74 | 74 | 80 | 83 | 86 | 87 | 83 | 81 | #N/A | #N/A
2022-07-24 17:00 | 7 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 73 | 72 | 76 | 82 | 84 | 85 | 83 | 81 | #N/A | #N/A
2022-07-24 18:00 | 7 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 70 | 71 | 75 | 80 | 80 | 83 | 81 | 77 | #N/A | #N/A
2022-07-24 19:00 | 7 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 66 | 70 | 75 | 76 | 78 | 83 | 75 | 74 | #N/A | #N/A
2022-07-24 20:00 | 7 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 65 | 68 | 73 | 70 | 76 | 78 | 72 | 72 | #N/A | #N/A
2022-07-24 21:00 | 7 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 65 | 67 | 70 | 70 | 74 | 75 | 71 | 71 | #N/A | #N/A
2022-07-24 22:00 | 7 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 64 | 67 | 69 | 67 | 72 | 75 | 73 | 68 | #N/A | #N/A
2022-07-24 23:00 | 7 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 66 | 67 | 67 | 71 | 73 | 68 | 68 | #N/A | #N/A
2022-07-25 | 7 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 66 | 67 | 67 | 71 | 72 | 67 | 68 | #N/A | #N/A
2022-07-25 01:00 | 7 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 66 | 66 | 66 | 70 | 72 | 66 | 67 | #N/A | #N/A
2022-07-25 02:00 | 7 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 67 | 66 | 64 | 70 | 72 | 68 | 66 | #N/A | #N/A
2022-07-25 03:00 | 7 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 59 | 67 | 66 | 65 | 70 | 72 | 67 | 66 | #N/A | #N/A
2022-07-25 04:00 | 7 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 58 | 67 | 66 | 63 | 69 | 69 | 67 | 64 | #N/A | #N/A
2022-07-25 05:00 | 7 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 67 | 66 | 65 | 71 | 70 | 66 | 63 | #N/A | #N/A
2022-07-25 06:00 | 7 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 62 | 67 | 69 | 70 | 74 | 73 | 68 | 65 | #N/A | #N/A
2022-07-25 07:00 | 7 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 67 | 71 | 72 | 74 | 78 | 76 | 71 | 68 | #N/A | #N/A
2022-07-25 08:00 | 7 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 70 | 75 | 75 | 78 | 82 | 77 | 71 | 73 | #N/A | #N/A
2022-07-25 09:00 | 7 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 70 | 79 | 80 | 80 | 82 | 80 | 75 | 73 | #N/A | #N/A
2022-07-25 10:00 | 7 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 69 | 79 | 81 | 81 | 86 | 84 | 76 | 73 | #N/A | #N/A
2022-07-25 11:00 | 7 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 70 | 79 | 78 | 82 | 89 | 85 | 79 | 74 | #N/A | #N/A
2022-07-25 12:00 | 7 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 70 | 79 | 77 | 84 | 87 | 85 | 80 | 73 | #N/A | #N/A
2022-07-25 13:00 | 7 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 70 | 78 | 79 | 85 | 90 | 86 | 83 | 73 | #N/A | #N/A
2022-07-25 14:00 | 7 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 65 | 78 | 80 | 86 | 86 | 86 | 82 | 74 | #N/A | #N/A
2022-07-25 15:00 | 7 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 68 | 77 | 80 | 86 | 86 | 89 | 82 | 75 | #N/A | #N/A
2022-07-25 16:00 | 7 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 72 | 74 | 80 | 86 | 84 | 87 | 81 | 74 | #N/A | #N/A
2022-07-25 17:00 | 7 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 70 | 72 | 79 | 84 | 84 | 84 | 80 | 74 | #N/A | #N/A
2022-07-25 18:00 | 7 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 68 | 69 | 75 | 81 | 81 | 83 | 78 | 73 | #N/A | #N/A
2022-07-25 19:00 | 7 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 65 | 69 | 74 | 76 | 79 | 81 | 76 | 72 | #N/A | #N/A
2022-07-25 20:00 | 7 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 64 | 70 | 73 | 73 | 78 | 80 | 75 | 72 | #N/A | #N/A
2022-07-25 21:00 | 7 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 62 | 70 | 70 | 71 | 77 | 79 | 74 | 72 | #N/A | #N/A
2022-07-25 22:00 | 7 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 62 | 70 | 71 | 70 | 77 | 78 | 74 | 70 | #N/A | #N/A
2022-07-25 23:00 | 7 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 62 | 70 | 74 | 68 | 77 | 78 | 73 | 69 | #N/A | #N/A
2022-07-26 | 7 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 62 | 70 | 74 | 67 | 77 | 75 | 72 | 70 | #N/A | #N/A
2022-07-26 01:00 | 7 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 60 | 70 | 73 | 66 | 77 | 77 | 72 | 70 | #N/A | #N/A
2022-07-26 02:00 | 7 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 60 | 70 | 72 | 64 | 77 | 72 | 71 | 70 | #N/A | #N/A
2022-07-26 03:00 | 7 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 58 | 70 | 72 | 64 | 77 | 72 | 71 | 70 | #N/A | #N/A
2022-07-26 04:00 | 7 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 57 | 70 | 72 | 62 | 78 | 68 | 70 | 70 | #N/A | #N/A
2022-07-26 05:00 | 7 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 59 | 71 | 71 | 63 | 77 | 68 | 71 | 69 | #N/A | #N/A
2022-07-26 06:00 | 7 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 61 | 71 | 70 | 69 | 79 | 71 | 71 | 70 | #N/A | #N/A
2022-07-26 07:00 | 7 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 65 | 71 | 70 | 76 | 81 | 72 | 70 | 71 | #N/A | #N/A
2022-07-26 08:00 | 7 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 68 | 71 | 70 | 79 | 83 | 73 | 68 | 73 | #N/A | #N/A
2022-07-26 09:00 | 7 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 71 | 71 | 75 | 80 | 85 | 76 | 68 | 74 | #N/A | #N/A
2022-07-26 10:00 | 7 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 74 | 73 | 74 | 83 | 87 | 79 | 67 | 76 | #N/A | #N/A
2022-07-26 11:00 | 7 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 77 | 75 | 73 | 84 | 86 | 81 | 65 | 77 | #N/A | #N/A
2022-07-26 12:00 | 7 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 77 | 77 | 73 | 86 | 75 | 81 | 64 | 80 | #N/A | #N/A
2022-07-26 13:00 | 7 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 78 | 76 | 73 | 86 | 76 | 83 | 64 | 81 | #N/A | #N/A
2022-07-26 14:00 | 7 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 79 | 74 | 75 | 87 | 77 | 82 | 65 | 82 | #N/A | #N/A
2022-07-26 15:00 | 7 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 77 | 73 | 75 | 88 | 79 | 83 | 67 | 82 | #N/A | #N/A
2022-07-26 16:00 | 7 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 77 | 71 | 74 | 84 | 81 | 83 | 69 | 81 | #N/A | #N/A
2022-07-26 17:00 | 7 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 76 | 69 | 73 | 85 | 82 | 82 | 69 | 81 | #N/A | #N/A
2022-07-26 18:00 | 7 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 74 | 67 | 72 | 83 | 81 | 79 | 68 | 80 | #N/A | #N/A
2022-07-26 19:00 | 7 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 72 | 66 | 71 | 80 | 79 | 76 | 67 | 80 | #N/A | #N/A
2022-07-26 20:00 | 7 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 71 | 65 | 70 | 75 | 78 | 74 | 66 | 79 | #N/A | #N/A
2022-07-26 21:00 | 7 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 70 | 64 | 70 | 73 | 78 | 72 | 66 | 78 | #N/A | #N/A
2022-07-26 22:00 | 7 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 70 | 63 | 71 | 71 | 69 | 71 | 65 | 77 | #N/A | #N/A
2022-07-26 23:00 | 7 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 69 | 63 | 70 | 70 | 70 | 66 | 65 | 77 | #N/A | #N/A
2022-07-27 | 7 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 68 | 62 | 69 | 68 | 70 | 67 | 64 | 77 | #N/A | #N/A
2022-07-27 01:00 | 7 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 68 | 62 | 67 | 67 | 70 | 68 | 64 | 76 | #N/A | #N/A
2022-07-27 02:00 | 7 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 68 | 62 | 67 | 66 | 70 | 67 | 62 | 75 | #N/A | #N/A
2022-07-27 03:00 | 7 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 69 | 62 | 66 | 65 | 70 | 67 | 63 | 75 | #N/A | #N/A
2022-07-27 04:00 | 7 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 70 | 62 | 66 | 64 | 70 | 65 | 62 | 75 | #N/A | #N/A
2022-07-27 05:00 | 7 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 70 | 62 | 65 | 66 | 71 | 64 | 62 | 76 | #N/A | #N/A
2022-07-27 06:00 | 7 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 70 | 62 | 69 | 71 | 73 | 65 | 63 | 76 | #N/A | #N/A
2022-07-27 07:00 | 7 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 72 | 63 | 69 | 76 | 76 | 67 | 65 | 78 | #N/A | #N/A
2022-07-27 08:00 | 7 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 75 | 63 | 70 | 81 | 79 | 68 | 67 | 79 | #N/A | #N/A
2022-07-27 09:00 | 7 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 78 | 64 | 70 | 82 | 81 | 69 | 72 | 82 | #N/A | #N/A
2022-07-27 10:00 | 7 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 78 | 66 | 70 | 83 | 83 | 72 | 73 | 84 | #N/A | #N/A
2022-07-27 11:00 | 7 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 81 | 67 | 71 | 85 | 84 | 78 | 74 | 87 | #N/A | #N/A
2022-07-27 12:00 | 7 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 83 | 69 | 72 | 86 | 84 | 82 | 76 | 88 | #N/A | #N/A
2022-07-27 13:00 | 7 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 84 | 71 | 72 | 88 | 86 | 83 | 79 | 87 | #N/A | #N/A
2022-07-27 14:00 | 7 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 82 | 72 | 73 | 89 | 85 | 82 | 80 | 87 | #N/A | #N/A
2022-07-27 15:00 | 7 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 84 | 74 | 73 | 88 | 87 | 83 | 81 | 87 | #N/A | #N/A
2022-07-27 16:00 | 7 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 83 | 73 | 73 | 87 | 86 | 82 | 81 | 87 | #N/A | #N/A
2022-07-27 17:00 | 7 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 81 | 72 | 72 | 85 | 85 | 82 | 80 | 86 | #N/A | #N/A
2022-07-27 18:00 | 7 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 79 | 71 | 68 | 82 | 83 | 81 | 76 | 81 | #N/A | #N/A
2022-07-27 19:00 | 7 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 70 | 67 | 67 | 79 | 80 | 79 | 71 | 76 | #N/A | #N/A
2022-07-27 20:00 | 7 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 65 | 63 | 63 | 78 | 78 | 78 | 68 | 73 | #N/A | #N/A
2022-07-27 21:00 | 7 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 65 | 59 | 64 | 76 | 77 | 76 | 64 | 73 | #N/A | #N/A
2022-07-27 22:00 | 7 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 65 | 58 | 64 | 74 | 77 | 73 | 62 | 71 | #N/A | #N/A
2022-07-27 23:00 | 7 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 65 | 57 | 65 | 73 | 76 | 72 | 61 | 71 | #N/A | #N/A
2022-07-28 | 7 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 56 | 66 | 71 | 74 | 70 | 59 | 70 | #N/A | #N/A
2022-07-28 01:00 | 7 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 56 | 66 | 69 | 73 | 68 | 58 | 70 | #N/A | #N/A
2022-07-28 02:00 | 7 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 64 | 55 | 67 | 68 | 72 | 66 | 57 | 70 | #N/A | #N/A
2022-07-28 03:00 | 7 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 64 | 55 | 69 | 68 | 73 | 64 | 56 | 70 | #N/A | #N/A
2022-07-28 04:00 | 7 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 64 | 57 | 69 | 68 | 73 | 62 | 55 | 69 | #N/A | #N/A
2022-07-28 05:00 | 7 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 59 | 63 | 68 | 74 | 63 | 56 | 69 | #N/A | #N/A
2022-07-28 06:00 | 7 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 63 | 61 | 65 | 73 | 75 | 66 | 60 | 70 | #N/A | #N/A
2022-07-28 07:00 | 7 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 65 | 64 | 68 | 75 | 76 | 72 | 64 | 73 | #N/A | #N/A
2022-07-28 08:00 | 7 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 63 | 66 | 71 | 77 | 78 | 78 | 67 | 76 | #N/A | #N/A
2022-07-28 09:00 | 7 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 63 | 69 | 75 | 79 | 81 | 80 | 71 | 78 | #N/A | #N/A
2022-07-28 10:00 | 7 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 66 | 70 | 75 | 79 | 83 | 81 | 75 | 79 | #N/A | #N/A
2022-07-28 11:00 | 7 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 66 | 72 | 79 | 82 | 85 | 81 | 78 | 80 | #N/A | #N/A
2022-07-28 12:00 | 7 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 67 | 73 | 77 | 84 | 89 | 81 | 78 | 79 | #N/A | #N/A
2022-07-28 13:00 | 7 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 67 | 73 | 74 | 84 | 90 | 81 | 80 | 78 | #N/A | #N/A
2022-07-28 14:00 | 7 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 66 | 73 | 73 | 85 | 90 | 81 | 83 | 78 | #N/A | #N/A
2022-07-28 15:00 | 7 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 65 | 73 | 74 | 85 | 90 | 81 | 81 | 79 | #N/A | #N/A
2022-07-28 16:00 | 7 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 66 | 71 | 74 | 85 | 89 | 80 | 82 | 76 | #N/A | #N/A
2022-07-28 17:00 | 7 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 65 | 68 | 73 | 83 | 88 | 79 | 80 | 76 | #N/A | #N/A
2022-07-28 18:00 | 7 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 65 | 66 | 72 | 80 | 82 | 79 | 76 | 74 | #N/A | #N/A
2022-07-28 19:00 | 7 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 62 | 66 | 71 | 77 | 80 | 77 | 72 | 70 | #N/A | #N/A
2022-07-28 20:00 | 7 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 61 | 65 | 70 | 75 | 79 | 74 | 70 | 67 | #N/A | #N/A
2022-07-28 21:00 | 7 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 60 | 65 | 69 | 74 | 78 | 73 | 68 | 65 | #N/A | #N/A
2022-07-28 22:00 | 7 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 59 | 64 | 66 | 72 | 77 | 70 | 67 | 63 | #N/A | #N/A
2022-07-28 23:00 | 7 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 58 | 64 | 65 | 71 | 76 | 63 | 66 | 61 | #N/A | #N/A
2022-07-29 | 7 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 58 | 63 | 65 | 70 | 76 | 67 | 67 | 60 | #N/A | #N/A
2022-07-29 01:00 | 7 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 57 | 62 | 65 | 69 | 76 | 65 | 67 | 59 | #N/A | #N/A
2022-07-29 02:00 | 7 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 56 | 60 | 64 | 70 | 77 | 65 | 65 | 58 | #N/A | #N/A
2022-07-29 03:00 | 7 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 52 | 59 | 63 | 70 | 76 | 65 | 65 | 59 | #N/A | #N/A
2022-07-29 04:00 | 7 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 50 | 60 | 62 | 69 | 76 | 65 | 64 | 60 | #N/A | #N/A
2022-07-29 05:00 | 7 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 51 | 60 | 60 | 70 | 77 | 67 | 64 | 59 | #N/A | #N/A
2022-07-29 06:00 | 7 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 54 | 61 | 60 | 73 | 79 | 68 | 66 | 59 | #N/A | #N/A
2022-07-29 07:00 | 7 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 58 | 63 | 60 | 76 | 80 | 72 | 66 | 60 | #N/A | #N/A
2022-07-29 08:00 | 7 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 62 | 66 | 60 | 78 | 82 | 73 | 68 | 61 | #N/A | #N/A
2022-07-29 09:00 | 7 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 66 | 68 | 60 | 78 | 86 | 75 | 70 | 62 | #N/A | #N/A
2022-07-29 10:00 | 7 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 69 | 70 | 61 | 81 | 87 | 75 | 73 | 63 | #N/A | #N/A
2022-07-29 11:00 | 7 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 70 | 72 | 61 | 82 | 91 | 72 | 75 | 67 | #N/A | #N/A
2022-07-29 12:00 | 7 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 71 | 74 | 66 | 86 | 91 | 74 | 76 | 68 | #N/A | #N/A
2022-07-29 13:00 | 7 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 70 | 75 | 66 | 85 | 91 | 72 | 75 | 68 | #N/A | #N/A
2022-07-29 14:00 | 7 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 69 | 76 | 69 | 85 | 92 | 72 | 75 | 72 | #N/A | #N/A
2022-07-29 15:00 | 7 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 69 | 77 | 70 | 86 | 87 | 74 | 76 | 73 | #N/A | #N/A
2022-07-29 16:00 | 7 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 69 | 76 | 69 | 85 | 86 | 70 | 73 | 73 | #N/A | #N/A
2022-07-29 17:00 | 7 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 69 | 74 | 68 | 81 | 83 | 70 | 73 | 72 | #N/A | #N/A
2022-07-29 18:00 | 7 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 66 | 73 | 65 | 80 | 81 | 71 | 71 | 71 | #N/A | #N/A
2022-07-29 19:00 | 7 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 66 | 69 | 61 | 77 | 77 | 69 | 67 | 71 | #N/A | #N/A
2022-07-29 20:00 | 7 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 65 | 65 | 58 | 74 | 75 | 67 | 64 | 70 | #N/A | #N/A
2022-07-29 21:00 | 7 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 65 | 61 | 57 | 73 | 74 | 67 | 63 | 70 | #N/A | #N/A
2022-07-29 22:00 | 7 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 66 | 60 | 58 | 72 | 74 | 67 | 62 | 70 | #N/A | #N/A
2022-07-29 23:00 | 7 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 66 | 58 | 56 | 70 | 73 | 66 | 62 | 70 | #N/A | #N/A
2022-07-30 | 7 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 65 | 57 | 55 | 70 | 73 | 65 | 62 | 70 | #N/A | #N/A
2022-07-30 01:00 | 7 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 56 | 55 | 71 | 73 | 63 | 61 | 70 | #N/A | #N/A
2022-07-30 02:00 | 7 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 62 | 54 | 54 | 70 | 72 | 63 | 59 | 70 | #N/A | #N/A
2022-07-30 03:00 | 7 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 59 | 53 | 53 | 71 | 71 | 64 | 57 | 68 | #N/A | #N/A
2022-07-30 04:00 | 7 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 58 | 55 | 53 | 71 | 70 | 63 | 58 | 66 | #N/A | #N/A
2022-07-30 05:00 | 7 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 58 | 57 | 55 | 71 | 71 | 64 | 60 | 67 | #N/A | #N/A
2022-07-30 06:00 | 7 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 58 | 59 | 61 | 72 | 73 | 64 | 62 | 68 | #N/A | #N/A
2022-07-30 07:00 | 7 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 60 | 63 | 69 | 75 | 76 | 65 | 65 | 68 | #N/A | #N/A
2022-07-30 08:00 | 7 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 61 | 67 | 71 | 77 | 78 | 67 | 67 | 72 | #N/A | #N/A
2022-07-30 09:00 | 7 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 64 | 71 | 72 | 78 | 80 | 68 | 71 | 74 | #N/A | #N/A
2022-07-30 10:00 | 7 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 65 | 73 | 73 | 79 | 81 | 75 | 75 | 74 | #N/A | #N/A
2022-07-30 11:00 | 7 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 64 | 74 | 74 | 83 | 82 | 75 | 77 | 76 | #N/A | #N/A
2022-07-30 12:00 | 7 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 66 | 76 | 74 | 84 | 84 | 75 | 77 | 77 | #N/A | #N/A
2022-07-30 13:00 | 7 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 67 | 77 | 75 | 85 | 87 | 76 | 77 | 77 | #N/A | #N/A
2022-07-30 14:00 | 7 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 70 | 78 | 76 | 83 | 87 | 78 | 76 | 76 | #N/A | #N/A
2022-07-30 15:00 | 7 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 66 | 79 | 76 | 85 | 86 | 80 | 77 | 75 | #N/A | #N/A
2022-07-30 16:00 | 7 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 67 | 77 | 76 | 85 | 84 | 77 | 77 | 75 | #N/A | #N/A
2022-07-30 17:00 | 7 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 65 | 74 | 75 | 83 | 83 | 78 | 75 | 74 | #N/A | #N/A
2022-07-30 18:00 | 7 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 62 | 72 | 73 | 81 | 80 | 77 | 73 | 72 | #N/A | #N/A
2022-07-30 19:00 | 7 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 59 | 70 | 68 | 77 | 77 | 75 | 71 | 68 | #N/A | #N/A
2022-07-30 20:00 | 7 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 57 | 67 | 64 | 77 | 79 | 73 | 70 | 65 | #N/A | #N/A
2022-07-30 21:00 | 7 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 56 | 65 | 61 | 75 | 76 | 70 | 70 | 66 | #N/A | #N/A
2022-07-30 22:00 | 7 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 55 | 65 | 60 | 74 | 75 | 65 | 70 | 64 | #N/A | #N/A
2022-07-30 23:00 | 7 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 54 | 66 | 59 | 74 | 74 | 63 | 70 | 63 | #N/A | #N/A
2022-07-31 | 7 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 53 | 66 | 57 | 75 | 72 | 62 | 70 | 63 | #N/A | #N/A
2022-07-31 01:00 | 7 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 53 | 66 | 56 | 74 | 71 | 61 | 69 | 62 | #N/A | #N/A
2022-07-31 02:00 | 7 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 53 | 65 | 56 | 73 | 70 | 61 | 69 | 63 | #N/A | #N/A
2022-07-31 03:00 | 7 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 53 | 65 | 57 | 73 | 70 | 59 | 69 | 63 | #N/A | #N/A
2022-07-31 04:00 | 7 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 52 | 66 | 57 | 72 | 69 | 58 | 69 | 64 | #N/A | #N/A
2022-07-31 05:00 | 7 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 53 | 67 | 58 | 72 | 70 | 59 | 67 | 62 | #N/A | #N/A
2022-07-31 06:00 | 7 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 55 | 68 | 64 | 73 | 72 | 62 | 68 | 61 | #N/A | #N/A
2022-07-31 07:00 | 7 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 57 | 71 | 73 | 75 | 75 | 65 | 70 | 61 | #N/A | #N/A
2022-07-31 08:00 | 7 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 59 | 75 | 75 | 78 | 74 | 67 | 74 | 62 | #N/A | #N/A
2022-07-31 09:00 | 7 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 58 | 78 | 78 | 80 | 77 | 68 | 74 | 63 | #N/A | #N/A
2022-07-31 10:00 | 7 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 58 | 80 | 78 | 80 | 77 | 72 | 78 | 65 | #N/A | #N/A
2022-07-31 11:00 | 7 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 59 | 81 | 79 | 83 | 75 | 76 | 78 | 65 | #N/A | #N/A
2022-07-31 12:00 | 7 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 59 | 83 | 78 | 82 | 78 | 77 | 80 | 66 | #N/A | #N/A
2022-07-31 13:00 | 7 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 60 | 83 | 79 | 81 | 79 | 80 | 81 | 67 | #N/A | #N/A
2022-07-31 14:00 | 7 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 60 | 82 | 80 | 80 | 79 | 80 | 82 | 67 | #N/A | #N/A
2022-07-31 15:00 | 7 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 60 | 82 | 81 | 81 | 78 | 81 | 83 | 68 | #N/A | #N/A
2022-07-31 16:00 | 7 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 60 | 78 | 80 | 81 | 78 | 81 | 82 | 68 | #N/A | #N/A
2022-07-31 17:00 | 7 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 60 | 73 | 79 | 80 | 75 | 79 | 82 | 68 | #N/A | #N/A
2022-07-31 18:00 | 7 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 60 | 69 | 76 | 78 | 73 | 78 | 79 | 68 | #N/A | #N/A
2022-07-31 19:00 | 7 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 60 | 69 | 72 | 74 | 70 | 75 | 74 | 68 | #N/A | #N/A
2022-07-31 20:00 | 7 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 68 | 69 | 73 | 69 | 73 | 72 | 68 | #N/A | #N/A
2022-07-31 21:00 | 7 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 67 | 69 | 72 | 69 | 72 | 70 | 66 | #N/A | #N/A
2022-07-31 22:00 | 7 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 66 | 68 | 70 | 69 | 70 | 68 | 63 | #N/A | #N/A
2022-07-31 23:00 | 7 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 58 | 64 | 68 | 69 | 69 | 69 | 66 | 61 | #N/A | #N/A
2022-08-01 | 8 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 57 | 63 | 67 | 67 | 69 | 67 | 65 | 58 | #N/A | #N/A
2022-08-01 01:00 | 8 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 56 | 62 | 67 | 66 | 69 | 66 | 63 | 56 | #N/A | #N/A
2022-08-01 02:00 | 8 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 56 | 60 | 66 | 64 | 69 | 64 | 61 | 53 | #N/A | #N/A
2022-08-01 03:00 | 8 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 55 | 59 | 66 | 63 | 69 | 63 | 59 | 51 | #N/A | #N/A
2022-08-01 04:00 | 8 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 54 | 58 | 66 | 63 | 69 | 63 | 60 | 50 | #N/A | #N/A
2022-08-01 05:00 | 8 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 54 | 59 | 66 | 63 | 72 | 62 | 60 | 51 | #N/A | #N/A
2022-08-01 06:00 | 8 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 56 | 61 | 67 | 64 | 73 | 63 | 60 | 56 | #N/A | #N/A
2022-08-01 07:00 | 8 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 59 | 58 | 67 | 65 | 76 | 64 | 62 | 60 | #N/A | #N/A
2022-08-01 08:00 | 8 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 63 | 59 | 72 | 68 | 78 | 65 | 64 | 66 | #N/A | #N/A
2022-08-01 09:00 | 8 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 65 | 62 | 77 | 70 | 81 | 67 | 67 | 72 | #N/A | #N/A
2022-08-01 10:00 | 8 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 68 | 61 | 77 | 71 | 84 | 68 | 70 | 76 | #N/A | #N/A
2022-08-01 11:00 | 8 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 69 | 65 | 78 | 72 | 82 | 71 | 72 | 76 | #N/A | #N/A
2022-08-01 12:00 | 8 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 71 | 67 | 78 | 73 | 85 | 73 | 72 | 79 | #N/A | #N/A
2022-08-01 13:00 | 8 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 71 | 68 | 79 | 73 | 86 | 74 | 74 | 79 | #N/A | #N/A
2022-08-01 14:00 | 8 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 72 | 70 | 78 | 75 | 85 | 77 | 72 | 81 | #N/A | #N/A
2022-08-01 15:00 | 8 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 71 | 70 | 78 | 74 | 83 | 75 | 72 | 80 | #N/A | #N/A
2022-08-01 16:00 | 8 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 71 | 70 | 77 | 75 | 84 | 74 | 72 | 80 | #N/A | #N/A
2022-08-01 17:00 | 8 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 69 | 67 | 77 | 74 | 82 | 74 | 72 | 77 | #N/A | #N/A
2022-08-01 18:00 | 8 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 67 | 66 | 77 | 72 | 80 | 73 | 70 | 76 | #N/A | #N/A
2022-08-01 19:00 | 8 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 64 | 63 | 76 | 70 | 77 | 71 | 66 | 67 | #N/A | #N/A
2022-08-01 20:00 | 8 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 62 | 60 | 76 | 69 | 74 | 71 | 64 | 63 | #N/A | #N/A
2022-08-01 21:00 | 8 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 61 | 60 | 75 | 69 | 73 | 69 | 63 | 61 | #N/A | #N/A
2022-08-01 22:00 | 8 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 60 | 60 | 74 | 68 | 72 | 66 | 62 | 58 | #N/A | #N/A
2022-08-01 23:00 | 8 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 59 | 60 | 74 | 68 | 71 | 62 | 62 | 58 | #N/A | #N/A
2022-08-02 | 8 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 58 | 61 | 72 | 67 | 70 | 65 | 62 | 55 | #N/A | #N/A
2022-08-02 01:00 | 8 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 56 | 60 | 72 | 67 | 70 | 65 | 62 | 54 | #N/A | #N/A
2022-08-02 02:00 | 8 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 56 | 59 | 72 | 67 | 70 | 60 | 61 | 54 | #N/A | #N/A
2022-08-02 03:00 | 8 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 55 | 58 | 71 | 67 | 71 | 59 | 60 | 53 | #N/A | #N/A
2022-08-02 04:00 | 8 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 55 | 56 | 72 | 66 | 70 | 60 | 60 | 52 | #N/A | #N/A
2022-08-02 05:00 | 8 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 56 | 56 | 72 | 67 | 71 | 60 | 60 | 52 | #N/A | #N/A
2022-08-02 06:00 | 8 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 59 | 59 | 74 | 68 | 73 | 62 | 63 | 57 | #N/A | #N/A
2022-08-02 07:00 | 8 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 61 | 62 | 75 | 72 | 76 | 66 | 66 | 61 | #N/A | #N/A
2022-08-02 08:00 | 8 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 65 | 65 | 76 | 73 | 80 | 71 | 69 | 66 | #N/A | #N/A
2022-08-02 09:00 | 8 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 67 | 68 | 75 | 75 | 83 | 74 | 72 | 72 | #N/A | #N/A
2022-08-02 10:00 | 8 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 69 | 72 | 74 | 77 | 86 | 76 | 75 | 76 | #N/A | #N/A
2022-08-02 11:00 | 8 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 71 | 75 | 73 | 80 | 89 | 78 | 77 | 79 | #N/A | #N/A
2022-08-02 12:00 | 8 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 71 | 77 | 74 | 80 | 88 | 80 | 70 | 80 | #N/A | #N/A
2022-08-02 13:00 | 8 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 72 | 74 | 73 | 83 | 86 | 82 | 75 | 81 | #N/A | #N/A
2022-08-02 14:00 | 8 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 73 | 72 | 69 | 81 | 86 | 82 | 76 | 82 | #N/A | #N/A
2022-08-02 15:00 | 8 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 74 | 75 | 73 | 80 | 84 | 83 | 75 | 83 | #N/A | #N/A
2022-08-02 16:00 | 8 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 73 | 75 | 73 | 82 | 83 | 81 | 75 | 83 | #N/A | #N/A
2022-08-02 17:00 | 8 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 71 | 72 | 73 | 79 | 81 | 81 | 75 | 81 | #N/A | #N/A
2022-08-02 18:00 | 8 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 69 | 72 | 69 | 77 | 80 | 79 | 69 | 77 | #N/A | #N/A
2022-08-02 19:00 | 8 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 65 | 69 | 70 | 75 | 79 | 75 | 67 | 74 | #N/A | #N/A
2022-08-02 20:00 | 8 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 64 | 68 | 71 | 74 | 77 | 73 | 68 | 71 | #N/A | #N/A
2022-08-02 21:00 | 8 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 62 | 66 | 70 | 72 | 76 | 74 | 67 | 65 | #N/A | #N/A
2022-08-02 22:00 | 8 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 60 | 69 | 70 | 71 | 77 | 71 | 66 | 64 | #N/A | #N/A
2022-08-02 23:00 | 8 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 58 | 69 | 70 | 72 | 77 | 71 | 67 | 61 | #N/A | #N/A
2022-08-03 | 8 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 57 | 67 | 70 | 71 | 77 | 71 | 66 | 59 | #N/A | #N/A
2022-08-03 01:00 | 8 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 57 | 68 | 70 | 70 | 77 | 68 | 66 | 58 | #N/A | #N/A
2022-08-03 02:00 | 8 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 58 | 66 | 70 | 70 | 77 | 66 | 66 | 58 | #N/A | #N/A
2022-08-03 03:00 | 8 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 56 | 65 | 70 | 70 | 77 | 66 | 65 | 57 | #N/A | #N/A
2022-08-03 04:00 | 8 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 55 | 63 | 71 | 70 | 77 | 66 | 65 | 55 | #N/A | #N/A
2022-08-03 05:00 | 8 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 55 | 64 | 71 | 68 | 78 | 65 | 65 | 57 | #N/A | #N/A
2022-08-03 06:00 | 8 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 57 | 67 | 72 | 73 | 78 | 68 | 66 | 60 | #N/A | #N/A
2022-08-03 07:00 | 8 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 63 | 70 | 73 | 78 | 79 | 72 | 69 | 65 | #N/A | #N/A
2022-08-03 08:00 | 8 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 67 | 72 | 76 | 81 | 83 | 76 | 72 | 69 | #N/A | #N/A
2022-08-03 09:00 | 8 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 72 | 74 | 76 | 83 | 86 | 79 | 75 | 75 | #N/A | #N/A
2022-08-03 10:00 | 8 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 74 | 74 | 77 | 86 | 88 | 80 | 77 | 80 | #N/A | #N/A
2022-08-03 11:00 | 8 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 76 | 78 | 78 | 87 | 90 | 82 | 79 | 82 | #N/A | #N/A
2022-08-03 12:00 | 8 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 77 | 80 | 79 | 86 | 92 | 85 | 83 | 84 | #N/A | #N/A
2022-08-03 13:00 | 8 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 77 | 83 | 81 | 88 | 93 | 85 | 83 | 84 | #N/A | #N/A
2022-08-03 14:00 | 8 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 78 | 83 | 80 | 89 | 93 | 86 | 85 | 87 | #N/A | #N/A
2022-08-03 15:00 | 8 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 78 | 83 | 79 | 89 | 93 | 86 | 85 | 85 | #N/A | #N/A
2022-08-03 16:00 | 8 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 76 | 81 | 80 | 89 | 92 | 86 | 84 | 84 | #N/A | #N/A
2022-08-03 17:00 | 8 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 76 | 77 | 80 | 87 | 90 | 84 | 83 | 83 | #N/A | #N/A
2022-08-03 18:00 | 8 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 71 | 77 | 77 | 84 | 87 | 82 | 81 | 78 | #N/A | #N/A
2022-08-03 19:00 | 8 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 68 | 74 | 75 | 80 | 82 | 78 | 78 | 71 | #N/A | #N/A
2022-08-03 20:00 | 8 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 67 | 74 | 73 | 79 | 85 | 76 | 75 | 72 | #N/A | #N/A
2022-08-03 21:00 | 8 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 66 | 72 | 71 | 77 | 82 | 75 | 76 | 68 | #N/A | #N/A
2022-08-03 22:00 | 8 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 65 | 70 | 69 | 76 | 80 | 74 | 76 | 65 | #N/A | #N/A
2022-08-03 23:00 | 8 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 64 | 70 | 68 | 75 | 79 | 74 | 75 | 63 | #N/A | #N/A
2022-08-04 | 8 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 63 | 71 | 68 | 73 | 78 | 74 | 74 | 63 | #N/A | #N/A
2022-08-04 01:00 | 8 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 60 | 70 | 67 | 72 | 75 | 73 | 74 | 61 | #N/A | #N/A
2022-08-04 02:00 | 8 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 59 | 70 | 66 | 71 | 77 | 73 | 73 | 61 | #N/A | #N/A
2022-08-04 03:00 | 8 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 58 | 70 | 66 | 71 | 76 | 73 | 72 | 61 | #N/A | #N/A
2022-08-04 04:00 | 8 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 71 | 66 | 69 | 76 | 73 | 72 | 61 | #N/A | #N/A
2022-08-04 05:00 | 8 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 57 | 71 | 66 | 71 | 76 | 73 | 72 | 60 | #N/A | #N/A
2022-08-04 06:00 | 8 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 62 | 71 | 69 | 75 | 80 | 74 | 73 | 64 | #N/A | #N/A
2022-08-04 07:00 | 8 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 67 | 72 | 75 | 78 | 84 | 77 | 74 | 68 | #N/A | #N/A
2022-08-04 08:00 | 8 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 70 | 73 | 79 | 82 | 87 | 80 | 77 | 72 | #N/A | #N/A
2022-08-04 09:00 | 8 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 75 | 77 | 83 | 85 | 89 | 82 | 80 | 76 | #N/A | #N/A
2022-08-04 10:00 | 8 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 78 | 80 | 83 | 87 | 91 | 83 | 83 | 80 | #N/A | #N/A
2022-08-04 11:00 | 8 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 80 | 77 | 83 | 89 | 93 | 85 | 84 | 84 | #N/A | #N/A
2022-08-04 12:00 | 8 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 80 | 80 | 81 | 90 | 95 | 88 | 86 | 85 | #N/A | #N/A
2022-08-04 13:00 | 8 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 78 | 79 | 79 | 92 | 93 | 86 | 88 | 85 | #N/A | #N/A
2022-08-04 14:00 | 8 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 91 | 82 | 81 | 80 | 91 | 97 | 87 | 86 | 87 | #N/A | #N/A
2022-08-04 15:00 | 8 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 92 | 80 | 80 | 80 | 90 | 95 | 86 | 86 | 88 | #N/A | #N/A
2022-08-04 16:00 | 8 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 93 | 77 | 79 | 80 | 89 | 94 | 84 | 87 | 86 | #N/A | #N/A
2022-08-04 17:00 | 8 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 89 | 78 | 73 | 79 | 88 | 92 | 83 | 85 | 84 | #N/A | #N/A
2022-08-04 18:00 | 8 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 84 | 75 | 71 | 79 | 86 | 88 | 79 | 82 | 80 | #N/A | #N/A
2022-08-04 19:00 | 8 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 71 | 71 | 77 | 85 | 87 | 75 | 82 | 75 | #N/A | #N/A
2022-08-04 20:00 | 8 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 68 | 71 | 77 | 85 | 84 | 73 | 82 | 72 | #N/A | #N/A
2022-08-04 21:00 | 8 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 69 | 70 | 77 | 84 | 80 | 73 | 83 | 71 | #N/A | #N/A
2022-08-04 22:00 | 8 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 66 | 70 | 75 | 84 | 80 | 72 | 75 | 72 | #N/A | #N/A
2022-08-04 23:00 | 8 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 64 | 70 | 74 | 81 | 79 | 71 | 74 | 69 | #N/A | #N/A
2022-08-05 | 8 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 63 | 70 | 73 | 76 | 78 | 71 | 73 | 67 | #N/A | #N/A
2022-08-05 01:00 | 8 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 62 | 70 | 72 | 77 | 77 | 70 | 73 | 66 | #N/A | #N/A
2022-08-05 02:00 | 8 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 61 | 70 | 71 | 76 | 76 | 71 | 73 | 67 | #N/A | #N/A
2022-08-05 03:00 | 8 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 60 | 69 | 71 | 75 | 75 | 72 | 73 | 65 | #N/A | #N/A
2022-08-05 04:00 | 8 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 61 | 69 | 70 | 74 | 74 | 72 | 72 | 64 | #N/A | #N/A
2022-08-05 05:00 | 8 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 60 | 69 | 69 | 74 | 75 | 72 | 73 | 66 | #N/A | #N/A
2022-08-05 06:00 | 8 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 64 | 71 | 69 | 77 | 78 | 73 | 74 | 67 | #N/A | #N/A
2022-08-05 07:00 | 8 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 68 | 72 | 68 | 81 | 84 | 75 | 74 | 69 | #N/A | #N/A
2022-08-05 08:00 | 8 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 73 | 75 | 68 | 83 | 87 | 78 | 76 | 72 | #N/A | #N/A
2022-08-05 09:00 | 8 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 75 | 76 | 69 | 86 | 91 | 80 | 79 | 74 | #N/A | #N/A
2022-08-05 10:00 | 8 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 77 | 78 | 70 | 87 | 93 | 82 | 81 | 78 | #N/A | #N/A
2022-08-05 11:00 | 8 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 79 | 80 | 69 | 88 | 93 | 85 | 83 | 82 | #N/A | #N/A
2022-08-05 12:00 | 8 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 81 | 83 | 69 | 88 | 93 | 86 | 83 | 85 | #N/A | #N/A
2022-08-05 13:00 | 8 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 80 | 82 | 69 | 90 | 75 | 88 | 83 | 86 | #N/A | #N/A
2022-08-05 14:00 | 8 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 80 | 83 | 70 | 91 | 75 | 88 | 86 | 87 | #N/A | #N/A
2022-08-05 15:00 | 8 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 78 | 82 | 70 | 91 | 77 | 88 | 87 | 88 | #N/A | #N/A
2022-08-05 16:00 | 8 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 77 | 81 | 70 | 89 | 77 | 87 | 89 | 87 | #N/A | #N/A
2022-08-05 17:00 | 8 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 75 | 79 | 69 | 88 | 74 | 86 | 84 | 84 | #N/A | #N/A
2022-08-05 18:00 | 8 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 73 | 80 | 68 | 86 | 74 | 83 | 76 | 80 | #N/A | #N/A
2022-08-05 19:00 | 8 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 69 | 75 | 67 | 80 | 73 | 81 | 69 | 75 | #N/A | #N/A
2022-08-05 20:00 | 8 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 68 | 73 | 66 | 80 | 73 | 79 | 69 | 76 | #N/A | #N/A
2022-08-05 21:00 | 8 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 67 | 71 | 63 | 79 | 73 | 77 | 69 | 72 | #N/A | #N/A
2022-08-05 22:00 | 8 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 65 | 70 | 62 | 79 | 72 | 74 | 69 | 70 | #N/A | #N/A
2022-08-05 23:00 | 8 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 65 | 69 | 61 | 80 | 71 | 73 | 68 | 69 | #N/A | #N/A
2022-08-06 | 8 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 64 | 68 | 60 | 79 | 71 | 72 | 67 | 67 | #N/A | #N/A
2022-08-06 01:00 | 8 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 62 | 67 | 59 | 76 | 72 | 71 | 68 | 67 | #N/A | #N/A
2022-08-06 02:00 | 8 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 63 | 67 | 58 | 75 | 71 | 69 | 67 | 68 | #N/A | #N/A
2022-08-06 03:00 | 8 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 61 | 67 | 58 | 74 | 71 | 68 | 66 | 68 | #N/A | #N/A
2022-08-06 04:00 | 8 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 59 | 68 | 57 | 74 | 69 | 67 | 66 | 66 | #N/A | #N/A
2022-08-06 05:00 | 8 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 60 | 69 | 58 | 75 | 68 | 67 | 67 | 66 | #N/A | #N/A
2022-08-06 06:00 | 8 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 61 | 70 | 60 | 79 | 67 | 68 | 68 | 68 | #N/A | #N/A
2022-08-06 07:00 | 8 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 66 | 69 | 66 | 81 | 68 | 70 | 72 | 72 | #N/A | #N/A
2022-08-06 08:00 | 8 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 69 | 68 | 70 | 82 | 68 | 72 | 76 | 77 | #N/A | #N/A
2022-08-06 09:00 | 8 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 71 | 68 | 71 | 83 | 70 | 74 | 79 | 79 | #N/A | #N/A
2022-08-06 10:00 | 8 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 76 | 68 | 73 | 87 | 72 | 78 | 82 | 81 | #N/A | #N/A
2022-08-06 11:00 | 8 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 76 | 72 | 74 | 88 | 75 | 81 | 83 | 82 | #N/A | #N/A
2022-08-06 12:00 | 8 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 76 | 74 | 74 | 89 | 77 | 82 | 85 | 86 | #N/A | #N/A
2022-08-06 13:00 | 8 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 78 | 77 | 74 | 89 | 77 | 83 | 86 | 87 | #N/A | #N/A
2022-08-06 14:00 | 8 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 78 | 68 | 75 | 90 | 76 | 84 | 86 | 88 | #N/A | #N/A
2022-08-06 15:00 | 8 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 76 | 73 | 74 | 90 | 77 | 72 | 86 | 86 | #N/A | #N/A
2022-08-06 16:00 | 8 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 76 | 75 | 75 | 89 | 76 | 73 | 82 | 86 | #N/A | #N/A
2022-08-06 17:00 | 8 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 72 | 74 | 74 | 81 | 75 | 73 | 74 | 84 | #N/A | #N/A
2022-08-06 18:00 | 8 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 71 | 72 | 72 | 76 | 73 | 72 | 73 | 81 | #N/A | #N/A
2022-08-06 19:00 | 8 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 68 | 66 | 70 | 75 | 72 | 71 | 71 | 79 | #N/A | #N/A
2022-08-06 20:00 | 8 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 67 | 64 | 68 | 73 | 70 | 71 | 70 | 76 | #N/A | #N/A
2022-08-06 21:00 | 8 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 66 | 62 | 66 | 71 | 71 | 71 | 70 | 72 | #N/A | #N/A
2022-08-06 22:00 | 8 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 65 | 63 | 65 | 71 | 70 | 69 | 68 | 67 | #N/A | #N/A
2022-08-06 23:00 | 8 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 65 | 62 | 65 | 70 | 68 | 67 | 68 | 66 | #N/A | #N/A
2022-08-07 | 8 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 61 | 65 | 70 | 68 | 65 | 67 | 63 | #N/A | #N/A
2022-08-07 01:00 | 8 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 58 | 63 | 70 | 65 | 64 | 68 | 64 | #N/A | #N/A
2022-08-07 02:00 | 8 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 64 | 56 | 63 | 69 | 66 | 63 | 68 | 61 | #N/A | #N/A
2022-08-07 03:00 | 8 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 62 | 56 | 62 | 69 | 66 | 63 | 67 | 60 | #N/A | #N/A
2022-08-07 04:00 | 8 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 63 | 56 | 60 | 70 | 65 | 62 | 65 | 59 | #N/A | #N/A
2022-08-07 05:00 | 8 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 62 | 55 | 60 | 71 | 66 | 61 | 65 | 60 | #N/A | #N/A
2022-08-07 06:00 | 8 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 66 | 55 | 64 | 72 | 71 | 60 | 65 | 64 | #N/A | #N/A
2022-08-07 07:00 | 8 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 69 | 55 | 70 | 70 | 74 | 60 | 65 | 67 | #N/A | #N/A
2022-08-07 08:00 | 8 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 68 | 58 | 75 | 70 | 76 | 61 | 67 | 75 | #N/A | #N/A
2022-08-07 09:00 | 8 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 67 | 53 | 77 | 70 | 78 | 61 | 65 | 76 | #N/A | #N/A
2022-08-07 10:00 | 8 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 71 | 54 | 78 | 71 | 80 | 62 | 65 | 80 | #N/A | #N/A
2022-08-07 11:00 | 8 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 72 | 59 | 80 | 74 | 81 | 62 | 66 | 82 | #N/A | #N/A
2022-08-07 12:00 | 8 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 76 | 55 | 81 | 77 | 83 | 64 | 67 | 84 | #N/A | #N/A
2022-08-07 13:00 | 8 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 75 | 58 | 81 | 74 | 85 | 64 | 67 | 86 | #N/A | #N/A
2022-08-07 14:00 | 8 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 75 | 58 | 81 | 74 | 84 | 64 | 65 | 87 | #N/A | #N/A
2022-08-07 15:00 | 8 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 71 | 57 | 81 | 73 | 83 | 66 | 63 | 87 | #N/A | #N/A
2022-08-07 16:00 | 8 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 66 | 58 | 79 | 72 | 82 | 65 | 63 | 86 | #N/A | #N/A
2022-08-07 17:00 | 8 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 65 | 57 | 78 | 72 | 80 | 66 | 61 | 84 | #N/A | #N/A
2022-08-07 18:00 | 8 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 65 | 55 | 78 | 70 | 78 | 64 | 60 | 81 | #N/A | #N/A
2022-08-07 19:00 | 8 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 65 | 51 | 76 | 66 | 76 | 63 | 59 | 79 | #N/A | #N/A
2022-08-07 20:00 | 8 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 64 | 50 | 73 | 64 | 75 | 62 | 57 | 78 | #N/A | #N/A
2022-08-07 21:00 | 8 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 64 | 50 | 73 | 62 | 73 | 58 | 55 | 70 | #N/A | #N/A
2022-08-07 22:00 | 8 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 65 | 50 | 73 | 60 | 72 | 55 | 54 | 70 | #N/A | #N/A
2022-08-07 23:00 | 8 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 64 | 47 | 73 | 61 | 72 | 54 | 52 | 68 | #N/A | #N/A
2022-08-08 | 8 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 46 | 73 | 55 | 72 | 53 | 50 | 68 | #N/A | #N/A
2022-08-08 01:00 | 8 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 47 | 71 | 53 | 72 | 52 | 49 | 66 | #N/A | #N/A
2022-08-08 02:00 | 8 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 48 | 72 | 52 | 71 | 50 | 48 | 65 | #N/A | #N/A
2022-08-08 03:00 | 8 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 64 | 46 | 70 | 51 | 71 | 50 | 47 | 68 | #N/A | #N/A
2022-08-08 04:00 | 8 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 64 | 44 | 71 | 52 | 71 | 49 | 47 | 69 | #N/A | #N/A
2022-08-08 05:00 | 8 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 45 | 73 | 53 | 72 | 49 | 48 | 69 | #N/A | #N/A
2022-08-08 06:00 | 8 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 65 | 49 | 72 | 55 | 73 | 51 | 51 | 70 | #N/A | #N/A
2022-08-08 07:00 | 8 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 67 | 50 | 73 | 61 | 75 | 55 | 55 | 73 | #N/A | #N/A
2022-08-08 08:00 | 8 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 70 | 52 | 73 | 65 | 78 | 54 | 58 | 73 | #N/A | #N/A
2022-08-08 09:00 | 8 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 74 | 53 | 74 | 67 | 82 | 59 | 62 | 75 | #N/A | #N/A
2022-08-08 10:00 | 8 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 76 | 55 | 76 | 68 | 84 | 58 | 63 | 77 | #N/A | #N/A
2022-08-08 11:00 | 8 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 77 | 56 | 73 | 68 | 86 | 62 | 65 | 78 | #N/A | #N/A
2022-08-08 12:00 | 8 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 79 | 56 | 73 | 70 | 87 | 60 | 61 | 82 | #N/A | #N/A
2022-08-08 13:00 | 8 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 80 | 56 | 73 | 67 | 87 | 61 | 63 | 83 | #N/A | #N/A
2022-08-08 14:00 | 8 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 82 | 57 | 73 | 68 | 89 | 62 | 64 | 86 | #N/A | #N/A
2022-08-08 15:00 | 8 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 78 | 57 | 73 | 70 | 88 | 63 | 64 | 85 | #N/A | #N/A
2022-08-08 16:00 | 8 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 80 | 57 | 73 | 68 | 88 | 64 | 64 | 85 | #N/A | #N/A
2022-08-08 17:00 | 8 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 79 | 56 | 73 | 67 | 86 | 63 | 63 | 84 | #N/A | #N/A
2022-08-08 18:00 | 8 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 76 | 55 | 72 | 64 | 83 | 62 | 62 | 82 | #N/A | #N/A
2022-08-08 19:00 | 8 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 71 | 52 | 70 | 62 | 82 | 59 | 57 | 77 | #N/A | #N/A
2022-08-08 20:00 | 8 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 69 | 49 | 69 | 59 | 80 | 55 | 57 | 78 | #N/A | #N/A
2022-08-08 21:00 | 8 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 68 | 45 | 69 | 57 | 79 | 55 | 54 | 72 | #N/A | #N/A
2022-08-08 22:00 | 8 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 65 | 45 | 69 | 56 | 78 | 53 | 53 | 70 | #N/A | #N/A
2022-08-08 23:00 | 8 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 65 | 44 | 69 | 55 | 80 | 52 | 52 | 69 | #N/A | #N/A
2022-08-09 | 8 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 65 | 44 | 68 | 54 | 79 | 52 | 50 | 71 | #N/A | #N/A
2022-08-09 01:00 | 8 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 64 | 43 | 68 | 53 | 77 | 50 | 49 | 72 | #N/A | #N/A
2022-08-09 02:00 | 8 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 40 | 69 | 52 | 77 | 49 | 49 | 71 | #N/A | #N/A
2022-08-09 03:00 | 8 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 61 | 40 | 70 | 53 | 76 | 48 | 47 | 71 | #N/A | #N/A
2022-08-09 04:00 | 8 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 59 | 40 | 69 | 53 | 75 | 47 | 47 | 70 | #N/A | #N/A
2022-08-09 05:00 | 8 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 39 | 65 | 52 | 76 | 48 | 47 | 71 | #N/A | #N/A
2022-08-09 06:00 | 8 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 65 | 45 | 66 | 57 | 76 | 52 | 50 | 73 | #N/A | #N/A
2022-08-09 07:00 | 8 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 69 | 53 | 67 | 63 | 78 | 56 | 56 | 73 | #N/A | #N/A
2022-08-09 08:00 | 8 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 73 | 56 | 69 | 65 | 79 | 63 | 60 | 73 | #N/A | #N/A
2022-08-09 09:00 | 8 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 76 | 62 | 69 | 69 | 83 | 67 | 64 | 74 | #N/A | #N/A
2022-08-09 10:00 | 8 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 79 | 64 | 71 | 70 | 83 | 70 | 67 | 77 | #N/A | #N/A
2022-08-09 11:00 | 8 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 81 | 67 | 71 | 71 | 85 | 71 | 68 | 82 | #N/A | #N/A
2022-08-09 12:00 | 8 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 83 | 70 | 74 | 73 | 87 | 74 | 70 | 82 | #N/A | #N/A
2022-08-09 13:00 | 8 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 84 | 71 | 74 | 73 | 88 | 76 | 70 | 83 | #N/A | #N/A
2022-08-09 14:00 | 8 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 83 | 70 | 75 | 76 | 88 | 76 | 72 | 85 | #N/A | #N/A
2022-08-09 15:00 | 8 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 81 | 67 | 77 | 75 | 90 | 78 | 72 | 84 | #N/A | #N/A
2022-08-09 16:00 | 8 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 82 | 66 | 78 | 74 | 89 | 77 | 71 | 84 | #N/A | #N/A
2022-08-09 17:00 | 8 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 81 | 68 | 78 | 72 | 82 | 76 | 70 | 83 | #N/A | #N/A
2022-08-09 18:00 | 8 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 78 | 64 | 77 | 70 | 80 | 73 | 67 | 80 | #N/A | #N/A
2022-08-09 19:00 | 8 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 76 | 58 | 70 | 65 | 78 | 68 | 63 | 79 | #N/A | #N/A
2022-08-09 20:00 | 8 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 74 | 54 | 70 | 62 | 79 | 65 | 61 | 79 | #N/A | #N/A
2022-08-09 21:00 | 8 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 73 | 53 | 70 | 60 | 75 | 64 | 58 | 78 | #N/A | #N/A
2022-08-09 22:00 | 8 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 68 | 51 | 70 | 59 | 75 | 61 | 57 | 76 | #N/A | #N/A
2022-08-09 23:00 | 8 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 67 | 48 | 70 | 58 | 76 | 58 | 56 | 76 | #N/A | #N/A
2022-08-10 | 8 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 49 | 70 | 57 | 75 | 57 | 55 | 76 | #N/A | #N/A
2022-08-10 01:00 | 8 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 64 | 46 | 68 | 56 | 75 | 57 | 53 | 75 | #N/A | #N/A
2022-08-10 02:00 | 8 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 47 | 67 | 54 | 74 | 55 | 52 | 74 | #N/A | #N/A
2022-08-10 03:00 | 8 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 61 | 44 | 66 | 54 | 73 | 54 | 52 | 75 | #N/A | #N/A
2022-08-10 04:00 | 8 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 62 | 45 | 65 | 53 | 73 | 54 | 51 | 70 | #N/A | #N/A
2022-08-10 05:00 | 8 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 62 | 47 | 64 | 53 | 74 | 53 | 51 | 70 | #N/A | #N/A
2022-08-10 06:00 | 8 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 51 | 64 | 57 | 75 | 58 | 54 | 70 | #N/A | #N/A
2022-08-10 07:00 | 8 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 69 | 59 | 65 | 62 | 77 | 62 | 60 | 70 | #N/A | #N/A
2022-08-10 08:00 | 8 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 74 | 65 | 66 | 68 | 79 | 68 | 64 | 71 | #N/A | #N/A
2022-08-10 09:00 | 8 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 78 | 67 | 66 | 71 | 80 | 73 | 70 | 72 | #N/A | #N/A
2022-08-10 10:00 | 8 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 81 | 72 | 66 | 74 | 83 | 76 | 73 | 72 | #N/A | #N/A
2022-08-10 11:00 | 8 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 83 | 73 | 71 | 73 | 86 | 77 | 74 | 73 | #N/A | #N/A
2022-08-10 12:00 | 8 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 83 | 75 | 72 | 75 | 87 | 77 | 75 | 74 | #N/A | #N/A
2022-08-10 13:00 | 8 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 84 | 75 | 72 | 77 | 84 | 80 | 76 | 75 | #N/A | #N/A
2022-08-10 14:00 | 8 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 80 | 75 | 72 | 73 | 83 | 81 | 76 | 74 | #N/A | #N/A
2022-08-10 15:00 | 8 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 83 | 75 | 73 | 75 | 83 | 80 | 76 | 73 | #N/A | #N/A
2022-08-10 16:00 | 8 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 80 | 76 | 73 | 72 | 80 | 81 | 74 | 74 | #N/A | #N/A
2022-08-10 17:00 | 8 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 79 | 73 | 73 | 71 | 77 | 77 | 71 | 71 | #N/A | #N/A
2022-08-10 18:00 | 8 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 76 | 70 | 71 | 70 | 73 | 75 | 69 | 71 | #N/A | #N/A
2022-08-10 19:00 | 8 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 73 | 62 | 68 | 69 | 71 | 72 | 66 | 70 | #N/A | #N/A
2022-08-10 20:00 | 8 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 72 | 61 | 65 | 66 | 70 | 70 | 64 | 69 | #N/A | #N/A
2022-08-10 21:00 | 8 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 72 | 56 | 64 | 67 | 68 | 64 | 62 | 68 | #N/A | #N/A
2022-08-10 22:00 | 8 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 70 | 55 | 63 | 67 | 67 | 66 | 61 | 69 | #N/A | #N/A
2022-08-10 23:00 | 8 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 70 | 53 | 62 | 66 | 67 | 64 | 60 | 68 | #N/A | #N/A
2022-08-11 | 8 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 69 | 53 | 62 | 66 | 66 | 62 | 59 | 68 | #N/A | #N/A
2022-08-11 01:00 | 8 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 69 | 52 | 61 | 66 | 65 | 63 | 59 | 67 | #N/A | #N/A
2022-08-11 02:00 | 8 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 69 | 53 | 60 | 66 | 64 | 62 | 58 | 67 | #N/A | #N/A
2022-08-11 03:00 | 8 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 67 | 52 | 59 | 64 | 63 | 60 | 59 | 66 | #N/A | #N/A
2022-08-11 04:00 | 8 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 66 | 53 | 59 | 62 | 63 | 60 | 59 | 66 | #N/A | #N/A
2022-08-11 05:00 | 8 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 67 | 54 | 60 | 61 | 63 | 60 | 59 | 67 | #N/A | #N/A
2022-08-11 06:00 | 8 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 67 | 56 | 62 | 61 | 67 | 61 | 61 | 68 | #N/A | #N/A
2022-08-11 07:00 | 8 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 69 | 58 | 68 | 61 | 72 | 64 | 62 | 72 | #N/A | #N/A
2022-08-11 08:00 | 8 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 69 | 63 | 70 | 63 | 75 | 65 | 63 | 75 | #N/A | #N/A
2022-08-11 09:00 | 8 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 71 | 68 | 72 | 63 | 78 | 69 | 63 | 76 | #N/A | #N/A
2022-08-11 10:00 | 8 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 74 | 68 | 75 | 63 | 80 | 72 | 67 | 80 | #N/A | #N/A
2022-08-11 11:00 | 8 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 68 | 70 | 73 | 64 | 83 | 72 | 69 | 83 | #N/A | #N/A
2022-08-11 12:00 | 8 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 71 | 71 | 73 | 67 | 84 | 74 | 69 | 84 | #N/A | #N/A
2022-08-11 13:00 | 8 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 77 | 72 | 73 | 69 | 86 | 75 | 68 | 87 | #N/A | #N/A
2022-08-11 14:00 | 8 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 78 | 72 | 73 | 70 | 85 | 74 | 65 | 85 | #N/A | #N/A
2022-08-11 15:00 | 8 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 78 | 72 | 73 | 69 | 84 | 74 | 63 | 87 | #N/A | #N/A
2022-08-11 16:00 | 8 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 77 | 70 | 73 | 66 | 82 | 73 | 63 | 87 | #N/A | #N/A
2022-08-11 17:00 | 8 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 74 | 69 | 73 | 65 | 82 | 71 | 63 | 85 | #N/A | #N/A
2022-08-11 18:00 | 8 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 67 | 71 | 65 | 79 | 69 | 62 | 80 | #N/A | #N/A
2022-08-11 19:00 | 8 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 66 | 62 | 70 | 65 | 78 | 67 | 62 | 77 | #N/A | #N/A
2022-08-11 20:00 | 8 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 62 | 68 | 64 | 74 | 66 | 62 | 75 | #N/A | #N/A
2022-08-11 21:00 | 8 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 63 | 61 | 67 | 64 | 72 | 65 | 61 | 73 | #N/A | #N/A
2022-08-11 22:00 | 8 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 62 | 60 | 64 | 64 | 71 | 65 | 61 | 69 | #N/A | #N/A
2022-08-11 23:00 | 8 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 59 | 63 | 63 | 69 | 63 | 61 | 67 | #N/A | #N/A
2022-08-12 | 8 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 60 | 60 | 62 | 64 | 69 | 63 | 61 | 68 | #N/A | #N/A
2022-08-12 01:00 | 8 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 60 | 60 | 62 | 64 | 68 | 62 | 60 | 66 | #N/A | #N/A
2022-08-12 02:00 | 8 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 59 | 59 | 66 | 64 | 68 | 61 | 60 | 65 | #N/A | #N/A
2022-08-12 03:00 | 8 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 58 | 57 | 67 | 63 | 68 | 58 | 60 | 65 | #N/A | #N/A
2022-08-12 04:00 | 8 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 57 | 57 | 64 | 63 | 67 | 59 | 60 | 65 | #N/A | #N/A
2022-08-12 05:00 | 8 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 58 | 57 | 65 | 63 | 67 | 57 | 60 | 66 | #N/A | #N/A
2022-08-12 06:00 | 8 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 60 | 59 | 68 | 64 | 69 | 60 | 61 | 69 | #N/A | #N/A
2022-08-12 07:00 | 8 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 64 | 62 | 69 | 66 | 71 | 66 | 62 | 70 | #N/A | #N/A
2022-08-12 08:00 | 8 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 66 | 65 | 74 | 66 | 75 | 70 | 63 | 72 | #N/A | #N/A
2022-08-12 09:00 | 8 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 69 | 67 | 77 | 68 | 76 | 73 | 64 | 73 | #N/A | #N/A
2022-08-12 10:00 | 8 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 72 | 69 | 80 | 70 | 78 | 77 | 65 | 74 | #N/A | #N/A
2022-08-12 11:00 | 8 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 75 | 70 | 79 | 73 | 78 | 79 | 66 | 79 | #N/A | #N/A
2022-08-12 12:00 | 8 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 76 | 69 | 79 | 74 | 80 | 80 | 66 | 79 | #N/A | #N/A
2022-08-12 13:00 | 8 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 77 | 71 | 79 | 74 | 84 | 79 | 67 | 79 | #N/A | #N/A
2022-08-12 14:00 | 8 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 77 | 73 | 79 | 75 | 84 | 80 | 69 | 82 | #N/A | #N/A
2022-08-12 15:00 | 8 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 77 | 74 | 80 | 73 | 83 | 82 | 70 | 81 | #N/A | #N/A
2022-08-12 16:00 | 8 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 76 | 72 | 80 | 72 | 81 | 82 | 69 | 81 | #N/A | #N/A
2022-08-12 17:00 | 8 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 73 | 71 | 78 | 72 | 78 | 80 | 69 | 78 | #N/A | #N/A
2022-08-12 18:00 | 8 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 70 | 69 | 76 | 71 | 74 | 76 | 68 | 75 | #N/A | #N/A
2022-08-12 19:00 | 8 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 67 | 61 | 75 | 71 | 71 | 73 | 68 | 66 | #N/A | #N/A
2022-08-12 20:00 | 8 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 59 | 74 | 70 | 68 | 71 | 67 | 65 | #N/A | #N/A
2022-08-12 21:00 | 8 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 62 | 57 | 73 | 70 | 65 | 69 | 67 | 64 | #N/A | #N/A
2022-08-12 22:00 | 8 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 61 | 56 | 73 | 69 | 63 | 69 | 66 | 62 | #N/A | #N/A
2022-08-12 23:00 | 8 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 59 | 53 | 73 | 69 | 63 | 67 | 65 | 61 | #N/A | #N/A
2022-08-13 | 8 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 59 | 52 | 72 | 70 | 62 | 66 | 66 | 59 | #N/A | #N/A
2022-08-13 01:00 | 8 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 59 | 51 | 71 | 70 | 62 | 64 | 66 | 57 | #N/A | #N/A
2022-08-13 02:00 | 8 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 57 | 50 | 71 | 70 | 61 | 62 | 66 | 56 | #N/A | #N/A
2022-08-13 03:00 | 8 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 54 | 51 | 69 | 69 | 61 | 63 | 66 | 56 | #N/A | #N/A
2022-08-13 04:00 | 8 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 53 | 50 | 69 | 69 | 60 | 63 | 65 | 54 | #N/A | #N/A
2022-08-13 05:00 | 8 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 54 | 51 | 69 | 68 | 62 | 62 | 66 | 53 | #N/A | #N/A
2022-08-13 06:00 | 8 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 60 | 54 | 70 | 71 | 66 | 63 | 67 | 57 | #N/A | #N/A
2022-08-13 07:00 | 8 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 65 | 61 | 73 | 73 | 72 | 67 | 69 | 61 | #N/A | #N/A
2022-08-13 08:00 | 8 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 70 | 67 | 75 | 74 | 75 | 73 | 70 | 66 | #N/A | #N/A
2022-08-13 09:00 | 8 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 75 | 69 | 78 | 76 | 77 | 77 | 72 | 70 | #N/A | #N/A
2022-08-13 10:00 | 8 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 78 | 70 | 81 | 78 | 79 | 80 | 74 | 73 | #N/A | #N/A
2022-08-13 11:00 | 8 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 82 | 76 | 83 | 81 | 79 | 80 | 76 | 77 | #N/A | #N/A
2022-08-13 12:00 | 8 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 83 | 76 | 85 | 81 | 81 | 81 | 77 | 77 | #N/A | #N/A
2022-08-13 13:00 | 8 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 83 | 76 | 86 | 82 | 81 | 83 | 79 | 80 | #N/A | #N/A
2022-08-13 14:00 | 8 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 83 | 76 | 85 | 82 | 78 | 82 | 81 | 80 | #N/A | #N/A
2022-08-13 15:00 | 8 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 83 | 74 | 86 | 83 | 80 | 83 | 80 | 80 | #N/A | #N/A
2022-08-13 16:00 | 8 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 82 | 73 | 86 | 82 | 79 | 82 | 80 | 80 | #N/A | #N/A
2022-08-13 17:00 | 8 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 78 | 69 | 84 | 81 | 76 | 80 | 79 | 79 | #N/A | #N/A
2022-08-13 18:00 | 8 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 78 | 64 | 82 | 78 | 72 | 78 | 75 | 73 | #N/A | #N/A
2022-08-13 19:00 | 8 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 76 | 63 | 79 | 75 | 69 | 75 | 72 | 69 | #N/A | #N/A
2022-08-13 20:00 | 8 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 75 | 62 | 78 | 73 | 66 | 72 | 69 | 66 | #N/A | #N/A
2022-08-13 21:00 | 8 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 74 | 62 | 77 | 73 | 64 | 69 | 68 | 65 | #N/A | #N/A
2022-08-13 22:00 | 8 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 73 | 60 | 76 | 71 | 64 | 68 | 68 | 64 | #N/A | #N/A
2022-08-13 23:00 | 8 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 73 | 59 | 75 | 68 | 62 | 67 | 67 | 63 | #N/A | #N/A
2022-08-14 | 8 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 73 | 56 | 73 | 69 | 61 | 65 | 66 | 68 | #N/A | #N/A
2022-08-14 01:00 | 8 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 73 | 55 | 72 | 67 | 61 | 62 | 65 | 70 | #N/A | #N/A
2022-08-14 02:00 | 8 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 72 | 54 | 72 | 66 | 62 | 62 | 64 | 70 | #N/A | #N/A
2022-08-14 03:00 | 8 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 71 | 53 | 71 | 66 | 63 | 62 | 64 | 67 | #N/A | #N/A
2022-08-14 04:00 | 8 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 71 | 52 | 70 | 66 | 62 | 62 | 63 | 70 | #N/A | #N/A
2022-08-14 05:00 | 8 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 71 | 51 | 70 | 66 | 64 | 60 | 64 | 69 | #N/A | #N/A
2022-08-14 06:00 | 8 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 73 | 56 | 71 | 68 | 67 | 63 | 64 | 70 | #N/A | #N/A
2022-08-14 07:00 | 8 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 76 | 60 | 73 | 71 | 72 | 67 | 70 | 72 | #N/A | #N/A
2022-08-14 08:00 | 8 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 79 | 67 | 76 | 74 | 75 | 74 | 71 | 72 | #N/A | #N/A
2022-08-14 09:00 | 8 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 80 | 71 | 79 | 76 | 77 | 79 | 77 | 73 | #N/A | #N/A
2022-08-14 10:00 | 8 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 83 | 74 | 82 | 79 | 80 | 82 | 80 | 73 | #N/A | #N/A
2022-08-14 11:00 | 8 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 78 | 74 | 85 | 81 | 81 | 84 | 82 | 74 | #N/A | #N/A
2022-08-14 12:00 | 8 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 89 | 75 | 87 | 81 | 80 | 83 | 84 | 75 | #N/A | #N/A
2022-08-14 13:00 | 8 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 93 | 77 | 88 | 79 | 80 | 84 | 83 | 76 | #N/A | #N/A
2022-08-14 14:00 | 8 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 90 | 79 | 89 | 78 | 82 | 86 | 82 | 77 | #N/A | #N/A
2022-08-14 15:00 | 8 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 92 | 78 | 89 | 76 | 79 | 84 | 80 | 77 | #N/A | #N/A
2022-08-14 16:00 | 8 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 83 | 79 | 89 | 73 | 80 | 82 | 76 | 77 | #N/A | #N/A
2022-08-14 17:00 | 8 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 77 | 76 | 87 | 73 | 80 | 82 | 75 | 77 | #N/A | #N/A
2022-08-14 18:00 | 8 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 77 | 71 | 82 | 72 | 77 | 79 | 73 | 75 | #N/A | #N/A
2022-08-14 19:00 | 8 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 75 | 66 | 79 | 70 | 75 | 76 | 71 | 72 | #N/A | #N/A
2022-08-14 20:00 | 8 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 72 | 64 | 78 | 69 | 73 | 73 | 68 | 69 | #N/A | #N/A
2022-08-14 21:00 | 8 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 71 | 62 | 77 | 68 | 71 | 73 | 67 | 68 | #N/A | #N/A
2022-08-14 22:00 | 8 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 73 | 64 | 73 | 68 | 70 | 70 | 66 | 70 | #N/A | #N/A
2022-08-14 23:00 | 8 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 73 | 63 | 74 | 67 | 70 | 67 | 66 | 69 | #N/A | #N/A
2022-08-15 | 8 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 72 | 62 | 73 | 67 | 70 | 66 | 64 | 70 | #N/A | #N/A
2022-08-15 01:00 | 8 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 71 | 61 | 71 | 67 | 70 | 64 | 63 | 70 | #N/A | #N/A
2022-08-15 02:00 | 8 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 72 | 58 | 71 | 67 | 70 | 63 | 62 | 68 | #N/A | #N/A
2022-08-15 03:00 | 8 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 71 | 58 | 70 | 67 | 71 | 63 | 62 | 69 | #N/A | #N/A
2022-08-15 04:00 | 8 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 71 | 57 | 69 | 68 | 71 | 62 | 62 | 69 | #N/A | #N/A
2022-08-15 05:00 | 8 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 71 | 56 | 69 | 68 | 71 | 62 | 61 | 69 | #N/A | #N/A
2022-08-15 06:00 | 8 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 72 | 60 | 70 | 69 | 72 | 64 | 65 | 69 | #N/A | #N/A
2022-08-15 07:00 | 8 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 75 | 66 | 73 | 70 | 74 | 68 | 69 | 69 | #N/A | #N/A
2022-08-15 08:00 | 8 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 78 | 70 | 77 | 71 | 78 | 70 | 72 | 70 | #N/A | #N/A
2022-08-15 09:00 | 8 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 83 | 73 | 82 | 73 | 81 | 78 | 74 | 70 | #N/A | #N/A
2022-08-15 10:00 | 8 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 87 | 75 | 85 | 75 | 82 | 80 | 77 | 73 | #N/A | #N/A
2022-08-15 11:00 | 8 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 86 | 75 | 87 | 76 | 83 | 83 | 79 | 77 | #N/A | #N/A
2022-08-15 12:00 | 8 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 89 | 68 | 89 | 79 | 86 | 83 | 79 | 77 | #N/A | #N/A
2022-08-15 13:00 | 8 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 90 | 78 | 90 | 79 | 87 | 84 | 82 | 76 | #N/A | #N/A
2022-08-15 14:00 | 8 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 87 | 78 | 91 | 79 | 88 | 86 | 81 | 77 | #N/A | #N/A
2022-08-15 15:00 | 8 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 85 | 77 | 90 | 77 | 88 | 84 | 79 | 78 | #N/A | #N/A
2022-08-15 16:00 | 8 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 84 | 78 | 87 | 78 | 87 | 75 | 80 | 79 | #N/A | #N/A
2022-08-15 17:00 | 8 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 82 | 75 | 87 | 77 | 84 | 81 | 77 | 78 | #N/A | #N/A
2022-08-15 18:00 | 8 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 80 | 72 | 83 | 75 | 80 | 77 | 75 | 77 | #N/A | #N/A
2022-08-15 19:00 | 8 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 75 | 69 | 79 | 74 | 76 | 74 | 74 | 75 | #N/A | #N/A
2022-08-15 20:00 | 8 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 72 | 64 | 76 | 73 | 75 | 72 | 73 | 74 | #N/A | #N/A
2022-08-15 21:00 | 8 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 72 | 68 | 76 | 73 | 74 | 71 | 72 | 73 | #N/A | #N/A
2022-08-15 22:00 | 8 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 62 | 75 | 72 | 73 | 70 | 72 | 72 | #N/A | #N/A
2022-08-15 23:00 | 8 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 69 | 61 | 74 | 71 | 71 | 69 | 71 | 71 | #N/A | #N/A
2022-08-16 | 8 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 67 | 61 | 73 | 71 | 71 | 68 | 71 | 71 | #N/A | #N/A
2022-08-16 01:00 | 8 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 67 | 61 | 73 | 70 | 70 | 67 | 71 | 70 | #N/A | #N/A
2022-08-16 02:00 | 8 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 65 | 61 | 73 | 69 | 70 | 66 | 70 | 69 | #N/A | #N/A
2022-08-16 03:00 | 8 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 64 | 63 | 72 | 69 | 69 | 65 | 70 | 68 | #N/A | #N/A
2022-08-16 04:00 | 8 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 63 | 61 | 71 | 69 | 68 | 66 | 70 | 68 | #N/A | #N/A
2022-08-16 05:00 | 8 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 62 | 61 | 71 | 70 | 70 | 67 | 69 | 68 | #N/A | #N/A
2022-08-16 06:00 | 8 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 62 | 73 | 70 | 74 | 68 | 70 | 69 | #N/A | #N/A
2022-08-16 07:00 | 8 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 63 | 63 | 78 | 71 | 79 | 69 | 71 | 72 | #N/A | #N/A
2022-08-16 08:00 | 8 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 63 | 64 | 81 | 75 | 82 | 71 | 74 | 74 | #N/A | #N/A
2022-08-16 09:00 | 8 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 64 | 68 | 85 | 78 | 85 | 72 | 75 | 76 | #N/A | #N/A
2022-08-16 10:00 | 8 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 66 | 70 | 87 | 81 | 86 | 76 | 79 | 80 | #N/A | #N/A
2022-08-16 11:00 | 8 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 67 | 72 | 89 | 83 | 87 | 80 | 74 | 82 | #N/A | #N/A
2022-08-16 12:00 | 8 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 71 | 73 | 89 | 83 | 88 | 80 | 76 | 84 | #N/A | #N/A
2022-08-16 13:00 | 8 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 71 | 71 | 91 | 83 | 90 | 83 | 73 | 85 | #N/A | #N/A
2022-08-16 14:00 | 8 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 71 | 73 | 87 | 83 | 90 | 83 | 74 | 86 | #N/A | #N/A
2022-08-16 15:00 | 8 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 73 | 73 | 86 | 84 | 89 | 81 | 72 | 83 | #N/A | #N/A
2022-08-16 16:00 | 8 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 72 | 70 | 86 | 83 | 87 | 82 | 75 | 84 | #N/A | #N/A
2022-08-16 17:00 | 8 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 71 | 69 | 86 | 82 | 86 | 81 | 73 | 83 | #N/A | #N/A
2022-08-16 18:00 | 8 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 69 | 68 | 84 | 80 | 83 | 78 | 72 | 81 | #N/A | #N/A
2022-08-16 19:00 | 8 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 66 | 61 | 81 | 75 | 82 | 75 | 68 | 78 | #N/A | #N/A
2022-08-16 20:00 | 8 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 65 | 59 | 78 | 75 | 80 | 73 | 69 | 75 | #N/A | #N/A
2022-08-16 21:00 | 8 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 64 | 56 | 77 | 72 | 79 | 70 | 68 | 73 | #N/A | #N/A
2022-08-16 22:00 | 8 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 64 | 55 | 77 | 72 | 77 | 69 | 67 | 74 | #N/A | #N/A
2022-08-16 23:00 | 8 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 63 | 54 | 76 | 71 | 76 | 68 | 66 | 72 | #N/A | #N/A
2022-08-17 | 8 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 61 | 55 | 79 | 68 | 76 | 66 | 64 | 72 | #N/A | #N/A
2022-08-17 01:00 | 8 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 60 | 50 | 78 | 70 | 76 | 65 | 62 | 74 | #N/A | #N/A
2022-08-17 02:00 | 8 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 58 | 50 | 78 | 68 | 76 | 64 | 62 | 74 | #N/A | #N/A
2022-08-17 03:00 | 8 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 57 | 49 | 77 | 67 | 76 | 63 | 61 | 72 | #N/A | #N/A
2022-08-17 04:00 | 8 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 57 | 51 | 75 | 67 | 76 | 63 | 60 | 71 | #N/A | #N/A
2022-08-17 05:00 | 8 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 58 | 53 | 76 | 68 | 75 | 63 | 60 | 70 | #N/A | #N/A
2022-08-17 06:00 | 8 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 59 | 56 | 77 | 69 | 77 | 64 | 62 | 69 | #N/A | #N/A
2022-08-17 07:00 | 8 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 64 | 59 | 80 | 72 | 80 | 68 | 67 | 67 | #N/A | #N/A
2022-08-17 08:00 | 8 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 68 | 65 | 81 | 74 | 84 | 71 | 70 | 68 | #N/A | #N/A
2022-08-17 09:00 | 8 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 72 | 66 | 84 | 77 | 87 | 71 | 71 | 68 | #N/A | #N/A
2022-08-17 10:00 | 8 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 74 | 69 | 86 | 80 | 89 | 73 | 72 | 69 | #N/A | #N/A
2022-08-17 11:00 | 8 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 88 | 76 | 71 | 84 | 80 | 91 | 77 | 73 | 70 | #N/A | #N/A
2022-08-17 12:00 | 8 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 90 | 79 | 69 | 85 | 82 | 92 | 78 | 75 | 70 | #N/A | #N/A
2022-08-17 13:00 | 8 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 81 | 70 | 82 | 80 | 93 | 79 | 76 | 70 | #N/A | #N/A
2022-08-17 14:00 | 8 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 82 | 71 | 81 | 82 | 94 | 81 | 76 | 71 | #N/A | #N/A
2022-08-17 15:00 | 8 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 80 | 72 | 80 | 80 | 94 | 81 | 76 | 71 | #N/A | #N/A
2022-08-17 16:00 | 8 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 79 | 71 | 80 | 79 | 92 | 80 | 75 | 72 | #N/A | #N/A
2022-08-17 17:00 | 8 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 77 | 70 | 79 | 78 | 91 | 78 | 73 | 72 | #N/A | #N/A
2022-08-17 18:00 | 8 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 73 | 68 | 78 | 76 | 88 | 76 | 68 | 72 | #N/A | #N/A
2022-08-17 19:00 | 8 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 70 | 62 | 77 | 71 | 86 | 75 | 66 | 70 | #N/A | #N/A
2022-08-17 20:00 | 8 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 69 | 60 | 76 | 68 | 83 | 71 | 64 | 69 | #N/A | #N/A
2022-08-17 21:00 | 8 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 65 | 56 | 76 | 66 | 81 | 69 | 62 | 68 | #N/A | #N/A
2022-08-17 22:00 | 8 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 64 | 57 | 76 | 64 | 80 | 66 | 60 | 70 | #N/A | #N/A
2022-08-17 23:00 | 8 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 62 | 55 | 75 | 63 | 80 | 64 | 58 | 69 | #N/A | #N/A
2022-08-18 | 8 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 61 | 54 | 74 | 63 | 80 | 64 | 57 | 69 | #N/A | #N/A
2022-08-18 01:00 | 8 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 59 | 52 | 73 | 64 | 78 | 63 | 56 | 69 | #N/A | #N/A
2022-08-18 02:00 | 8 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 58 | 49 | 72 | 65 | 78 | 61 | 55 | 70 | #N/A | #N/A
2022-08-18 03:00 | 8 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 57 | 50 | 72 | 64 | 77 | 62 | 54 | 68 | #N/A | #N/A
2022-08-18 04:00 | 8 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 56 | 50 | 71 | 63 | 78 | 62 | 53 | 69 | #N/A | #N/A
2022-08-18 05:00 | 8 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 56 | 50 | 70 | 63 | 79 | 62 | 53 | 69 | #N/A | #N/A
2022-08-18 06:00 | 8 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 61 | 51 | 72 | 64 | 80 | 62 | 55 | 70 | #N/A | #N/A
2022-08-18 07:00 | 8 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 65 | 55 | 74 | 66 | 83 | 65 | 58 | 71 | #N/A | #N/A
2022-08-18 08:00 | 8 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 71 | 58 | 75 | 68 | 84 | 67 | 62 | 71 | #N/A | #N/A
2022-08-18 09:00 | 8 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 74 | 61 | 76 | 69 | 86 | 70 | 66 | 72 | #N/A | #N/A
2022-08-18 10:00 | 8 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 77 | 67 | 78 | 71 | 88 | 73 | 70 | 72 | #N/A | #N/A
2022-08-18 11:00 | 8 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 77 | 70 | 78 | 73 | 89 | 74 | 72 | 72 | #N/A | #N/A
2022-08-18 12:00 | 8 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 79 | 73 | 78 | 73 | 90 | 73 | 73 | 73 | #N/A | #N/A
2022-08-18 13:00 | 8 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 78 | 70 | 79 | 73 | 91 | 72 | 74 | 72 | #N/A | #N/A
2022-08-18 14:00 | 8 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 76 | 71 | 78 | 73 | 92 | 74 | 74 | 73 | #N/A | #N/A
2022-08-18 15:00 | 8 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 74 | 72 | 78 | 75 | 91 | 73 | 72 | 72 | #N/A | #N/A
2022-08-18 16:00 | 8 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 73 | 72 | 78 | 72 | 89 | 72 | 71 | 71 | #N/A | #N/A
2022-08-18 17:00 | 8 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 69 | 71 | 77 | 71 | 88 | 67 | 70 | 69 | #N/A | #N/A
2022-08-18 18:00 | 8 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 67 | 65 | 73 | 70 | 82 | 66 | 68 | 66 | #N/A | #N/A
2022-08-18 19:00 | 8 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 65 | 60 | 71 | 70 | 82 | 65 | 67 | 64 | #N/A | #N/A
2022-08-18 20:00 | 8 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 64 | 58 | 69 | 69 | 80 | 65 | 66 | 63 | #N/A | #N/A
2022-08-18 21:00 | 8 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 62 | 56 | 67 | 69 | 77 | 65 | 65 | 62 | #N/A | #N/A
2022-08-18 22:00 | 8 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 61 | 54 | 69 | 68 | 77 | 65 | 65 | 60 | #N/A | #N/A
2022-08-18 23:00 | 8 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 60 | 55 | 68 | 68 | 76 | 65 | 65 | 59 | #N/A | #N/A
2022-08-19 | 8 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 59 | 52 | 67 | 68 | 73 | 65 | 64 | 57 | #N/A | #N/A
2022-08-19 01:00 | 8 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 51 | 68 | 64 | 74 | 65 | 64 | 55 | #N/A | #N/A
2022-08-19 02:00 | 8 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 61 | 49 | 67 | 60 | 72 | 64 | 64 | 54 | #N/A | #N/A
2022-08-19 03:00 | 8 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 60 | 51 | 67 | 60 | 70 | 64 | 64 | 54 | #N/A | #N/A
2022-08-19 04:00 | 8 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 61 | 51 | 66 | 60 | 72 | 64 | 61 | 50 | #N/A | #N/A
2022-08-19 05:00 | 8 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 61 | 53 | 66 | 61 | 73 | 64 | 62 | 49 | #N/A | #N/A
2022-08-19 06:00 | 8 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 63 | 57 | 69 | 61 | 73 | 64 | 62 | 54 | #N/A | #N/A
2022-08-19 07:00 | 8 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 65 | 62 | 69 | 62 | 75 | 62 | 61 | 57 | #N/A | #N/A
2022-08-19 08:00 | 8 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 67 | 66 | 72 | 62 | 78 | 63 | 63 | 61 | #N/A | #N/A
2022-08-19 09:00 | 8 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 69 | 69 | 73 | 61 | 83 | 66 | 66 | 62 | #N/A | #N/A
2022-08-19 10:00 | 8 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 72 | 67 | 75 | 62 | 87 | 69 | 71 | 65 | #N/A | #N/A
2022-08-19 11:00 | 8 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 76 | 67 | 76 | 64 | 88 | 71 | 69 | 67 | #N/A | #N/A
2022-08-19 12:00 | 8 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 74 | 65 | 77 | 64 | 85 | 73 | 69 | 69 | #N/A | #N/A
2022-08-19 13:00 | 8 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 79 | 66 | 78 | 64 | 84 | 73 | 68 | 72 | #N/A | #N/A
2022-08-19 14:00 | 8 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 79 | 67 | 78 | 65 | 85 | 75 | 68 | 73 | #N/A | #N/A
2022-08-19 15:00 | 8 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 79 | 66 | 76 | 66 | 85 | 78 | 67 | 73 | #N/A | #N/A
2022-08-19 16:00 | 8 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 85 | 78 | 66 | 77 | 67 | 85 | 78 | 64 | 72 | #N/A | #N/A
2022-08-19 17:00 | 8 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 76 | 64 | 75 | 67 | 83 | 74 | 64 | 70 | #N/A | #N/A
2022-08-19 18:00 | 8 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 74 | 63 | 73 | 67 | 81 | 73 | 64 | 66 | #N/A | #N/A
2022-08-19 19:00 | 8 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 70 | 63 | 73 | 66 | 80 | 65 | 63 | 58 | #N/A | #N/A
2022-08-19 20:00 | 8 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 69 | 62 | 68 | 64 | 78 | 62 | 64 | 58 | #N/A | #N/A
2022-08-19 21:00 | 8 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 68 | 61 | 67 | 64 | 76 | 62 | 64 | 55 | #N/A | #N/A
2022-08-19 22:00 | 8 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 65 | 61 | 72 | 63 | 74 | 62 | 64 | 52 | #N/A | #N/A
2022-08-19 23:00 | 8 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 61 | 72 | 64 | 74 | 61 | 64 | 53 | #N/A | #N/A
2022-08-20 | 8 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 61 | 71 | 65 | 73 | 61 | 65 | 51 | #N/A | #N/A
2022-08-20 01:00 | 8 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 62 | 60 | 71 | 66 | 72 | 61 | 64 | 50 | #N/A | #N/A
2022-08-20 02:00 | 8 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 61 | 60 | 70 | 66 | 71 | 61 | 64 | 49 | #N/A | #N/A
2022-08-20 03:00 | 8 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 61 | 60 | 69 | 66 | 70 | 60 | 64 | 48 | #N/A | #N/A
2022-08-20 04:00 | 8 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 60 | 60 | 68 | 66 | 69 | 60 | 64 | 47 | #N/A | #N/A
2022-08-20 05:00 | 8 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 60 | 60 | 67 | 66 | 69 | 62 | 64 | 48 | #N/A | #N/A
2022-08-20 06:00 | 8 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 61 | 69 | 67 | 72 | 62 | 65 | 49 | #N/A | #N/A
2022-08-20 07:00 | 8 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 63 | 60 | 70 | 68 | 76 | 65 | 65 | 50 | #N/A | #N/A
2022-08-20 08:00 | 8 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 67 | 62 | 72 | 69 | 79 | 67 | 68 | 54 | #N/A | #N/A
2022-08-20 09:00 | 8 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 73 | 65 | 72 | 74 | 82 | 71 | 68 | 59 | #N/A | #N/A
2022-08-20 10:00 | 8 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 73 | 67 | 73 | 78 | 83 | 77 | 71 | 65 | #N/A | #N/A
2022-08-20 11:00 | 8 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 69 | 68 | 74 | 80 | 85 | 76 | 72 | 69 | #N/A | #N/A
2022-08-20 12:00 | 8 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 71 | 68 | 74 | 82 | 87 | 70 | 74 | 72 | #N/A | #N/A
2022-08-20 13:00 | 8 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 73 | 66 | 74 | 83 | 83 | 73 | 74 | 74 | #N/A | #N/A
2022-08-20 14:00 | 8 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 74 | 64 | 74 | 84 | 83 | 77 | 74 | 74 | #N/A | #N/A
2022-08-20 15:00 | 8 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 73 | 63 | 74 | 82 | 83 | 80 | 75 | 75 | #N/A | #N/A
2022-08-20 16:00 | 8 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 71 | 65 | 75 | 81 | 84 | 78 | 74 | 75 | #N/A | #N/A
2022-08-20 17:00 | 8 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 69 | 64 | 74 | 80 | 82 | 76 | 72 | 73 | #N/A | #N/A
2022-08-20 18:00 | 8 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 67 | 65 | 71 | 79 | 76 | 76 | 72 | 70 | #N/A | #N/A
2022-08-20 19:00 | 8 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 64 | 66 | 67 | 78 | 74 | 75 | 71 | 65 | #N/A | #N/A
2022-08-20 20:00 | 8 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 61 | 67 | 64 | 77 | 72 | 75 | 71 | 61 | #N/A | #N/A
2022-08-20 21:00 | 8 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 60 | 67 | 63 | 77 | 71 | 74 | 70 | 60 | #N/A | #N/A
2022-08-20 22:00 | 8 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 59 | 67 | 62 | 75 | 70 | 73 | 68 | 58 | #N/A | #N/A
2022-08-20 23:00 | 8 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 58 | 67 | 61 | 73 | 68 | 73 | 68 | 56 | #N/A | #N/A
2022-08-21 | 8 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 59 | 67 | 61 | 73 | 67 | 72 | 69 | 55 | #N/A | #N/A
2022-08-21 01:00 | 8 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 58 | 67 | 61 | 75 | 66 | 72 | 67 | 54 | #N/A | #N/A
2022-08-21 02:00 | 8 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 58 | 67 | 59 | 75 | 66 | 72 | 67 | 54 | #N/A | #N/A
2022-08-21 03:00 | 8 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 57 | 67 | 59 | 72 | 63 | 72 | 69 | 54 | #N/A | #N/A
2022-08-21 04:00 | 8 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 57 | 66 | 60 | 72 | 62 | 72 | 68 | 55 | #N/A | #N/A
2022-08-21 05:00 | 8 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 56 | 66 | 61 | 71 | 63 | 72 | 69 | 56 | #N/A | #N/A
2022-08-21 06:00 | 8 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 59 | 67 | 64 | 73 | 68 | 73 | 70 | 57 | #N/A | #N/A
2022-08-21 07:00 | 8 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 63 | 67 | 67 | 75 | 74 | 74 | 72 | 60 | #N/A | #N/A
2022-08-21 08:00 | 8 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 65 | 68 | 69 | 77 | 78 | 76 | 73 | 67 | #N/A | #N/A
2022-08-21 09:00 | 8 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 65 | 71 | 71 | 78 | 79 | 78 | 76 | 70 | #N/A | #N/A
2022-08-21 10:00 | 8 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 66 | 70 | 79 | 81 | 82 | 80 | 78 | 76 | #N/A | #N/A
2022-08-21 11:00 | 8 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 65 | 70 | 83 | 82 | 85 | 82 | 80 | 79 | #N/A | #N/A
2022-08-21 12:00 | 8 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 64 | 76 | 82 | 84 | 85 | 84 | 80 | 82 | #N/A | #N/A
2022-08-21 13:00 | 8 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 81 | 65 | 76 | 82 | 85 | 85 | 85 | 81 | 83 | #N/A | #N/A
2022-08-21 14:00 | 8 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 82 | 65 | 77 | 83 | 85 | 86 | 85 | 80 | 84 | #N/A | #N/A
2022-08-21 15:00 | 8 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 64 | 78 | 81 | 85 | 85 | 85 | 81 | 85 | #N/A | #N/A
2022-08-21 16:00 | 8 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 83 | 63 | 74 | 80 | 83 | 84 | 82 | 80 | 81 | #N/A | #N/A
2022-08-21 17:00 | 8 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 63 | 73 | 79 | 81 | 82 | 81 | 78 | 76 | #N/A | #N/A
2022-08-21 18:00 | 8 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 61 | 68 | 75 | 79 | 78 | 78 | 75 | 72 | #N/A | #N/A
2022-08-21 19:00 | 8 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 60 | 65 | 73 | 77 | 76 | 75 | 74 | 71 | #N/A | #N/A
2022-08-21 20:00 | 8 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 60 | 62 | 71 | 76 | 75 | 74 | 71 | 68 | #N/A | #N/A
2022-08-21 21:00 | 8 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 60 | 60 | 72 | 75 | 71 | 70 | 71 | 69 | #N/A | #N/A
2022-08-21 22:00 | 8 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 59 | 59 | 69 | 72 | 72 | 68 | 70 | 69 | #N/A | #N/A
2022-08-21 23:00 | 8 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 57 | 58 | 69 | 70 | 71 | 67 | 70 | 68 | #N/A | #N/A
2022-08-22 | 8 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 57 | 56 | 70 | 70 | 70 | 69 | 67 | 66 | #N/A | #N/A
2022-08-22 01:00 | 8 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 56 | 54 | 68 | 70 | 71 | 69 | 65 | 65 | #N/A | #N/A
2022-08-22 02:00 | 8 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 56 | 54 | 69 | 68 | 72 | 68 | 66 | 64 | #N/A | #N/A
2022-08-22 03:00 | 8 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 55 | 54 | 69 | 66 | 72 | 67 | 62 | 64 | #N/A | #N/A
2022-08-22 04:00 | 8 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 56 | 50 | 68 | 64 | 72 | 67 | 61 | 64 | #N/A | #N/A
2022-08-22 05:00 | 8 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 55 | 49 | 68 | 63 | 74 | 68 | 60 | 64 | #N/A | #N/A
2022-08-22 06:00 | 8 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 57 | 57 | 69 | 69 | 75 | 69 | 64 | 65 | #N/A | #N/A
2022-08-22 07:00 | 8 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 60 | 61 | 72 | 72 | 74 | 72 | 67 | 68 | #N/A | #N/A
2022-08-22 08:00 | 8 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 64 | 67 | 76 | 77 | 74 | 74 | 70 | 69 | #N/A | #N/A
2022-08-22 09:00 | 8 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 63 | 72 | 74 | 79 | 73 | 77 | 72 | 74 | #N/A | #N/A
2022-08-22 10:00 | 8 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 65 | 75 | 73 | 81 | 73 | 79 | 74 | 77 | #N/A | #N/A
2022-08-22 11:00 | 8 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 64 | 78 | 74 | 82 | 74 | 80 | 76 | 80 | #N/A | #N/A
2022-08-22 12:00 | 8 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 63 | 76 | 73 | 84 | 79 | 82 | 78 | 82 | #N/A | #N/A
2022-08-22 13:00 | 8 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 62 | 74 | 73 | 85 | 81 | 80 | 79 | 83 | #N/A | #N/A
2022-08-22 14:00 | 8 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 63 | 73 | 75 | 85 | 80 | 80 | 80 | 85 | #N/A | #N/A
2022-08-22 15:00 | 8 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 67 | 71 | 75 | 87 | 79 | 77 | 79 | 83 | #N/A | #N/A
2022-08-22 16:00 | 8 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 64 | 67 | 75 | 85 | 80 | 78 | 78 | 83 | #N/A | #N/A
2022-08-22 17:00 | 8 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 64 | 67 | 73 | 82 | 78 | 76 | 77 | 82 | #N/A | #N/A
2022-08-22 18:00 | 8 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 61 | 67 | 69 | 81 | 78 | 75 | 75 | 75 | #N/A | #N/A
2022-08-22 19:00 | 8 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 59 | 68 | 66 | 80 | 78 | 73 | 74 | 74 | #N/A | #N/A
2022-08-22 20:00 | 8 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 58 | 68 | 65 | 78 | 78 | 71 | 72 | 70 | #N/A | #N/A
2022-08-22 21:00 | 8 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 58 | 68 | 65 | 77 | 77 | 71 | 73 | 69 | #N/A | #N/A
2022-08-22 22:00 | 8 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 56 | 68 | 64 | 75 | 77 | 71 | 71 | 68 | #N/A | #N/A
2022-08-22 23:00 | 8 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 55 | 69 | 63 | 74 | 77 | 71 | 70 | 68 | #N/A | #N/A
2022-08-23 | 8 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 53 | 68 | 64 | 73 | 75 | 71 | 70 | 69 | #N/A | #N/A
2022-08-23 01:00 | 8 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 53 | 69 | 63 | 73 | 75 | 72 | 70 | 69 | #N/A | #N/A
2022-08-23 02:00 | 8 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 52 | 68 | 63 | 71 | 74 | 72 | 70 | 69 | #N/A | #N/A
2022-08-23 03:00 | 8 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 51 | 69 | 63 | 71 | 72 | 71 | 70 | 68 | #N/A | #N/A
2022-08-23 04:00 | 8 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 49 | 67 | 64 | 71 | 68 | 71 | 70 | 69 | #N/A | #N/A
2022-08-23 05:00 | 8 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 49 | 67 | 64 | 72 | 67 | 70 | 69 | 70 | #N/A | #N/A
2022-08-23 06:00 | 8 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 52 | 68 | 64 | 73 | 67 | 71 | 71 | 69 | #N/A | #N/A
2022-08-23 07:00 | 8 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 58 | 68 | 64 | 74 | 69 | 73 | 73 | 70 | #N/A | #N/A
2022-08-23 08:00 | 8 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 62 | 71 | 66 | 77 | 71 | 75 | 75 | 71 | #N/A | #N/A
2022-08-23 09:00 | 8 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 66 | 71 | 65 | 82 | 72 | 75 | 77 | 73 | #N/A | #N/A
2022-08-23 10:00 | 8 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 68 | 75 | 67 | 83 | 73 | 77 | 80 | 77 | #N/A | #N/A
2022-08-23 11:00 | 8 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 69 | 77 | 68 | 87 | 75 | 80 | 82 | 82 | #N/A | #N/A
2022-08-23 12:00 | 8 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 72 | 76 | 68 | 87 | 76 | 84 | 81 | 84 | #N/A | #N/A
2022-08-23 13:00 | 8 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 73 | 75 | 69 | 88 | 75 | 83 | 83 | 84 | #N/A | #N/A
2022-08-23 14:00 | 8 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 73 | 70 | 67 | 89 | 74 | 84 | 72 | 84 | #N/A | #N/A
2022-08-23 15:00 | 8 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 73 | 71 | 68 | 88 | 74 | 84 | 73 | 86 | #N/A | #N/A
2022-08-23 16:00 | 8 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 71 | 70 | 66 | 86 | 76 | 82 | 76 | 85 | #N/A | #N/A
2022-08-23 17:00 | 8 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 70 | 68 | 65 | 84 | 73 | 79 | 74 | 83 | #N/A | #N/A
2022-08-23 18:00 | 8 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 65 | 68 | 65 | 82 | 69 | 76 | 71 | 81 | #N/A | #N/A
2022-08-23 19:00 | 8 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 63 | 65 | 65 | 79 | 67 | 75 | 70 | 79 | #N/A | #N/A
2022-08-23 20:00 | 8 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 62 | 63 | 64 | 78 | 63 | 72 | 68 | 78 | #N/A | #N/A
2022-08-23 21:00 | 8 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 61 | 61 | 63 | 77 | 61 | 71 | 66 | 74 | #N/A | #N/A
2022-08-23 22:00 | 8 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 58 | 61 | 63 | 74 | 61 | 71 | 64 | 72 | #N/A | #N/A
2022-08-23 23:00 | 8 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 58 | 58 | 63 | 74 | 61 | 69 | 63 | 71 | #N/A | #N/A
2022-08-24 | 8 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 58 | 56 | 62 | 73 | 60 | 68 | 62 | 69 | #N/A | #N/A
2022-08-24 01:00 | 8 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 56 | 56 | 61 | 71 | 61 | 67 | 60 | 70 | #N/A | #N/A
2022-08-24 02:00 | 8 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 56 | 54 | 60 | 69 | 60 | 67 | 59 | 68 | #N/A | #N/A
2022-08-24 03:00 | 8 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 56 | 53 | 60 | 68 | 59 | 65 | 59 | 67 | #N/A | #N/A
2022-08-24 04:00 | 8 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 56 | 52 | 60 | 67 | 57 | 66 | 56 | 66 | #N/A | #N/A
2022-08-24 05:00 | 8 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 56 | 53 | 60 | 66 | 58 | 65 | 58 | 66 | #N/A | #N/A
2022-08-24 06:00 | 8 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 57 | 54 | 60 | 69 | 61 | 66 | 59 | 68 | #N/A | #N/A
2022-08-24 07:00 | 8 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 60 | 61 | 61 | 70 | 65 | 67 | 62 | 73 | #N/A | #N/A
2022-08-24 08:00 | 8 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 62 | 65 | 62 | 73 | 67 | 69 | 66 | 78 | #N/A | #N/A
2022-08-24 09:00 | 8 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 66 | 66 | 65 | 74 | 69 | 72 | 68 | 83 | #N/A | #N/A
2022-08-24 10:00 | 8 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 69 | 70 | 66 | 76 | 71 | 75 | 71 | 82 | #N/A | #N/A
2022-08-24 11:00 | 8 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 74 | 70 | 66 | 77 | 72 | 78 | 73 | 77 | #N/A | #N/A
2022-08-24 12:00 | 8 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 74 | 72 | 66 | 78 | 74 | 77 | 73 | 73 | #N/A | #N/A
2022-08-24 13:00 | 8 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 73 | 73 | 65 | 80 | 73 | 78 | 74 | 78 | #N/A | #N/A
2022-08-24 14:00 | 8 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 73 | 74 | 66 | 81 | 74 | 78 | 75 | 82 | #N/A | #N/A
2022-08-24 15:00 | 8 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 72 | 73 | 65 | 79 | 74 | 80 | 73 | 84 | #N/A | #N/A
2022-08-24 16:00 | 8 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 71 | 74 | 65 | 80 | 72 | 81 | 74 | 85 | #N/A | #N/A
2022-08-24 17:00 | 8 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 69 | 71 | 64 | 77 | 71 | 79 | 72 | 83 | #N/A | #N/A
2022-08-24 18:00 | 8 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 68 | 65 | 62 | 74 | 67 | 76 | 67 | 80 | #N/A | #N/A
2022-08-24 19:00 | 8 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 66 | 61 | 58 | 69 | 65 | 73 | 64 | 77 | #N/A | #N/A
2022-08-24 20:00 | 8 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 63 | 58 | 57 | 66 | 63 | 73 | 62 | 75 | #N/A | #N/A
2022-08-24 21:00 | 8 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 62 | 56 | 56 | 65 | 62 | 69 | 59 | 74 | #N/A | #N/A
2022-08-24 22:00 | 8 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 60 | 54 | 54 | 66 | 59 | 68 | 58 | 74 | #N/A | #N/A
2022-08-24 23:00 | 8 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 60 | 53 | 53 | 66 | 59 | 66 | 55 | 72 | #N/A | #N/A
2022-08-25 | 8 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 59 | 50 | 51 | 64 | 58 | 63 | 54 | 73 | #N/A | #N/A
2022-08-25 01:00 | 8 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 59 | 50 | 51 | 62 | 56 | 62 | 53 | 70 | #N/A | #N/A
2022-08-25 02:00 | 8 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 58 | 47 | 50 | 60 | 58 | 62 | 51 | 69 | #N/A | #N/A
2022-08-25 03:00 | 8 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 58 | 47 | 50 | 59 | 57 | 61 | 50 | 66 | #N/A | #N/A
2022-08-25 04:00 | 8 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 58 | 47 | 51 | 58 | 57 | 60 | 49 | 65 | #N/A | #N/A
2022-08-25 05:00 | 8 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 58 | 46 | 51 | 58 | 57 | 59 | 49 | 65 | #N/A | #N/A
2022-08-25 06:00 | 8 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 59 | 48 | 53 | 59 | 58 | 61 | 51 | 67 | #N/A | #N/A
2022-08-25 07:00 | 8 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 60 | 52 | 56 | 64 | 62 | 64 | 55 | 71 | #N/A | #N/A
2022-08-25 08:00 | 8 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 61 | 58 | 59 | 65 | 69 | 69 | 59 | 74 | #N/A | #N/A
2022-08-25 09:00 | 8 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 63 | 61 | 63 | 67 | 73 | 73 | 62 | 77 | #N/A | #N/A
2022-08-25 10:00 | 8 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 66 | 65 | 66 | 70 | 74 | 76 | 64 | 77 | #N/A | #N/A
2022-08-25 11:00 | 8 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 69 | 68 | 67 | 72 | 76 | 78 | 66 | 76 | #N/A | #N/A
2022-08-25 12:00 | 8 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 69 | 69 | 70 | 74 | 74 | 81 | 69 | 75 | #N/A | #N/A
2022-08-25 13:00 | 8 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 68 | 72 | 70 | 76 | 75 | 83 | 70 | 75 | #N/A | #N/A
2022-08-25 14:00 | 8 | 4 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 68 | 72 | 69 | 76 | 74 | 84 | 71 | 77 | #N/A | #N/A
2022-08-25 15:00 | 8 | 4 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 69 | 72 | 69 | 78 | 73 | 83 | 71 | 77 | #N/A | #N/A
2022-08-25 16:00 | 8 | 4 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 68 | 72 | 67 | 76 | 73 | 82 | 71 | 77 | #N/A | #N/A
2022-08-25 17:00 | 8 | 4 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 67 | 72 | 66 | 75 | 70 | 80 | 69 | 77 | #N/A | #N/A
2022-08-25 18:00 | 8 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 66 | 63 | 65 | 67 | 68 | 77 | 67 | 74 | #N/A | #N/A
2022-08-25 19:00 | 8 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 66 | 55 | 61 | 63 | 67 | 73 | 61 | 70 | #N/A | #N/A
2022-08-25 20:00 | 8 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 66 | 53 | 60 | 61 | 63 | 72 | 58 | 70 | #N/A | #N/A
2022-08-25 21:00 | 8 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 65 | 51 | 59 | 59 | 64 | 69 | 55 | 70 | #N/A | #N/A
2022-08-25 22:00 | 8 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 65 | 49 | 59 | 58 | 63 | 68 | 53 | 68 | #N/A | #N/A
2022-08-25 23:00 | 8 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 65 | 47 | 58 | 57 | 61 | 67 | 52 | 68 | #N/A | #N/A
2022-08-26 | 8 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 64 | 47 | 56 | 57 | 62 | 63 | 50 | 68 | #N/A | #N/A
2022-08-26 01:00 | 8 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 64 | 46 | 56 | 57 | 60 | 63 | 50 | 68 | #N/A | #N/A
2022-08-26 02:00 | 8 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 64 | 46 | 56 | 56 | 60 | 61 | 49 | 68 | #N/A | #N/A
2022-08-26 03:00 | 8 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 64 | 46 | 56 | 56 | 60 | 59 | 48 | 68 | #N/A | #N/A
2022-08-26 04:00 | 8 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 65 | 45 | 57 | 57 | 61 | 58 | 47 | 68 | #N/A | #N/A
2022-08-26 05:00 | 8 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 65 | 44 | 58 | 56 | 62 | 57 | 48 | 68 | #N/A | #N/A
2022-08-26 06:00 | 8 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 65 | 48 | 60 | 60 | 63 | 60 | 50 | 68 | #N/A | #N/A
2022-08-26 07:00 | 8 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 67 | 56 | 63 | 65 | 65 | 65 | 56 | 71 | #N/A | #N/A
2022-08-26 08:00 | 8 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 69 | 63 | 64 | 68 | 71 | 71 | 60 | 73 | #N/A | #N/A
2022-08-26 09:00 | 8 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 71 | 69 | 64 | 71 | 74 | 76 | 65 | 75 | #N/A | #N/A
2022-08-26 10:00 | 8 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 74 | 71 | 63 | 75 | 76 | 79 | 69 | 79 | #N/A | #N/A
2022-08-26 11:00 | 8 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 75 | 73 | 63 | 77 | 78 | 81 | 70 | 81 | #N/A | #N/A
2022-08-26 12:00 | 8 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 78 | 76 | 61 | 77 | 79 | 83 | 73 | 85 | #N/A | #N/A
2022-08-26 13:00 | 8 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 76 | 78 | 61 | 79 | 79 | 84 | 74 | 86 | #N/A | #N/A
2022-08-26 14:00 | 8 | 5 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 77 | 78 | 60 | 78 | 79 | 84 | 74 | 86 | #N/A | #N/A
2022-08-26 15:00 | 8 | 5 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 78 | 78 | 59 | 79 | 77 | 83 | 74 | 85 | #N/A | #N/A
2022-08-26 16:00 | 8 | 5 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 75 | 77 | 59 | 79 | 76 | 83 | 74 | 83 | #N/A | #N/A
2022-08-26 17:00 | 8 | 5 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 74 | 75 | 59 | 79 | 74 | 80 | 72 | 81 | #N/A | #N/A
2022-08-26 18:00 | 8 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 72 | 70 | 59 | 74 | 72 | 77 | 69 | 79 | #N/A | #N/A
2022-08-26 19:00 | 8 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 71 | 59 | 59 | 71 | 71 | 74 | 64 | 76 | #N/A | #N/A
2022-08-26 20:00 | 8 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 69 | 55 | 60 | 68 | 70 | 71 | 61 | 75 | #N/A | #N/A
2022-08-26 21:00 | 8 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 69 | 54 | 60 | 66 | 70 | 73 | 59 | 70 | #N/A | #N/A
2022-08-26 22:00 | 8 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 66 | 53 | 60 | 64 | 70 | 69 | 57 | 71 | #N/A | #N/A
2022-08-26 23:00 | 8 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 65 | 52 | 60 | 65 | 66 | 68 | 56 | 68 | #N/A | #N/A
2022-08-27 | 8 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 64 | 53 | 61 | 63 | 67 | 67 | 54 | 66 | #N/A | #N/A
2022-08-27 01:00 | 8 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 63 | 54 | 63 | 63 | 66 | 67 | 53 | 64 | #N/A | #N/A
2022-08-27 02:00 | 8 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 63 | 54 | 64 | 64 | 67 | 60 | 53 | 64 | #N/A | #N/A
2022-08-27 03:00 | 8 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 62 | 54 | 65 | 62 | 66 | 58 | 51 | 64 | #N/A | #N/A
2022-08-27 04:00 | 8 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 62 | 52 | 65 | 62 | 65 | 59 | 50 | 63 | #N/A | #N/A
2022-08-27 05:00 | 8 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 62 | 53 | 65 | 61 | 65 | 59 | 50 | 62 | #N/A | #N/A
2022-08-27 06:00 | 8 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 62 | 55 | 64 | 62 | 64 | 62 | 55 | 65 | #N/A | #N/A
2022-08-27 07:00 | 8 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 64 | 59 | 63 | 65 | 65 | 63 | 60 | 68 | #N/A | #N/A
2022-08-27 08:00 | 8 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 66 | 64 | 63 | 68 | 65 | 67 | 63 | 75 | #N/A | #N/A
2022-08-27 09:00 | 8 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 67 | 65 | 63 | 70 | 66 | 74 | 68 | 78 | #N/A | #N/A
2022-08-27 10:00 | 8 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 70 | 66 | 64 | 72 | 67 | 79 | 69 | 81 | #N/A | #N/A
2022-08-27 11:00 | 8 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 71 | 70 | 64 | 75 | 69 | 82 | 72 | 83 | #N/A | #N/A
2022-08-27 12:00 | 8 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 72 | 75 | 64 | 75 | 71 | 84 | 74 | 84 | #N/A | #N/A
2022-08-27 13:00 | 8 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 74 | 76 | 64 | 75 | 74 | 84 | 74 | 85 | #N/A | #N/A
2022-08-27 14:00 | 8 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 73 | 75 | 64 | 76 | 73 | 84 | 74 | 86 | #N/A | #N/A
2022-08-27 15:00 | 8 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 74 | 74 | 65 | 77 | 75 | 83 | 75 | 86 | #N/A | #N/A
2022-08-27 16:00 | 8 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 72 | 73 | 63 | 76 | 72 | 81 | 75 | 85 | #N/A | #N/A
2022-08-27 17:00 | 8 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 69 | 72 | 63 | 75 | 70 | 79 | 73 | 83 | #N/A | #N/A
2022-08-27 18:00 | 8 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 68 | 69 | 62 | 73 | 69 | 78 | 70 | 73 | #N/A | #N/A
2022-08-27 19:00 | 8 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 66 | 64 | 62 | 71 | 68 | 77 | 69 | 71 | #N/A | #N/A
2022-08-27 20:00 | 8 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 64 | 66 | 63 | 68 | 66 | 77 | 68 | 68 | #N/A | #N/A
2022-08-27 21:00 | 8 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 63 | 64 | 62 | 67 | 65 | 77 | 68 | 65 | #N/A | #N/A
2022-08-27 22:00 | 8 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 61 | 63 | 62 | 67 | 65 | 75 | 67 | 66 | #N/A | #N/A
2022-08-27 23:00 | 8 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 60 | 63 | 62 | 68 | 64 | 73 | 67 | 63 | #N/A | #N/A
2022-08-28 | 8 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 57 | 62 | 61 | 67 | 64 | 70 | 67 | 63 | #N/A | #N/A
2022-08-28 01:00 | 8 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 58 | 60 | 61 | 66 | 64 | 66 | 66 | 62 | #N/A | #N/A
2022-08-28 02:00 | 8 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 57 | 58 | 61 | 67 | 64 | 65 | 64 | 62 | #N/A | #N/A
2022-08-28 03:00 | 8 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 57 | 56 | 61 | 66 | 64 | 63 | 65 | 60 | #N/A | #N/A
2022-08-28 04:00 | 8 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 55 | 55 | 61 | 67 | 65 | 61 | 64 | 60 | #N/A | #N/A
2022-08-28 05:00 | 8 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 55 | 51 | 60 | 68 | 65 | 61 | 65 | 60 | #N/A | #N/A
2022-08-28 06:00 | 8 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 57 | 54 | 60 | 69 | 67 | 64 | 66 | 63 | #N/A | #N/A
2022-08-28 07:00 | 8 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 60 | 66 | 61 | 70 | 68 | 72 | 68 | 66 | #N/A | #N/A
2022-08-28 08:00 | 8 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 64 | 73 | 61 | 71 | 69 | 77 | 70 | 72 | #N/A | #N/A
2022-08-28 09:00 | 8 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 67 | 75 | 64 | 73 | 71 | 80 | 73 | 75 | #N/A | #N/A
2022-08-28 10:00 | 8 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 70 | 77 | 65 | 76 | 71 | 81 | 77 | 81 | #N/A | #N/A
2022-08-28 11:00 | 8 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 73 | 77 | 66 | 81 | 72 | 83 | 80 | 83 | #N/A | #N/A
2022-08-28 12:00 | 8 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 73 | 79 | 66 | 80 | 72 | 84 | 80 | 85 | #N/A | #N/A
2022-08-28 13:00 | 8 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 75 | 80 | 65 | 81 | 73 | 87 | 80 | 86 | #N/A | #N/A
2022-08-28 14:00 | 8 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 75 | 77 | 65 | 84 | 73 | 87 | 80 | 87 | #N/A | #N/A
2022-08-28 15:00 | 8 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 75 | 79 | 63 | 81 | 73 | 85 | 80 | 87 | #N/A | #N/A
2022-08-28 16:00 | 8 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 73 | 79 | 62 | 82 | 73 | 83 | 78 | 85 | #N/A | #N/A
2022-08-28 17:00 | 8 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 72 | 75 | 62 | 80 | 72 | 82 | 77 | 83 | #N/A | #N/A
2022-08-28 18:00 | 8 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 69 | 70 | 62 | 78 | 70 | 79 | 74 | 80 | #N/A | #N/A
2022-08-28 19:00 | 8 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 68 | 68 | 62 | 76 | 69 | 75 | 72 | 77 | #N/A | #N/A
2022-08-28 20:00 | 8 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 64 | 67 | 62 | 74 | 68 | 74 | 70 | 72 | #N/A | #N/A
2022-08-28 21:00 | 8 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 64 | 64 | 62 | 74 | 67 | 73 | 69 | 69 | #N/A | #N/A
2022-08-28 22:00 | 8 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 62 | 65 | 61 | 72 | 67 | 71 | 69 | 68 | #N/A | #N/A
2022-08-28 23:00 | 8 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 62 | 64 | 61 | 73 | 67 | 71 | 69 | 67 | #N/A | #N/A
2022-08-29 | 8 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 62 | 65 | 60 | 72 | 67 | 70 | 68 | 67 | #N/A | #N/A
2022-08-29 01:00 | 8 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 61 | 64 | 59 | 71 | 66 | 70 | 68 | 65 | #N/A | #N/A
2022-08-29 02:00 | 8 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 60 | 63 | 59 | 71 | 68 | 70 | 68 | 65 | #N/A | #N/A
2022-08-29 03:00 | 8 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 59 | 62 | 60 | 71 | 67 | 70 | 69 | 64 | #N/A | #N/A
2022-08-29 04:00 | 8 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 58 | 62 | 60 | 72 | 67 | 70 | 68 | 63 | #N/A | #N/A
2022-08-29 05:00 | 8 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 58 | 62 | 59 | 72 | 66 | 72 | 68 | 63 | #N/A | #N/A
2022-08-29 06:00 | 8 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 59 | 66 | 60 | 73 | 68 | 71 | 68 | 65 | #N/A | #N/A
2022-08-29 07:00 | 8 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 62 | 64 | 62 | 73 | 71 | 72 | 69 | 66 | #N/A | #N/A
2022-08-29 08:00 | 8 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 66 | 64 | 63 | 74 | 74 | 72 | 69 | 69 | #N/A | #N/A
2022-08-29 09:00 | 8 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 67 | 65 | 64 | 74 | 76 | 76 | 72 | 71 | #N/A | #N/A
2022-08-29 10:00 | 8 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 65 | 66 | 66 | 76 | 76 | 80 | 72 | 72 | #N/A | #N/A
2022-08-29 11:00 | 8 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 65 | 69 | 68 | 78 | 77 | 81 | 73 | 75 | #N/A | #N/A
2022-08-29 12:00 | 8 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 66 | 68 | 68 | 80 | 77 | 84 | 74 | 75 | #N/A | #N/A
2022-08-29 13:00 | 8 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 66 | 70 | 68 | 82 | 79 | 85 | 73 | 78 | #N/A | #N/A
2022-08-29 14:00 | 8 | 1 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 66 | 73 | 68 | 82 | 77 | 85 | 72 | 81 | #N/A | #N/A
2022-08-29 15:00 | 8 | 1 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 66 | 73 | 68 | 82 | 76 | 84 | 71 | 81 | #N/A | #N/A
2022-08-29 16:00 | 8 | 1 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 64 | 72 | 67 | 80 | 75 | 85 | 72 | 79 | #N/A | #N/A
2022-08-29 17:00 | 8 | 1 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 63 | 72 | 67 | 78 | 72 | 82 | 72 | 78 | #N/A | #N/A
2022-08-29 18:00 | 8 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 62 | 70 | 64 | 76 | 69 | 80 | 71 | 73 | #N/A | #N/A
2022-08-29 19:00 | 8 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 62 | 69 | 60 | 74 | 67 | 77 | 71 | 73 | #N/A | #N/A
2022-08-29 20:00 | 8 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 60 | 69 | 58 | 73 | 65 | 76 | 70 | 69 | #N/A | #N/A
2022-08-29 21:00 | 8 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 60 | 68 | 56 | 72 | 63 | 76 | 69 | 67 | #N/A | #N/A
2022-08-29 22:00 | 8 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 61 | 68 | 55 | 71 | 63 | 71 | 69 | 65 | #N/A | #N/A
2022-08-29 23:00 | 8 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 60 | 68 | 54 | 71 | 62 | 70 | 70 | 64 | #N/A | #N/A
2022-08-30 | 8 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 59 | 67 | 54 | 71 | 62 | 70 | 70 | 63 | #N/A | #N/A
2022-08-30 01:00 | 8 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 60 | 68 | 54 | 71 | 61 | 68 | 70 | 64 | #N/A | #N/A
2022-08-30 02:00 | 8 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 60 | 67 | 54 | 71 | 60 | 68 | 70 | 63 | #N/A | #N/A
2022-08-30 03:00 | 8 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 60 | 68 | 54 | 72 | 58 | 69 | 70 | 64 | #N/A | #N/A
2022-08-30 04:00 | 8 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 60 | 67 | 54 | 72 | 57 | 69 | 69 | 63 | #N/A | #N/A
2022-08-30 05:00 | 8 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 60 | 66 | 54 | 72 | 57 | 68 | 69 | 62 | #N/A | #N/A
2022-08-30 06:00 | 8 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 62 | 65 | 56 | 72 | 60 | 68 | 70 | 67 | #N/A | #N/A
2022-08-30 07:00 | 8 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 64 | 66 | 61 | 74 | 65 | 70 | 71 | 70 | #N/A | #N/A
2022-08-30 08:00 | 8 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 66 | 68 | 66 | 78 | 69 | 73 | 73 | 74 | #N/A | #N/A
2022-08-30 09:00 | 8 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 65 | 70 | 69 | 81 | 73 | 76 | 76 | 76 | #N/A | #N/A
2022-08-30 10:00 | 8 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 64 | 71 | 72 | 83 | 76 | 79 | 80 | 80 | #N/A | #N/A
2022-08-30 11:00 | 8 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 64 | 72 | 73 | 84 | 78 | 81 | 82 | 82 | #N/A | #N/A
2022-08-30 12:00 | 8 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 62 | 73 | 76 | 85 | 79 | 83 | 80 | 84 | #N/A | #N/A
2022-08-30 13:00 | 8 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 62 | 74 | 75 | 86 | 80 | 83 | 82 | 83 | #N/A | #N/A
2022-08-30 14:00 | 8 | 2 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 62 | 74 | 77 | 86 | 80 | 83 | 81 | 83 | #N/A | #N/A
2022-08-30 15:00 | 8 | 2 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 62 | 72 | 75 | 86 | 79 | 83 | 80 | 84 | #N/A | #N/A
2022-08-30 16:00 | 8 | 2 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 61 | 69 | 75 | 85 | 77 | 82 | 79 | 82 | #N/A | #N/A
2022-08-30 17:00 | 8 | 2 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 61 | 68 | 74 | 83 | 74 | 80 | 76 | 77 | #N/A | #N/A
2022-08-30 18:00 | 8 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 60 | 64 | 69 | 78 | 70 | 77 | 72 | 72 | #N/A | #N/A
2022-08-30 19:00 | 8 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 60 | 62 | 66 | 75 | 67 | 74 | 70 | 70 | #N/A | #N/A
2022-08-30 20:00 | 8 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 60 | 65 | 71 | 64 | 71 | 69 | 72 | #N/A | #N/A
2022-08-30 21:00 | 8 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 59 | 57 | 64 | 68 | 63 | 68 | 68 | 68 | #N/A | #N/A
2022-08-30 22:00 | 8 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 59 | 56 | 63 | 70 | 61 | 63 | 66 | 67 | #N/A | #N/A
2022-08-30 23:00 | 8 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 56 | 55 | 63 | 68 | 61 | 59 | 66 | 65 | #N/A | #N/A
2022-08-31 | 8 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 55 | 51 | 63 | 68 | 60 | 61 | 63 | 63 | #N/A | #N/A
2022-08-31 01:00 | 8 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 54 | 50 | 63 | 64 | 59 | 62 | 62 | 64 | #N/A | #N/A
2022-08-31 02:00 | 8 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 53 | 49 | 62 | 64 | 59 | 58 | 62 | 64 | #N/A | #N/A
2022-08-31 03:00 | 8 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 53 | 52 | 64 | 62 | 57 | 57 | 60 | 65 | #N/A | #N/A
2022-08-31 04:00 | 8 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 53 | 49 | 64 | 60 | 58 | 57 | 59 | 65 | #N/A | #N/A
2022-08-31 05:00 | 8 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 52 | 50 | 64 | 61 | 58 | 57 | 59 | 63 | #N/A | #N/A
2022-08-31 06:00 | 8 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 52 | 55 | 65 | 65 | 62 | 58 | 62 | 65 | #N/A | #N/A
2022-08-31 07:00 | 8 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 53 | 61 | 66 | 69 | 67 | 65 | 64 | 68 | #N/A | #N/A
2022-08-31 08:00 | 8 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 53 | 65 | 64 | 72 | 71 | 70 | 66 | 73 | #N/A | #N/A
2022-08-31 09:00 | 8 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 54 | 66 | 61 | 74 | 75 | 75 | 69 | 76 | #N/A | #N/A
2022-08-31 10:00 | 8 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 54 | 68 | 63 | 76 | 77 | 77 | 71 | 77 | #N/A | #N/A
2022-08-31 11:00 | 8 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 55 | 71 | 67 | 78 | 77 | 79 | 73 | 78 | #N/A | #N/A
2022-08-31 12:00 | 8 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 55 | 72 | 67 | 80 | 80 | 82 | 74 | 81 | #N/A | #N/A
2022-08-31 13:00 | 8 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 55 | 75 | 68 | 80 | 79 | 83 | 76 | 82 | #N/A | #N/A
2022-08-31 14:00 | 8 | 3 | 15 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 56 | 76 | 70 | 82 | 77 | 85 | 77 | 83 | #N/A | #N/A
2022-08-31 15:00 | 8 | 3 | 16 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 56 | 75 | 71 | 82 | 76 | 85 | 78 | 82 | #N/A | #N/A
2022-08-31 16:00 | 8 | 3 | 17 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 55 | 76 | 65 | 82 | 76 | 84 | 77 | 82 | #N/A | #N/A
2022-08-31 17:00 | 8 | 3 | 18 | 1 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 55 | 74 | 65 | 83 | 74 | 81 | 76 | 79 | #N/A | #N/A
2022-08-31 18:00 | 8 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 54 | 68 | 64 | 77 | 72 | 77 | 70 | 70 | #N/A | #N/A
2022-08-31 19:00 | 8 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 53 | 64 | 60 | 71 | 70 | 74 | 67 | 66 | #N/A | #N/A
2022-08-31 20:00 | 8 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 52 | 64 | 61 | 71 | 70 | 72 | 66 | 62 | #N/A | #N/A
2022-08-31 21:00 | 8 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 53 | 61 | 63 | 69 | 71 | 71 | 64 | 62 | #N/A | #N/A
2022-08-31 22:00 | 8 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 53 | 58 | 64 | 68 | 72 | 70 | 62 | 63 | #N/A | #N/A
2022-08-31 23:00 | 8 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 54 | 55 | 66 | 66 | 73 | 69 | 60 | 63 | #N/A | #N/A
2022-09-01 | 9 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 54 | 51 | 67 | 64 | 73 | 67 | 58 | 63 | #N/A | #N/A
2022-09-01 01:00 | 9 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 55 | 48 | 69 | 62 | 74 | 66 | 55 | 64 | #N/A | #N/A
2022-09-01 02:00 | 9 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 55 | 45 | 70 | 61 | 75 | 65 | 53 | 64 | #N/A | #N/A
2022-09-01 03:00 | 9 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 56 | 42 | 72 | 59 | 76 | 64 | 51 | 64 | #N/A | #N/A
2022-09-01 04:00 | 9 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 57 | 41 | 71 | 60 | 76 | 64 | 52 | 63 | #N/A | #N/A
2022-09-01 05:00 | 9 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 57 | 42 | 71 | 57 | 77 | 63 | 52 | 62 | #N/A | #N/A
2022-09-01 06:00 | 9 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 58 | 46 | 72 | 59 | 78 | 64 | 53 | 62 | #N/A | #N/A
2022-09-01 07:00 | 9 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 61 | 54 | 76 | 64 | 80 | 68 | 59 | 64 | #N/A | #N/A
2022-09-01 08:00 | 9 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 64 | 64 | 78 | 67 | 82 | 72 | 65 | 68 | #N/A | #N/A
2022-09-01 09:00 | 9 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 67 | 68 | 74 | 69 | 84 | 77 | 71 | 71 | #N/A | #N/A
2022-09-01 10:00 | 9 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 69 | 70 | 77 | 68 | 86 | 79 | 73 | 73 | #N/A | #N/A
2022-09-01 11:00 | 9 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 72 | 71 | 81 | 68 | 88 | 81 | 75 | 75 | #N/A | #N/A
2022-09-01 12:00 | 9 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 74 | 74 | 78 | 70 | 89 | 82 | 77 | 77 | #N/A | #N/A
2022-09-01 13:00 | 9 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 73 | 74 | 81 | 71 | 88 | 82 | 77 | 78 | #N/A | #N/A
2022-09-01 14:00 | 9 | 4 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 73 | 73 | 78 | 71 | 88 | 83 | 76 | 79 | #N/A | #N/A
2022-09-01 15:00 | 9 | 4 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 72 | 73 | 80 | 73 | 87 | 83 | 76 | 79 | #N/A | #N/A
2022-09-01 16:00 | 9 | 4 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 69 | 71 | 80 | 71 | 85 | 81 | 75 | 79 | #N/A | #N/A
2022-09-01 17:00 | 9 | 4 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 66 | 69 | 80 | 70 | 82 | 80 | 74 | 77 | #N/A | #N/A
2022-09-01 18:00 | 9 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 63 | 64 | 78 | 66 | 80 | 76 | 73 | 69 | #N/A | #N/A
2022-09-01 19:00 | 9 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 62 | 58 | 77 | 62 | 79 | 73 | 72 | 64 | #N/A | #N/A
2022-09-01 20:00 | 9 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 61 | 56 | 76 | 59 | 77 | 73 | 70 | 65 | #N/A | #N/A
2022-09-01 21:00 | 9 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 60 | 55 | 75 | 58 | 77 | 71 | 69 | 62 | #N/A | #N/A
2022-09-01 22:00 | 9 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 59 | 53 | 75 | 57 | 76 | 70 | 68 | 60 | #N/A | #N/A
2022-09-01 23:00 | 9 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 58 | 52 | 75 | 56 | 75 | 69 | 67 | 59 | #N/A | #N/A
2022-09-02 | 9 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 57 | 51 | 74 | 56 | 74 | 68 | 66 | 58 | #N/A | #N/A
2022-09-02 01:00 | 9 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 57 | 54 | 73 | 54 | 73 | 68 | 65 | 57 | #N/A | #N/A
2022-09-02 02:00 | 9 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 56 | 51 | 73 | 52 | 73 | 67 | 65 | 56 | #N/A | #N/A
2022-09-02 03:00 | 9 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 56 | 51 | 71 | 50 | 72 | 67 | 64 | 57 | #N/A | #N/A
2022-09-02 04:00 | 9 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 56 | 47 | 71 | 51 | 71 | 66 | 63 | 57 | #N/A | #N/A
2022-09-02 05:00 | 9 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 55 | 48 | 72 | 50 | 70 | 67 | 62 | 55 | #N/A | #N/A
2022-09-02 06:00 | 9 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 55 | 50 | 72 | 57 | 69 | 68 | 61 | 55 | #N/A | #N/A
2022-09-02 07:00 | 9 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 56 | 60 | 75 | 61 | 70 | 69 | 61 | 56 | #N/A | #N/A
2022-09-02 08:00 | 9 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 56 | 64 | 79 | 67 | 72 | 73 | 60 | 56 | #N/A | #N/A
2022-09-02 09:00 | 9 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 57 | 68 | 81 | 72 | 77 | 77 | 60 | 58 | #N/A | #N/A
2022-09-02 10:00 | 9 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 58 | 71 | 80 | 75 | 78 | 80 | 61 | 65 | #N/A | #N/A
2022-09-02 11:00 | 9 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 59 | 72 | 77 | 77 | 81 | 82 | 62 | 71 | #N/A | #N/A
2022-09-02 12:00 | 9 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 60 | 74 | 78 | 79 | 82 | 82 | 63 | 77 | #N/A | #N/A
2022-09-02 13:00 | 9 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 61 | 74 | 78 | 79 | 81 | 81 | 63 | 78 | #N/A | #N/A
2022-09-02 14:00 | 9 | 5 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 61 | 74 | 80 | 77 | 81 | 80 | 63 | 79 | #N/A | #N/A
2022-09-02 15:00 | 9 | 5 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 62 | 75 | 79 | 76 | 83 | 77 | 63 | 80 | #N/A | #N/A
2022-09-02 16:00 | 9 | 5 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 60 | 72 | 81 | 75 | 80 | 76 | 62 | 79 | #N/A | #N/A
2022-09-02 17:00 | 9 | 5 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 58 | 72 | 77 | 72 | 80 | 76 | 62 | 76 | #N/A | #N/A
2022-09-02 18:00 | 9 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 56 | 64 | 74 | 69 | 77 | 75 | 61 | 75 | #N/A | #N/A
2022-09-02 19:00 | 9 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 54 | 59 | 73 | 68 | 73 | 73 | 58 | 69 | #N/A | #N/A
2022-09-02 20:00 | 9 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 52 | 57 | 73 | 66 | 71 | 72 | 56 | 67 | #N/A | #N/A
2022-09-02 21:00 | 9 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 50 | 56 | 72 | 64 | 70 | 70 | 53 | 63 | #N/A | #N/A
2022-09-02 22:00 | 9 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 49 | 56 | 72 | 62 | 69 | 70 | 52 | 62 | #N/A | #N/A
2022-09-02 23:00 | 9 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 49 | 58 | 71 | 60 | 69 | 70 | 50 | 60 | #N/A | #N/A
2022-09-03 | 9 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 48 | 59 | 71 | 59 | 68 | 70 | 49 | 59 | #N/A | #N/A
2022-09-03 01:00 | 9 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 47 | 58 | 69 | 59 | 66 | 69 | 48 | 59 | #N/A | #N/A
2022-09-03 02:00 | 9 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 47 | 56 | 70 | 58 | 66 | 70 | 47 | 59 | #N/A | #N/A
2022-09-03 03:00 | 9 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 46 | 57 | 70 | 59 | 65 | 70 | 46 | 58 | #N/A | #N/A
2022-09-03 04:00 | 9 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 44 | 56 | 70 | 57 | 65 | 69 | 46 | 58 | #N/A | #N/A
2022-09-03 05:00 | 9 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 42 | 57 | 68 | 56 | 65 | 68 | 46 | 58 | #N/A | #N/A
2022-09-03 06:00 | 9 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 40 | 57 | 69 | 59 | 68 | 69 | 46 | 59 | #N/A | #N/A
2022-09-03 07:00 | 9 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 45 | 59 | 72 | 62 | 73 | 70 | 50 | 60 | #N/A | #N/A
2022-09-03 08:00 | 9 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 51 | 63 | 75 | 65 | 76 | 70 | 55 | 61 | #N/A | #N/A
2022-09-03 09:00 | 9 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 56 | 65 | 75 | 68 | 78 | 73 | 59 | 66 | #N/A | #N/A
2022-09-03 10:00 | 9 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 59 | 67 | 76 | 70 | 80 | 75 | 62 | 69 | #N/A | #N/A
2022-09-03 11:00 | 9 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 61 | 67 | 78 | 72 | 82 | 77 | 66 | 69 | #N/A | #N/A
2022-09-03 12:00 | 9 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 64 | 70 | 79 | 74 | 83 | 79 | 69 | 71 | #N/A | #N/A
2022-09-03 13:00 | 9 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 65 | 69 | 80 | 73 | 84 | 81 | 70 | 74 | #N/A | #N/A
2022-09-03 14:00 | 9 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 66 | 69 | 79 | 75 | 85 | 80 | 70 | 75 | #N/A | #N/A
2022-09-03 15:00 | 9 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 67 | 71 | 77 | 74 | 85 | 81 | 71 | 77 | #N/A | #N/A
2022-09-03 16:00 | 9 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 65 | 71 | 78 | 74 | 83 | 81 | 69 | 75 | #N/A | #N/A
2022-09-03 17:00 | 9 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 69 | 76 | 72 | 81 | 80 | 66 | 74 | #N/A | #N/A
2022-09-03 18:00 | 9 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 60 | 67 | 74 | 68 | 74 | 77 | 64 | 72 | #N/A | #N/A
2022-09-03 19:00 | 9 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 59 | 66 | 71 | 61 | 72 | 74 | 63 | 70 | #N/A | #N/A
2022-09-03 20:00 | 9 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 58 | 66 | 71 | 59 | 70 | 71 | 61 | 70 | #N/A | #N/A
2022-09-03 21:00 | 9 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 57 | 65 | 69 | 61 | 69 | 71 | 60 | 68 | #N/A | #N/A
2022-09-03 22:00 | 9 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 57 | 63 | 68 | 57 | 68 | 69 | 58 | 66 | #N/A | #N/A
2022-09-03 23:00 | 9 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 56 | 61 | 69 | 54 | 67 | 69 | 57 | 65 | #N/A | #N/A
2022-09-04 | 9 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 56 | 61 | 70 | 54 | 67 | 67 | 55 | 65 | #N/A | #N/A
2022-09-04 01:00 | 9 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 55 | 61 | 72 | 53 | 66 | 67 | 56 | 66 | #N/A | #N/A
2022-09-04 02:00 | 9 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 55 | 61 | 72 | 52 | 65 | 66 | 56 | 65 | #N/A | #N/A
2022-09-04 03:00 | 9 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 54 | 61 | 72 | 51 | 65 | 65 | 57 | 65 | #N/A | #N/A
2022-09-04 04:00 | 9 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 55 | 61 | 71 | 52 | 64 | 65 | 58 | 64 | #N/A | #N/A
2022-09-04 05:00 | 9 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 55 | 61 | 70 | 51 | 64 | 64 | 59 | 64 | #N/A | #N/A
2022-09-04 06:00 | 9 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 56 | 62 | 71 | 55 | 67 | 65 | 60 | 65 | #N/A | #N/A
2022-09-04 07:00 | 9 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 58 | 62 | 69 | 61 | 72 | 68 | 62 | 68 | #N/A | #N/A
2022-09-04 08:00 | 9 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 60 | 63 | 67 | 64 | 76 | 73 | 63 | 69 | #N/A | #N/A
2022-09-04 09:00 | 9 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 62 | 63 | 64 | 68 | 80 | 77 | 65 | 71 | #N/A | #N/A
2022-09-04 10:00 | 9 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 64 | 63 | 70 | 82 | 79 | 67 | 72 | #N/A | #N/A
2022-09-04 11:00 | 9 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 67 | 65 | 62 | 73 | 84 | 82 | 70 | 73 | #N/A | #N/A
2022-09-04 12:00 | 9 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 69 | 66 | 62 | 74 | 85 | 83 | 72 | 74 | #N/A | #N/A
2022-09-04 13:00 | 9 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 69 | 66 | 62 | 74 | 86 | 84 | 73 | 77 | #N/A | #N/A
2022-09-04 14:00 | 9 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 70 | 63 | 75 | 88 | 84 | 75 | 78 | #N/A | #N/A
2022-09-04 15:00 | 9 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 75 | 70 | 70 | 61 | 75 | 87 | 83 | 76 | 79 | #N/A | #N/A
2022-09-04 16:00 | 9 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 69 | 69 | 61 | 73 | 85 | 82 | 74 | 79 | #N/A | #N/A
2022-09-04 17:00 | 9 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 68 | 65 | 61 | 72 | 81 | 80 | 72 | 77 | #N/A | #N/A
2022-09-04 18:00 | 9 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 67 | 62 | 59 | 68 | 77 | 77 | 70 | 67 | #N/A | #N/A
2022-09-04 19:00 | 9 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 67 | 61 | 56 | 65 | 74 | 76 | 70 | 64 | #N/A | #N/A
2022-09-04 20:00 | 9 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 66 | 58 | 54 | 62 | 72 | 74 | 69 | 63 | #N/A | #N/A
2022-09-04 21:00 | 9 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 66 | 58 | 54 | 59 | 71 | 73 | 69 | 60 | #N/A | #N/A
2022-09-04 22:00 | 9 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 65 | 57 | 55 | 59 | 69 | 70 | 68 | 59 | #N/A | #N/A
2022-09-04 23:00 | 9 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 64 | 57 | 54 | 60 | 69 | 69 | 68 | 58 | #N/A | #N/A
2022-09-05 | 9 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 63 | 57 | 56 | 58 | 68 | 68 | 67 | 56 | #N/A | #N/A
2022-09-05 01:00 | 9 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 63 | 57 | 55 | 57 | 67 | 68 | 67 | 55 | #N/A | #N/A
2022-09-05 02:00 | 9 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 62 | 56 | 53 | 54 | 67 | 68 | 67 | 55 | #N/A | #N/A
2022-09-05 03:00 | 9 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 62 | 56 | 53 | 54 | 67 | 67 | 67 | 56 | #N/A | #N/A
2022-09-05 04:00 | 9 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 60 | 56 | 53 | 52 | 66 | 67 | 67 | 55 | #N/A | #N/A
2022-09-05 05:00 | 9 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 59 | 56 | 52 | 53 | 67 | 67 | 67 | 54 | #N/A | #N/A
2022-09-05 06:00 | 9 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 57 | 56 | 52 | 55 | 68 | 67 | 67 | 57 | #N/A | #N/A
2022-09-05 07:00 | 9 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 58 | 52 | 53 | 58 | 71 | 70 | 67 | 63 | #N/A | #N/A
2022-09-05 08:00 | 9 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 60 | 51 | 56 | 62 | 75 | 73 | 67 | 67 | #N/A | #N/A
2022-09-05 09:00 | 9 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 61 | 50 | 59 | 64 | 79 | 75 | 67 | 72 | #N/A | #N/A
2022-09-05 10:00 | 9 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 61 | 50 | 60 | 67 | 82 | 77 | 68 | 75 | #N/A | #N/A
2022-09-05 11:00 | 9 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 61 | 52 | 61 | 68 | 85 | 79 | 68 | 78 | #N/A | #N/A
2022-09-05 12:00 | 9 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 61 | 51 | 62 | 68 | 86 | 79 | 69 | 80 | #N/A | #N/A
2022-09-05 13:00 | 9 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 61 | 49 | 63 | 68 | 88 | 78 | 70 | 83 | #N/A | #N/A
2022-09-05 14:00 | 9 | 1 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 61 | 50 | 63 | 68 | 86 | 77 | 70 | 84 | #N/A | #N/A
2022-09-05 15:00 | 9 | 1 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 61 | 50 | 63 | 68 | 87 | 76 | 71 | 84 | #N/A | #N/A
2022-09-05 16:00 | 9 | 1 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 59 | 49 | 62 | 68 | 87 | 75 | 68 | 82 | #N/A | #N/A
2022-09-05 17:00 | 9 | 1 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 56 | 49 | 61 | 68 | 82 | 73 | 66 | 80 | #N/A | #N/A
2022-09-05 18:00 | 9 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 54 | 46 | 59 | 67 | 79 | 72 | 63 | 75 | #N/A | #N/A
2022-09-05 19:00 | 9 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 53 | 47 | 57 | 66 | 76 | 71 | 61 | 72 | #N/A | #N/A
2022-09-05 20:00 | 9 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 51 | 46 | 56 | 65 | 74 | 70 | 58 | 68 | #N/A | #N/A
2022-09-05 21:00 | 9 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 50 | 45 | 51 | 65 | 73 | 70 | 56 | 67 | #N/A | #N/A
2022-09-05 22:00 | 9 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 50 | 45 | 50 | 64 | 73 | 70 | 55 | 66 | #N/A | #N/A
2022-09-05 23:00 | 9 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 50 | 44 | 49 | 64 | 71 | 70 | 53 | 65 | #N/A | #N/A
2022-09-06 | 9 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 50 | 44 | 50 | 64 | 70 | 70 | 52 | 64 | #N/A | #N/A
2022-09-06 01:00 | 9 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 49 | 41 | 51 | 64 | 69 | 70 | 52 | 63 | #N/A | #N/A
2022-09-06 02:00 | 9 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 49 | 39 | 50 | 63 | 69 | 69 | 51 | 63 | #N/A | #N/A
2022-09-06 03:00 | 9 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 48 | 39 | 50 | 61 | 68 | 69 | 51 | 64 | #N/A | #N/A
2022-09-06 04:00 | 9 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 48 | 38 | 49 | 61 | 68 | 70 | 51 | 64 | #N/A | #N/A
2022-09-06 05:00 | 9 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 47 | 36 | 48 | 61 | 67 | 70 | 50 | 64 | #N/A | #N/A
2022-09-06 06:00 | 9 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 47 | 39 | 50 | 61 | 71 | 70 | 50 | 63 | #N/A | #N/A
2022-09-06 07:00 | 9 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 50 | 44 | 53 | 61 | 79 | 71 | 53 | 64 | #N/A | #N/A
2022-09-06 08:00 | 9 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 53 | 45 | 59 | 61 | 84 | 72 | 56 | 66 | #N/A | #N/A
2022-09-06 09:00 | 9 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 56 | 48 | 63 | 62 | 84 | 73 | 59 | 68 | #N/A | #N/A
2022-09-06 10:00 | 9 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 58 | 49 | 65 | 62 | 87 | 77 | 61 | 72 | #N/A | #N/A
2022-09-06 11:00 | 9 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 60 | 54 | 67 | 63 | 90 | 79 | 64 | 77 | #N/A | #N/A
2022-09-06 12:00 | 9 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 62 | 53 | 71 | 64 | 92 | 81 | 66 | 80 | #N/A | #N/A
2022-09-06 13:00 | 9 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 62 | 55 | 70 | 65 | 91 | 81 | 66 | 84 | #N/A | #N/A
2022-09-06 14:00 | 9 | 2 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 61 | 53 | 68 | 65 | 93 | 82 | 67 | 87 | #N/A | #N/A
2022-09-06 15:00 | 9 | 2 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 61 | 54 | 68 | 65 | 90 | 81 | 67 | 88 | #N/A | #N/A
2022-09-06 16:00 | 9 | 2 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 59 | 52 | 68 | 65 | 84 | 79 | 65 | 87 | #N/A | #N/A
2022-09-06 17:00 | 9 | 2 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 57 | 51 | 67 | 65 | 82 | 77 | 63 | 84 | #N/A | #N/A
2022-09-06 18:00 | 9 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 55 | 50 | 64 | 65 | 78 | 75 | 61 | 82 | #N/A | #N/A
2022-09-06 19:00 | 9 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 54 | 47 | 56 | 65 | 76 | 72 | 59 | 78 | #N/A | #N/A
2022-09-06 20:00 | 9 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 52 | 47 | 54 | 65 | 74 | 72 | 56 | 75 | #N/A | #N/A
2022-09-06 21:00 | 9 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 51 | 46 | 52 | 65 | 72 | 71 | 54 | 75 | #N/A | #N/A
2022-09-06 22:00 | 9 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 50 | 47 | 57 | 65 | 71 | 70 | 52 | 75 | #N/A | #N/A
2022-09-06 23:00 | 9 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 49 | 47 | 56 | 65 | 70 | 68 | 50 | 74 | #N/A | #N/A
2022-09-07 | 9 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 48 | 47 | 56 | 65 | 70 | 67 | 48 | 76 | #N/A | #N/A
2022-09-07 01:00 | 9 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 48 | 47 | 56 | 65 | 70 | 67 | 47 | 77 | #N/A | #N/A
2022-09-07 02:00 | 9 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 49 | 46 | 56 | 65 | 70 | 67 | 47 | 76 | #N/A | #N/A
2022-09-07 03:00 | 9 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 49 | 46 | 55 | 65 | 69 | 65 | 46 | 75 | #N/A | #N/A
2022-09-07 04:00 | 9 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 49 | 45 | 54 | 65 | 69 | 65 | 47 | 74 | #N/A | #N/A
2022-09-07 05:00 | 9 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 50 | 44 | 54 | 65 | 69 | 65 | 48 | 73 | #N/A | #N/A
2022-09-07 06:00 | 9 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 50 | 47 | 55 | 66 | 70 | 66 | 49 | 74 | #N/A | #N/A
2022-09-07 07:00 | 9 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 58 | 53 | 49 | 58 | 66 | 73 | 67 | 54 | 77 | #N/A | #N/A
2022-09-07 08:00 | 9 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 57 | 54 | 62 | 67 | 78 | 69 | 58 | 79 | #N/A | #N/A
2022-09-07 09:00 | 9 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 60 | 56 | 68 | 67 | 81 | 71 | 63 | 80 | #N/A | #N/A
2022-09-07 10:00 | 9 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 63 | 58 | 71 | 69 | 84 | 71 | 66 | 82 | #N/A | #N/A
2022-09-07 11:00 | 9 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 67 | 59 | 73 | 71 | 86 | 74 | 70 | 84 | #N/A | #N/A
2022-09-07 12:00 | 9 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 70 | 59 | 74 | 71 | 87 | 76 | 73 | 83 | #N/A | #N/A
2022-09-07 13:00 | 9 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 71 | 59 | 76 | 71 | 89 | 73 | 74 | 83 | #N/A | #N/A
2022-09-07 14:00 | 9 | 3 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 72 | 61 | 77 | 71 | 88 | 74 | 76 | 83 | #N/A | #N/A
2022-09-07 15:00 | 9 | 3 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 73 | 61 | 77 | 72 | 86 | 73 | 77 | 81 | #N/A | #N/A
2022-09-07 16:00 | 9 | 3 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 71 | 59 | 77 | 73 | 85 | 70 | 76 | 81 | #N/A | #N/A
2022-09-07 17:00 | 9 | 3 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 69 | 58 | 74 | 72 | 82 | 69 | 74 | 80 | #N/A | #N/A
2022-09-07 18:00 | 9 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 67 | 53 | 69 | 72 | 78 | 64 | 73 | 79 | #N/A | #N/A
2022-09-07 19:00 | 9 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 66 | 48 | 65 | 71 | 75 | 62 | 71 | 77 | #N/A | #N/A
2022-09-07 20:00 | 9 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 65 | 46 | 64 | 70 | 74 | 59 | 68 | 73 | #N/A | #N/A
2022-09-07 21:00 | 9 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 64 | 44 | 64 | 70 | 74 | 58 | 66 | 71 | #N/A | #N/A
2022-09-07 22:00 | 9 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 63 | 44 | 63 | 70 | 73 | 58 | 65 | 70 | #N/A | #N/A
2022-09-07 23:00 | 9 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 61 | 44 | 63 | 70 | 72 | 58 | 65 | 68 | #N/A | #N/A
2022-09-08 | 9 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 60 | 43 | 63 | 70 | 71 | 57 | 64 | 68 | #N/A | #N/A
2022-09-08 01:00 | 9 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 60 | 42 | 63 | 70 | 72 | 57 | 64 | 66 | #N/A | #N/A
2022-09-08 02:00 | 9 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 59 | 41 | 62 | 70 | 71 | 57 | 63 | 65 | #N/A | #N/A
2022-09-08 03:00 | 9 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 59 | 39 | 64 | 70 | 70 | 56 | 63 | 64 | #N/A | #N/A
2022-09-08 04:00 | 9 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 59 | 39 | 65 | 70 | 69 | 55 | 62 | 63 | #N/A | #N/A
2022-09-08 05:00 | 9 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 59 | 40 | 66 | 70 | 69 | 55 | 61 | 61 | #N/A | #N/A
2022-09-08 06:00 | 9 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 59 | 45 | 66 | 71 | 72 | 54 | 60 | 61 | #N/A | #N/A
2022-09-08 07:00 | 9 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 63 | 53 | 67 | 71 | 75 | 55 | 65 | 61 | #N/A | #N/A
2022-09-08 08:00 | 9 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 66 | 57 | 71 | 71 | 80 | 57 | 69 | 61 | #N/A | #N/A
2022-09-08 09:00 | 9 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 70 | 60 | 74 | 70 | 83 | 60 | 74 | 63 | #N/A | #N/A
2022-09-08 10:00 | 9 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 72 | 62 | 78 | 69 | 85 | 62 | 77 | 64 | #N/A | #N/A
2022-09-08 11:00 | 9 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 75 | 65 | 81 | 69 | 87 | 61 | 79 | 64 | #N/A | #N/A
2022-09-08 12:00 | 9 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 77 | 68 | 80 | 70 | 88 | 60 | 82 | 63 | #N/A | #N/A
2022-09-08 13:00 | 9 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 77 | 68 | 78 | 70 | 87 | 60 | 82 | 63 | #N/A | #N/A
2022-09-08 14:00 | 9 | 4 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 77 | 68 | 80 | 70 | 89 | 62 | 83 | 64 | #N/A | #N/A
2022-09-08 15:00 | 9 | 4 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 77 | 68 | 78 | 70 | 77 | 61 | 83 | 64 | #N/A | #N/A
2022-09-08 16:00 | 9 | 4 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 74 | 66 | 76 | 72 | 73 | 60 | 81 | 64 | #N/A | #N/A
2022-09-08 17:00 | 9 | 4 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 72 | 64 | 74 | 73 | 72 | 59 | 78 | 64 | #N/A | #N/A
2022-09-08 18:00 | 9 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 69 | 59 | 73 | 71 | 72 | 56 | 76 | 63 | #N/A | #N/A
2022-09-08 19:00 | 9 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 67 | 54 | 72 | 70 | 71 | 55 | 73 | 62 | #N/A | #N/A
2022-09-08 20:00 | 9 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 66 | 54 | 72 | 69 | 71 | 53 | 70 | 62 | #N/A | #N/A
2022-09-08 21:00 | 9 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 64 | 53 | 70 | 69 | 71 | 52 | 67 | 62 | #N/A | #N/A
2022-09-08 22:00 | 9 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 54 | 71 | 68 | 70 | 51 | 66 | 62 | #N/A | #N/A
2022-09-08 23:00 | 9 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 53 | 72 | 67 | 70 | 49 | 65 | 62 | #N/A | #N/A
2022-09-09 | 9 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 61 | 52 | 71 | 66 | 69 | 48 | 64 | 60 | #N/A | #N/A
2022-09-09 01:00 | 9 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 61 | 51 | 70 | 66 | 69 | 48 | 63 | 61 | #N/A | #N/A
2022-09-09 02:00 | 9 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 62 | 51 | 69 | 66 | 69 | 47 | 61 | 63 | #N/A | #N/A
2022-09-09 03:00 | 9 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 62 | 51 | 70 | 65 | 68 | 47 | 60 | 63 | #N/A | #N/A
2022-09-09 04:00 | 9 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 59 | 49 | 69 | 65 | 68 | 45 | 60 | 64 | #N/A | #N/A
2022-09-09 05:00 | 9 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 57 | 45 | 69 | 66 | 67 | 45 | 60 | 66 | #N/A | #N/A
2022-09-09 06:00 | 9 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 54 | 47 | 70 | 68 | 69 | 46 | 60 | 66 | #N/A | #N/A
2022-09-09 07:00 | 9 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 57 | 55 | 70 | 71 | 71 | 49 | 64 | 67 | #N/A | #N/A
2022-09-09 08:00 | 9 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 60 | 60 | 73 | 74 | 74 | 53 | 67 | 68 | #N/A | #N/A
2022-09-09 09:00 | 9 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 63 | 64 | 74 | 77 | 78 | 58 | 71 | 71 | #N/A | #N/A
2022-09-09 10:00 | 9 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 67 | 66 | 75 | 78 | 78 | 61 | 74 | 72 | #N/A | #N/A
2022-09-09 11:00 | 9 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 70 | 69 | 77 | 80 | 78 | 61 | 76 | 74 | #N/A | #N/A
2022-09-09 12:00 | 9 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 74 | 69 | 74 | 81 | 79 | 64 | 79 | 74 | #N/A | #N/A
2022-09-09 13:00 | 9 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 75 | 70 | 75 | 80 | 83 | 66 | 79 | 75 | #N/A | #N/A
2022-09-09 14:00 | 9 | 5 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 75 | 69 | 76 | 81 | 84 | 67 | 80 | 75 | #N/A | #N/A
2022-09-09 15:00 | 9 | 5 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 76 | 69 | 77 | 79 | 84 | 67 | 80 | 75 | #N/A | #N/A
2022-09-09 16:00 | 9 | 5 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 74 | 68 | 78 | 79 | 81 | 67 | 78 | 73 | #N/A | #N/A
2022-09-09 17:00 | 9 | 5 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 72 | 67 | 77 | 78 | 79 | 66 | 77 | 70 | #N/A | #N/A
2022-09-09 18:00 | 9 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 70 | 66 | 73 | 74 | 76 | 63 | 75 | 64 | #N/A | #N/A
2022-09-09 19:00 | 9 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 69 | 64 | 72 | 70 | 74 | 61 | 73 | 60 | #N/A | #N/A
2022-09-09 20:00 | 9 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 67 | 60 | 69 | 69 | 73 | 58 | 70 | 58 | #N/A | #N/A
2022-09-09 21:00 | 9 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 66 | 59 | 69 | 68 | 72 | 57 | 68 | 57 | #N/A | #N/A
2022-09-09 22:00 | 9 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 65 | 58 | 68 | 69 | 71 | 54 | 68 | 54 | #N/A | #N/A
2022-09-09 23:00 | 9 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 65 | 58 | 69 | 67 | 70 | 52 | 67 | 53 | #N/A | #N/A
2022-09-10 | 9 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 57 | 69 | 65 | 68 | 52 | 67 | 51 | #N/A | #N/A
2022-09-10 01:00 | 9 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 63 | 57 | 68 | 64 | 66 | 50 | 67 | 50 | #N/A | #N/A
2022-09-10 02:00 | 9 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 63 | 56 | 68 | 63 | 65 | 51 | 66 | 52 | #N/A | #N/A
2022-09-10 03:00 | 9 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 54 | 70 | 62 | 63 | 51 | 66 | 52 | #N/A | #N/A
2022-09-10 04:00 | 9 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 54 | 70 | 62 | 63 | 48 | 66 | 51 | #N/A | #N/A
2022-09-10 05:00 | 9 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 61 | 52 | 70 | 61 | 62 | 48 | 66 | 50 | #N/A | #N/A
2022-09-10 06:00 | 9 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 61 | 56 | 71 | 66 | 63 | 51 | 66 | 52 | #N/A | #N/A
2022-09-10 07:00 | 9 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 60 | 58 | 72 | 67 | 65 | 56 | 65 | 57 | #N/A | #N/A
2022-09-10 08:00 | 9 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 64 | 74 | 73 | 67 | 62 | 65 | 60 | #N/A | #N/A
2022-09-10 09:00 | 9 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 58 | 68 | 78 | 73 | 70 | 66 | 64 | 62 | #N/A | #N/A
2022-09-10 10:00 | 9 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 59 | 70 | 81 | 78 | 72 | 69 | 63 | 64 | #N/A | #N/A
2022-09-10 11:00 | 9 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 61 | 71 | 81 | 77 | 73 | 72 | 63 | 66 | #N/A | #N/A
2022-09-10 12:00 | 9 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 62 | 73 | 81 | 77 | 75 | 74 | 62 | 68 | #N/A | #N/A
2022-09-10 13:00 | 9 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 62 | 73 | 82 | 80 | 74 | 75 | 62 | 68 | #N/A | #N/A
2022-09-10 14:00 | 9 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 62 | 74 | 82 | 81 | 75 | 76 | 63 | 63 | #N/A | #N/A
2022-09-10 15:00 | 9 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 74 | 75 | 82 | 75 | 76 | 63 | 65 | #N/A | #N/A
2022-09-10 16:00 | 9 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 71 | 74 | 80 | 74 | 76 | 63 | 63 | #N/A | #N/A
2022-09-10 17:00 | 9 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 57 | 68 | 73 | 78 | 72 | 74 | 63 | 64 | #N/A | #N/A
2022-09-10 18:00 | 9 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 54 | 60 | 73 | 69 | 68 | 70 | 63 | 62 | #N/A | #N/A
2022-09-10 19:00 | 9 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 52 | 59 | 72 | 69 | 65 | 67 | 61 | 62 | #N/A | #N/A
2022-09-10 20:00 | 9 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 51 | 56 | 72 | 67 | 63 | 66 | 59 | 62 | #N/A | #N/A
2022-09-10 21:00 | 9 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 49 | 50 | 72 | 65 | 61 | 64 | 57 | 61 | #N/A | #N/A
2022-09-10 22:00 | 9 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 48 | 50 | 72 | 63 | 59 | 64 | 55 | 59 | #N/A | #N/A
2022-09-10 23:00 | 9 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 48 | 51 | 71 | 62 | 58 | 64 | 53 | 60 | #N/A | #N/A
2022-09-11 | 9 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 47 | 50 | 70 | 61 | 57 | 65 | 51 | 61 | #N/A | #N/A
2022-09-11 01:00 | 9 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 46 | 46 | 69 | 61 | 55 | 65 | 50 | 62 | #N/A | #N/A
2022-09-11 02:00 | 9 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 46 | 43 | 69 | 60 | 54 | 64 | 50 | 63 | #N/A | #N/A
2022-09-11 03:00 | 9 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 45 | 42 | 68 | 61 | 54 | 62 | 49 | 64 | #N/A | #N/A
2022-09-11 04:00 | 9 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 45 | 42 | 67 | 60 | 53 | 61 | 49 | 65 | #N/A | #N/A
2022-09-11 05:00 | 9 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 46 | 45 | 68 | 62 | 54 | 62 | 49 | 64 | #N/A | #N/A
2022-09-11 06:00 | 9 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 46 | 44 | 68 | 64 | 57 | 60 | 49 | 64 | #N/A | #N/A
2022-09-11 07:00 | 9 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 48 | 48 | 71 | 65 | 61 | 64 | 52 | 64 | #N/A | #N/A
2022-09-11 08:00 | 9 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 50 | 53 | 73 | 69 | 64 | 67 | 55 | 66 | #N/A | #N/A
2022-09-11 09:00 | 9 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 52 | 57 | 76 | 71 | 68 | 69 | 58 | 67 | #N/A | #N/A
2022-09-11 10:00 | 9 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 52 | 60 | 79 | 75 | 70 | 72 | 59 | 69 | #N/A | #N/A
2022-09-11 11:00 | 9 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 51 | 62 | 80 | 78 | 73 | 71 | 61 | 71 | #N/A | #N/A
2022-09-11 12:00 | 9 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 51 | 61 | 80 | 79 | 73 | 72 | 62 | 76 | #N/A | #N/A
2022-09-11 13:00 | 9 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 51 | 60 | 83 | 80 | 74 | 72 | 63 | 77 | #N/A | #N/A
2022-09-11 14:00 | 9 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 52 | 60 | 82 | 82 | 75 | 73 | 63 | 78 | #N/A | #N/A
2022-09-11 15:00 | 9 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 52 | 58 | 80 | 81 | 76 | 73 | 64 | 78 | #N/A | #N/A
2022-09-11 16:00 | 9 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 52 | 56 | 79 | 80 | 75 | 75 | 63 | 78 | #N/A | #N/A
2022-09-11 17:00 | 9 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 51 | 53 | 78 | 77 | 73 | 73 | 62 | 78 | #N/A | #N/A
2022-09-11 18:00 | 9 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 51 | 50 | 73 | 76 | 69 | 71 | 61 | 75 | #N/A | #N/A
2022-09-11 19:00 | 9 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 50 | 47 | 73 | 76 | 65 | 69 | 58 | 73 | #N/A | #N/A
2022-09-11 20:00 | 9 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 50 | 46 | 73 | 74 | 62 | 67 | 55 | 71 | #N/A | #N/A
2022-09-11 21:00 | 9 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 49 | 44 | 74 | 73 | 60 | 66 | 52 | 71 | #N/A | #N/A
2022-09-11 22:00 | 9 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 48 | 43 | 72 | 72 | 60 | 64 | 51 | 69 | #N/A | #N/A
2022-09-11 23:00 | 9 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 48 | 42 | 72 | 68 | 60 | 62 | 51 | 69 | #N/A | #N/A
2022-09-12 | 9 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 47 | 40 | 71 | 68 | 59 | 60 | 50 | 68 | #N/A | #N/A
2022-09-12 01:00 | 9 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 46 | 40 | 71 | 68 | 58 | 59 | 49 | 68 | #N/A | #N/A
2022-09-12 02:00 | 9 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 46 | 38 | 72 | 68 | 60 | 59 | 48 | 68 | #N/A | #N/A
2022-09-12 03:00 | 9 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 45 | 39 | 72 | 69 | 58 | 57 | 47 | 67 | #N/A | #N/A
2022-09-12 04:00 | 9 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 46 | 39 | 71 | 69 | 56 | 56 | 47 | 67 | #N/A | #N/A
2022-09-12 05:00 | 9 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 46 | 38 | 70 | 68 | 57 | 56 | 47 | 66 | #N/A | #N/A
2022-09-12 06:00 | 9 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 47 | 40 | 69 | 68 | 62 | 56 | 47 | 66 | #N/A | #N/A
2022-09-12 07:00 | 9 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 58 | 52 | 48 | 70 | 69 | 67 | 60 | 53 | 68 | #N/A | #N/A
2022-09-12 08:00 | 9 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 56 | 55 | 74 | 69 | 70 | 63 | 59 | 71 | #N/A | #N/A
2022-09-12 09:00 | 9 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 61 | 66 | 78 | 70 | 74 | 67 | 65 | 76 | #N/A | #N/A
2022-09-12 10:00 | 9 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 64 | 71 | 77 | 71 | 77 | 73 | 68 | 82 | #N/A | #N/A
2022-09-12 11:00 | 9 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 67 | 74 | 76 | 72 | 79 | 77 | 71 | 71 | #N/A | #N/A
2022-09-12 12:00 | 9 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 70 | 74 | 76 | 76 | 81 | 79 | 74 | 73 | #N/A | #N/A
2022-09-12 13:00 | 9 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 72 | 77 | 74 | 76 | 79 | 80 | 75 | 75 | #N/A | #N/A
2022-09-12 14:00 | 9 | 1 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 73 | 76 | 74 | 75 | 80 | 81 | 77 | 76 | #N/A | #N/A
2022-09-12 15:00 | 9 | 1 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 82 | 75 | 74 | 72 | 74 | 77 | 81 | 78 | 70 | #N/A | #N/A
2022-09-12 16:00 | 9 | 1 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 73 | 72 | 71 | 73 | 78 | 80 | 75 | 68 | #N/A | #N/A
2022-09-12 17:00 | 9 | 1 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 71 | 70 | 70 | 73 | 76 | 77 | 73 | 67 | #N/A | #N/A
2022-09-12 18:00 | 9 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 69 | 67 | 69 | 72 | 74 | 73 | 70 | 66 | #N/A | #N/A
2022-09-12 19:00 | 9 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 67 | 65 | 67 | 72 | 72 | 70 | 69 | 64 | #N/A | #N/A
2022-09-12 20:00 | 9 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 65 | 63 | 67 | 72 | 71 | 68 | 67 | 63 | #N/A | #N/A
2022-09-12 21:00 | 9 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 63 | 63 | 66 | 72 | 70 | 67 | 66 | 62 | #N/A | #N/A
2022-09-12 22:00 | 9 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 62 | 63 | 65 | 71 | 70 | 66 | 64 | 60 | #N/A | #N/A
2022-09-12 23:00 | 9 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 60 | 63 | 63 | 70 | 71 | 65 | 61 | 60 | #N/A | #N/A
2022-09-13 | 9 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 59 | 63 | 61 | 70 | 70 | 64 | 59 | 60 | #N/A | #N/A
2022-09-13 01:00 | 9 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 58 | 64 | 54 | 70 | 70 | 64 | 58 | 59 | #N/A | #N/A
2022-09-13 02:00 | 9 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 57 | 64 | 53 | 70 | 70 | 63 | 57 | 59 | #N/A | #N/A
2022-09-13 03:00 | 9 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 56 | 65 | 52 | 70 | 70 | 62 | 56 | 59 | #N/A | #N/A
2022-09-13 04:00 | 9 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 57 | 65 | 51 | 70 | 70 | 61 | 56 | 56 | #N/A | #N/A
2022-09-13 05:00 | 9 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 58 | 65 | 51 | 70 | 71 | 61 | 55 | 57 | #N/A | #N/A
2022-09-13 06:00 | 9 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 59 | 65 | 53 | 70 | 72 | 61 | 55 | 57 | #N/A | #N/A
2022-09-13 07:00 | 9 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 62 | 66 | 57 | 72 | 74 | 64 | 59 | 60 | #N/A | #N/A
2022-09-13 08:00 | 9 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 65 | 67 | 65 | 73 | 75 | 69 | 64 | 61 | #N/A | #N/A
2022-09-13 09:00 | 9 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 68 | 67 | 66 | 74 | 78 | 72 | 68 | 63 | #N/A | #N/A
2022-09-13 10:00 | 9 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 71 | 65 | 66 | 75 | 82 | 75 | 72 | 66 | #N/A | #N/A
2022-09-13 11:00 | 9 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 84 | 74 | 61 | 67 | 75 | 82 | 78 | 76 | 68 | #N/A | #N/A
2022-09-13 12:00 | 9 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 77 | 59 | 66 | 77 | 85 | 81 | 80 | 69 | #N/A | #N/A
2022-09-13 13:00 | 9 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 77 | 59 | 67 | 79 | 85 | 81 | 81 | 70 | #N/A | #N/A
2022-09-13 14:00 | 9 | 2 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 78 | 61 | 68 | 79 | 86 | 78 | 81 | 70 | #N/A | #N/A
2022-09-13 15:00 | 9 | 2 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 87 | 78 | 60 | 67 | 77 | 84 | 78 | 82 | 71 | #N/A | #N/A
2022-09-13 16:00 | 9 | 2 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 76 | 59 | 67 | 77 | 83 | 74 | 79 | 70 | #N/A | #N/A
2022-09-13 17:00 | 9 | 2 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 73 | 57 | 66 | 74 | 83 | 72 | 75 | 68 | #N/A | #N/A
2022-09-13 18:00 | 9 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 71 | 51 | 62 | 72 | 83 | 68 | 72 | 63 | #N/A | #N/A
2022-09-13 19:00 | 9 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 72 | 69 | 50 | 58 | 72 | 76 | 65 | 70 | 60 | #N/A | #N/A
2022-09-13 20:00 | 9 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 67 | 49 | 57 | 69 | 73 | 65 | 68 | 60 | #N/A | #N/A
2022-09-13 21:00 | 9 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 65 | 46 | 56 | 68 | 74 | 65 | 66 | 59 | #N/A | #N/A
2022-09-13 22:00 | 9 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 65 | 42 | 56 | 67 | 74 | 65 | 64 | 59 | #N/A | #N/A
2022-09-13 23:00 | 9 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 64 | 45 | 56 | 65 | 73 | 65 | 63 | 59 | #N/A | #N/A
2022-09-14 | 9 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 64 | 43 | 56 | 65 | 73 | 66 | 61 | 59 | #N/A | #N/A
2022-09-14 01:00 | 9 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 63 | 44 | 57 | 66 | 73 | 68 | 61 | 59 | #N/A | #N/A
2022-09-14 02:00 | 9 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 62 | 41 | 57 | 65 | 73 | 69 | 60 | 59 | #N/A | #N/A
2022-09-14 03:00 | 9 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 61 | 40 | 58 | 64 | 73 | 70 | 60 | 59 | #N/A | #N/A
2022-09-14 04:00 | 9 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 61 | 38 | 57 | 63 | 73 | 70 | 59 | 58 | #N/A | #N/A
2022-09-14 05:00 | 9 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 62 | 38 | 57 | 63 | 73 | 71 | 59 | 58 | #N/A | #N/A
2022-09-14 06:00 | 9 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 62 | 40 | 58 | 66 | 73 | 72 | 58 | 59 | #N/A | #N/A
2022-09-14 07:00 | 9 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 64 | 48 | 62 | 69 | 74 | 74 | 62 | 60 | #N/A | #N/A
2022-09-14 08:00 | 9 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 67 | 54 | 68 | 71 | 76 | 69 | 65 | 62 | #N/A | #N/A
2022-09-14 09:00 | 9 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 69 | 58 | 71 | 74 | 81 | 65 | 69 | 63 | #N/A | #N/A
2022-09-14 10:00 | 9 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 79 | 72 | 61 | 73 | 77 | 83 | 65 | 74 | 65 | #N/A | #N/A
2022-09-14 11:00 | 9 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 74 | 64 | 72 | 79 | 87 | 66 | 78 | 65 | #N/A | #N/A
2022-09-14 12:00 | 9 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 77 | 66 | 71 | 81 | 87 | 65 | 83 | 67 | #N/A | #N/A
2022-09-14 13:00 | 9 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 77 | 65 | 69 | 82 | 91 | 66 | 83 | 68 | #N/A | #N/A
2022-09-14 14:00 | 9 | 3 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 77 | 67 | 68 | 81 | 88 | 62 | 84 | 69 | #N/A | #N/A
2022-09-14 15:00 | 9 | 3 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 86 | 77 | 64 | 68 | 80 | 83 | 64 | 84 | 68 | #N/A | #N/A
2022-09-14 16:00 | 9 | 3 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 83 | 75 | 64 | 67 | 79 | 85 | 61 | 81 | 68 | #N/A | #N/A
2022-09-14 17:00 | 9 | 3 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 73 | 61 | 66 | 76 | 82 | 62 | 77 | 67 | #N/A | #N/A
2022-09-14 18:00 | 9 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 71 | 58 | 60 | 70 | 81 | 60 | 74 | 66 | #N/A | #N/A
2022-09-14 19:00 | 9 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 70 | 56 | 58 | 67 | 80 | 58 | 71 | 66 | #N/A | #N/A
2022-09-14 20:00 | 9 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 69 | 53 | 58 | 64 | 78 | 58 | 68 | 65 | #N/A | #N/A
2022-09-14 21:00 | 9 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 68 | 52 | 61 | 63 | 75 | 56 | 65 | 65 | #N/A | #N/A
2022-09-14 22:00 | 9 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 67 | 49 | 60 | 62 | 72 | 53 | 64 | 65 | #N/A | #N/A
2022-09-14 23:00 | 9 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 67 | 47 | 61 | 60 | 70 | 51 | 64 | 64 | #N/A | #N/A
2022-09-15 | 9 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 66 | 44 | 61 | 59 | 67 | 50 | 63 | 64 | #N/A | #N/A
2022-09-15 01:00 | 9 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 65 | 42 | 61 | 58 | 66 | 51 | 63 | 62 | #N/A | #N/A
2022-09-15 02:00 | 9 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 65 | 42 | 61 | 58 | 65 | 50 | 63 | 61 | #N/A | #N/A
2022-09-15 03:00 | 9 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 64 | 41 | 61 | 58 | 63 | 49 | 63 | 61 | #N/A | #N/A
2022-09-15 04:00 | 9 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 64 | 46 | 58 | 57 | 62 | 48 | 63 | 61 | #N/A | #N/A
2022-09-15 05:00 | 9 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 63 | 45 | 60 | 56 | 62 | 48 | 62 | 61 | #N/A | #N/A
2022-09-15 06:00 | 9 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 63 | 45 | 60 | 57 | 64 | 48 | 62 | 62 | #N/A | #N/A
2022-09-15 07:00 | 9 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 65 | 46 | 60 | 61 | 67 | 53 | 64 | 63 | #N/A | #N/A
2022-09-15 08:00 | 9 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 66 | 53 | 60 | 66 | 71 | 57 | 67 | 64 | #N/A | #N/A
2022-09-15 09:00 | 9 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 68 | 55 | 57 | 69 | 71 | 58 | 69 | 65 | #N/A | #N/A
2022-09-15 10:00 | 9 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 69 | 58 | 60 | 71 | 74 | 60 | 72 | 66 | #N/A | #N/A
2022-09-15 11:00 | 9 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 70 | 59 | 60 | 75 | 76 | 62 | 74 | 67 | #N/A | #N/A
2022-09-15 12:00 | 9 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 71 | 60 | 56 | 75 | 77 | 62 | 77 | 69 | #N/A | #N/A
2022-09-15 13:00 | 9 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 71 | 62 | 57 | 74 | 77 | 64 | 77 | 72 | #N/A | #N/A
2022-09-15 14:00 | 9 | 4 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 71 | 62 | 54 | 77 | 79 | 65 | 76 | 75 | #N/A | #N/A
2022-09-15 15:00 | 9 | 4 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 71 | 63 | 59 | 76 | 77 | 64 | 76 | 80 | #N/A | #N/A
2022-09-15 16:00 | 9 | 4 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 70 | 61 | 59 | 74 | 76 | 64 | 74 | 78 | #N/A | #N/A
2022-09-15 17:00 | 9 | 4 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 69 | 58 | 57 | 72 | 74 | 62 | 72 | 74 | #N/A | #N/A
2022-09-15 18:00 | 9 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 68 | 50 | 55 | 70 | 73 | 58 | 70 | 68 | #N/A | #N/A
2022-09-15 19:00 | 9 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 67 | 45 | 58 | 69 | 68 | 56 | 69 | 66 | #N/A | #N/A
2022-09-15 20:00 | 9 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 66 | 43 | 58 | 70 | 66 | 54 | 68 | 63 | #N/A | #N/A
2022-09-15 21:00 | 9 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 65 | 41 | 57 | 68 | 64 | 53 | 67 | 63 | #N/A | #N/A
2022-09-15 22:00 | 9 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 64 | 40 | 57 | 67 | 64 | 50 | 66 | 62 | #N/A | #N/A
2022-09-15 23:00 | 9 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 64 | 38 | 57 | 66 | 62 | 48 | 66 | 60 | #N/A | #N/A
2022-09-16 | 9 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 63 | 37 | 56 | 66 | 61 | 47 | 65 | 59 | #N/A | #N/A
2022-09-16 01:00 | 9 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 63 | 35 | 56 | 66 | 61 | 46 | 64 | 58 | #N/A | #N/A
2022-09-16 02:00 | 9 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 62 | 34 | 55 | 64 | 62 | 46 | 63 | 57 | #N/A | #N/A
2022-09-16 03:00 | 9 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 62 | 35 | 54 | 62 | 62 | 45 | 62 | 57 | #N/A | #N/A
2022-09-16 04:00 | 9 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 61 | 35 | 53 | 61 | 62 | 44 | 62 | 57 | #N/A | #N/A
2022-09-16 05:00 | 9 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 38 | 54 | 61 | 61 | 44 | 63 | 57 | #N/A | #N/A
2022-09-16 06:00 | 9 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 39 | 53 | 63 | 63 | 45 | 63 | 58 | #N/A | #N/A
2022-09-16 07:00 | 9 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 60 | 44 | 54 | 67 | 65 | 50 | 63 | 59 | #N/A | #N/A
2022-09-16 08:00 | 9 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 62 | 50 | 55 | 71 | 71 | 57 | 64 | 60 | #N/A | #N/A
2022-09-16 09:00 | 9 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 63 | 53 | 54 | 73 | 70 | 62 | 64 | 63 | #N/A | #N/A
2022-09-16 10:00 | 9 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 64 | 56 | 56 | 76 | 71 | 64 | 65 | 64 | #N/A | #N/A
2022-09-16 11:00 | 9 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 64 | 59 | 56 | 76 | 73 | 66 | 66 | 67 | #N/A | #N/A
2022-09-16 12:00 | 9 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 65 | 62 | 59 | 79 | 72 | 67 | 67 | 68 | #N/A | #N/A
2022-09-16 13:00 | 9 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 65 | 64 | 59 | 81 | 71 | 68 | 67 | 69 | #N/A | #N/A
2022-09-16 14:00 | 9 | 5 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 65 | 65 | 57 | 80 | 70 | 69 | 66 | 72 | #N/A | #N/A
2022-09-16 15:00 | 9 | 5 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 65 | 64 | 57 | 80 | 69 | 69 | 66 | 74 | #N/A | #N/A
2022-09-16 16:00 | 9 | 5 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 64 | 63 | 59 | 78 | 68 | 70 | 66 | 75 | #N/A | #N/A
2022-09-16 17:00 | 9 | 5 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 64 | 59 | 58 | 77 | 67 | 66 | 66 | 72 | #N/A | #N/A
2022-09-16 18:00 | 9 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 56 | 58 | 77 | 66 | 65 | 66 | 68 | #N/A | #N/A
2022-09-16 19:00 | 9 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 56 | 57 | 76 | 64 | 61 | 66 | 66 | #N/A | #N/A
2022-09-16 20:00 | 9 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 63 | 55 | 57 | 74 | 63 | 59 | 67 | 66 | #N/A | #N/A
2022-09-16 21:00 | 9 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 63 | 55 | 52 | 73 | 62 | 58 | 67 | 63 | #N/A | #N/A
2022-09-16 22:00 | 9 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 55 | 50 | 72 | 62 | 55 | 67 | 61 | #N/A | #N/A
2022-09-16 23:00 | 9 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 63 | 55 | 50 | 71 | 63 | 53 | 66 | 60 | #N/A | #N/A
2022-09-17 | 9 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 63 | 56 | 50 | 70 | 64 | 53 | 66 | 60 | #N/A | #N/A
2022-09-17 01:00 | 9 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 63 | 57 | 51 | 69 | 64 | 52 | 66 | 59 | #N/A | #N/A
2022-09-17 02:00 | 9 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 62 | 57 | 51 | 69 | 64 | 51 | 66 | 59 | #N/A | #N/A
2022-09-17 03:00 | 9 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 62 | 57 | 53 | 69 | 63 | 49 | 66 | 58 | #N/A | #N/A
2022-09-17 04:00 | 9 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 62 | 55 | 51 | 69 | 64 | 49 | 66 | 57 | #N/A | #N/A
2022-09-17 05:00 | 9 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 62 | 55 | 52 | 69 | 65 | 46 | 66 | 57 | #N/A | #N/A
2022-09-17 06:00 | 9 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 62 | 56 | 53 | 68 | 63 | 49 | 66 | 56 | #N/A | #N/A
2022-09-17 07:00 | 9 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 73 | 63 | 57 | 56 | 70 | 63 | 54 | 69 | 56 | #N/A | #N/A
2022-09-17 08:00 | 9 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 65 | 58 | 60 | 73 | 63 | 59 | 71 | 57 | #N/A | #N/A
2022-09-17 09:00 | 9 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 66 | 59 | 64 | 74 | 63 | 64 | 74 | 59 | #N/A | #N/A
2022-09-17 10:00 | 9 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 76 | 69 | 59 | 66 | 73 | 65 | 69 | 75 | 62 | #N/A | #N/A
2022-09-17 11:00 | 9 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 71 | 61 | 69 | 74 | 65 | 71 | 77 | 65 | #N/A | #N/A
2022-09-17 12:00 | 9 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 74 | 62 | 71 | 74 | 67 | 73 | 78 | 68 | #N/A | #N/A
2022-09-17 13:00 | 9 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 78 | 71 | 63 | 71 | 78 | 69 | 74 | 77 | 70 | #N/A | #N/A
2022-09-17 14:00 | 9 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 79 | 67 | 63 | 72 | 80 | 71 | 74 | 77 | 70 | #N/A | #N/A
2022-09-17 15:00 | 9 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 80 | 64 | 63 | 72 | 78 | 71 | 74 | 76 | 71 | #N/A | #N/A
2022-09-17 16:00 | 9 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 77 | 64 | 64 | 71 | 70 | 71 | 74 | 73 | 70 | #N/A | #N/A
2022-09-17 17:00 | 9 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 74 | 65 | 64 | 69 | 71 | 71 | 72 | 71 | 69 | #N/A | #N/A
2022-09-17 18:00 | 9 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 65 | 64 | 63 | 69 | 69 | 67 | 68 | 67 | #N/A | #N/A
2022-09-17 19:00 | 9 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 63 | 64 | 63 | 69 | 68 | 64 | 67 | 67 | #N/A | #N/A
2022-09-17 20:00 | 9 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 62 | 64 | 63 | 66 | 67 | 61 | 67 | 65 | #N/A | #N/A
2022-09-17 21:00 | 9 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 60 | 63 | 62 | 65 | 65 | 60 | 66 | 65 | #N/A | #N/A
2022-09-17 22:00 | 9 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 60 | 62 | 62 | 66 | 65 | 58 | 65 | 64 | #N/A | #N/A
2022-09-17 23:00 | 9 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 59 | 63 | 60 | 66 | 64 | 56 | 63 | 64 | #N/A | #N/A
2022-09-18 | 9 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 59 | 63 | 59 | 66 | 65 | 56 | 62 | 64 | #N/A | #N/A
2022-09-18 01:00 | 9 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 58 | 63 | 58 | 66 | 64 | 55 | 61 | 65 | #N/A | #N/A
2022-09-18 02:00 | 9 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 58 | 62 | 57 | 67 | 65 | 55 | 61 | 64 | #N/A | #N/A
2022-09-18 03:00 | 9 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 57 | 62 | 56 | 66 | 64 | 53 | 60 | 65 | #N/A | #N/A
2022-09-18 04:00 | 9 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 57 | 62 | 55 | 66 | 63 | 52 | 60 | 65 | #N/A | #N/A
2022-09-18 05:00 | 9 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 57 | 62 | 54 | 66 | 62 | 49 | 60 | 65 | #N/A | #N/A
2022-09-18 06:00 | 9 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 57 | 62 | 54 | 67 | 63 | 52 | 60 | 66 | #N/A | #N/A
2022-09-18 07:00 | 9 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 58 | 62 | 58 | 68 | 66 | 58 | 61 | 67 | #N/A | #N/A
2022-09-18 08:00 | 9 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 59 | 63 | 63 | 70 | 69 | 63 | 62 | 68 | #N/A | #N/A
2022-09-18 09:00 | 9 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 60 | 65 | 67 | 74 | 72 | 68 | 63 | 70 | #N/A | #N/A
2022-09-18 10:00 | 9 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 62 | 65 | 70 | 76 | 73 | 71 | 65 | 73 | #N/A | #N/A
2022-09-18 11:00 | 9 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 65 | 66 | 68 | 77 | 76 | 71 | 67 | 78 | #N/A | #N/A
2022-09-18 12:00 | 9 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 67 | 71 | 70 | 78 | 76 | 71 | 69 | 80 | #N/A | #N/A
2022-09-18 13:00 | 9 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 70 | 67 | 72 | 70 | 74 | 76 | 71 | 69 | 81 | #N/A | #N/A
2022-09-18 14:00 | 9 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 67 | 73 | 71 | 72 | 77 | 73 | 70 | 82 | #N/A | #N/A
2022-09-18 15:00 | 9 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 67 | 75 | 71 | 71 | 76 | 72 | 70 | 81 | #N/A | #N/A
2022-09-18 16:00 | 9 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 66 | 73 | 71 | 72 | 75 | 73 | 69 | 79 | #N/A | #N/A
2022-09-18 17:00 | 9 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 64 | 68 | 70 | 69 | 73 | 71 | 68 | 77 | #N/A | #N/A
2022-09-18 18:00 | 9 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 63 | 65 | 67 | 64 | 70 | 67 | 67 | 75 | #N/A | #N/A
2022-09-18 19:00 | 9 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 62 | 65 | 65 | 62 | 67 | 65 | 67 | 75 | #N/A | #N/A
2022-09-18 20:00 | 9 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 62 | 63 | 65 | 60 | 66 | 66 | 66 | 74 | #N/A | #N/A
2022-09-18 21:00 | 9 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 61 | 64 | 63 | 59 | 64 | 64 | 66 | 74 | #N/A | #N/A
2022-09-18 22:00 | 9 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 61 | 65 | 62 | 59 | 63 | 64 | 66 | 74 | #N/A | #N/A
2022-09-18 23:00 | 9 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 61 | 65 | 62 | 57 | 61 | 63 | 65 | 74 | #N/A | #N/A
2022-09-19 | 9 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 61 | 64 | 61 | 57 | 61 | 62 | 65 | 74 | #N/A | #N/A
2022-09-19 01:00 | 9 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 60 | 64 | 61 | 56 | 60 | 62 | 65 | 74 | #N/A | #N/A
2022-09-19 02:00 | 9 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 60 | 64 | 60 | 56 | 59 | 60 | 64 | 72 | #N/A | #N/A
2022-09-19 03:00 | 9 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 59 | 64 | 60 | 56 | 59 | 58 | 64 | 73 | #N/A | #N/A
2022-09-19 04:00 | 9 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 58 | 64 | 60 | 56 | 58 | 56 | 63 | 72 | #N/A | #N/A
2022-09-19 05:00 | 9 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 58 | 64 | 59 | 56 | 58 | 56 | 62 | 72 | #N/A | #N/A
2022-09-19 06:00 | 9 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 57 | 64 | 59 | 56 | 59 | 56 | 61 | 72 | #N/A | #N/A
2022-09-19 07:00 | 9 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 60 | 64 | 61 | 56 | 63 | 56 | 63 | 72 | #N/A | #N/A
2022-09-19 08:00 | 9 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 63 | 65 | 64 | 57 | 66 | 57 | 65 | 71 | #N/A | #N/A
2022-09-19 09:00 | 9 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 66 | 68 | 69 | 57 | 68 | 58 | 67 | 72 | #N/A | #N/A
2022-09-19 10:00 | 9 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 68 | 70 | 73 | 58 | 72 | 60 | 70 | 71 | #N/A | #N/A
2022-09-19 11:00 | 9 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 77 | 70 | 74 | 74 | 58 | 75 | 61 | 73 | 72 | #N/A | #N/A
2022-09-19 12:00 | 9 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 72 | 75 | 76 | 58 | 76 | 62 | 76 | 71 | #N/A | #N/A
2022-09-19 13:00 | 9 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 80 | 72 | 77 | 77 | 58 | 75 | 63 | 76 | 70 | #N/A | #N/A
2022-09-19 14:00 | 9 | 1 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 71 | 77 | 77 | 58 | 73 | 63 | 77 | 69 | #N/A | #N/A
2022-09-19 15:00 | 9 | 1 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 81 | 71 | 75 | 75 | 58 | 70 | 63 | 77 | 68 | #N/A | #N/A
2022-09-19 16:00 | 9 | 1 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 78 | 69 | 75 | 75 | 58 | 69 | 62 | 74 | 67 | #N/A | #N/A
2022-09-19 17:00 | 9 | 1 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 68 | 72 | 72 | 58 | 68 | 60 | 70 | 67 | #N/A | #N/A
2022-09-19 18:00 | 9 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 71 | 66 | 70 | 68 | 58 | 67 | 56 | 67 | 67 | #N/A | #N/A
2022-09-19 19:00 | 9 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 64 | 69 | 67 | 58 | 66 | 53 | 66 | 67 | #N/A | #N/A
2022-09-19 20:00 | 9 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 62 | 69 | 66 | 58 | 66 | 50 | 64 | 66 | #N/A | #N/A
2022-09-19 21:00 | 9 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 68 | 65 | 58 | 65 | 47 | 63 | 66 | #N/A | #N/A
2022-09-19 22:00 | 9 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 59 | 68 | 66 | 58 | 64 | 46 | 61 | 66 | #N/A | #N/A
2022-09-19 23:00 | 9 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 58 | 68 | 67 | 58 | 64 | 46 | 59 | 65 | #N/A | #N/A
2022-09-20 | 9 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 57 | 67 | 67 | 58 | 65 | 44 | 57 | 65 | #N/A | #N/A
2022-09-20 01:00 | 9 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 57 | 67 | 68 | 58 | 64 | 42 | 57 | 65 | #N/A | #N/A
2022-09-20 02:00 | 9 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 57 | 67 | 68 | 58 | 64 | 42 | 57 | 65 | #N/A | #N/A
2022-09-20 03:00 | 9 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 57 | 67 | 66 | 58 | 64 | 42 | 57 | 65 | #N/A | #N/A
2022-09-20 04:00 | 9 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 58 | 68 | 67 | 58 | 64 | 43 | 57 | 65 | #N/A | #N/A
2022-09-20 05:00 | 9 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 58 | 68 | 67 | 57 | 63 | 39 | 57 | 65 | #N/A | #N/A
2022-09-20 06:00 | 9 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 59 | 65 | 67 | 57 | 64 | 40 | 57 | 65 | #N/A | #N/A
2022-09-20 07:00 | 9 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 60 | 66 | 70 | 57 | 64 | 47 | 61 | 65 | #N/A | #N/A
2022-09-20 08:00 | 9 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 62 | 66 | 73 | 58 | 66 | 52 | 64 | 66 | #N/A | #N/A
2022-09-20 09:00 | 9 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 63 | 68 | 76 | 59 | 71 | 59 | 68 | 66 | #N/A | #N/A
2022-09-20 10:00 | 9 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 63 | 68 | 79 | 60 | 72 | 64 | 69 | 68 | #N/A | #N/A
2022-09-20 11:00 | 9 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 75 | 64 | 72 | 81 | 62 | 74 | 66 | 71 | 70 | #N/A | #N/A
2022-09-20 12:00 | 9 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 76 | 64 | 73 | 82 | 62 | 75 | 69 | 72 | 71 | #N/A | #N/A
2022-09-20 13:00 | 9 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 63 | 73 | 82 | 63 | 75 | 71 | 70 | 72 | #N/A | #N/A
2022-09-20 14:00 | 9 | 2 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 63 | 74 | 82 | 62 | 75 | 70 | 67 | 73 | #N/A | #N/A
2022-09-20 15:00 | 9 | 2 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 62 | 70 | 83 | 62 | 75 | 69 | 65 | 74 | #N/A | #N/A
2022-09-20 16:00 | 9 | 2 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 61 | 69 | 80 | 62 | 73 | 68 | 64 | 73 | #N/A | #N/A
2022-09-20 17:00 | 9 | 2 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 61 | 68 | 78 | 62 | 73 | 66 | 64 | 72 | #N/A | #N/A
2022-09-20 18:00 | 9 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 60 | 65 | 78 | 61 | 72 | 64 | 63 | 71 | #N/A | #N/A
2022-09-20 19:00 | 9 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 59 | 63 | 70 | 59 | 69 | 62 | 63 | 70 | #N/A | #N/A
2022-09-20 20:00 | 9 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 58 | 60 | 71 | 58 | 68 | 58 | 63 | 68 | #N/A | #N/A
2022-09-20 21:00 | 9 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 57 | 58 | 72 | 59 | 67 | 59 | 63 | 68 | #N/A | #N/A
2022-09-20 22:00 | 9 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 56 | 58 | 61 | 59 | 67 | 59 | 63 | 66 | #N/A | #N/A
2022-09-20 23:00 | 9 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 55 | 58 | 61 | 60 | 67 | 58 | 62 | 66 | #N/A | #N/A
2022-09-21 | 9 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 54 | 58 | 59 | 60 | 67 | 60 | 62 | 66 | #N/A | #N/A
2022-09-21 01:00 | 9 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 53 | 57 | 58 | 61 | 66 | 60 | 62 | 66 | #N/A | #N/A
2022-09-21 02:00 | 9 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 52 | 56 | 57 | 60 | 66 | 59 | 61 | 66 | #N/A | #N/A
2022-09-21 03:00 | 9 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 51 | 55 | 56 | 60 | 66 | 60 | 61 | 66 | #N/A | #N/A
2022-09-21 04:00 | 9 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 51 | 55 | 54 | 60 | 66 | 61 | 60 | 67 | #N/A | #N/A
2022-09-21 05:00 | 9 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 51 | 55 | 54 | 60 | 67 | 61 | 59 | 67 | #N/A | #N/A
2022-09-21 06:00 | 9 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 51 | 54 | 54 | 61 | 68 | 61 | 58 | 68 | #N/A | #N/A
2022-09-21 07:00 | 9 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 52 | 54 | 55 | 62 | 69 | 62 | 59 | 68 | #N/A | #N/A
2022-09-21 08:00 | 9 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 53 | 55 | 55 | 63 | 70 | 62 | 59 | 69 | #N/A | #N/A
2022-09-21 09:00 | 9 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 54 | 56 | 57 | 66 | 75 | 62 | 60 | 70 | #N/A | #N/A
2022-09-21 10:00 | 9 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 55 | 56 | 58 | 67 | 76 | 62 | 61 | 72 | #N/A | #N/A
2022-09-21 11:00 | 9 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 56 | 57 | 59 | 71 | 77 | 62 | 61 | 74 | #N/A | #N/A
2022-09-21 12:00 | 9 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 57 | 56 | 59 | 73 | 79 | 62 | 62 | 76 | #N/A | #N/A
2022-09-21 13:00 | 9 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 58 | 56 | 59 | 71 | 80 | 62 | 62 | 77 | #N/A | #N/A
2022-09-21 14:00 | 9 | 3 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 58 | 53 | 59 | 73 | 82 | 61 | 63 | 78 | #N/A | #N/A
2022-09-21 15:00 | 9 | 3 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 59 | 53 | 59 | 70 | 80 | 61 | 63 | 79 | #N/A | #N/A
2022-09-21 16:00 | 9 | 3 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 57 | 52 | 59 | 63 | 79 | 60 | 61 | 79 | #N/A | #N/A
2022-09-21 17:00 | 9 | 3 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 55 | 52 | 59 | 63 | 77 | 60 | 59 | 77 | #N/A | #N/A
2022-09-21 18:00 | 9 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 53 | 51 | 59 | 62 | 74 | 60 | 57 | 77 | #N/A | #N/A
2022-09-21 19:00 | 9 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 52 | 51 | 58 | 62 | 73 | 60 | 55 | 74 | #N/A | #N/A
2022-09-21 20:00 | 9 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 51 | 51 | 57 | 61 | 72 | 60 | 52 | 74 | #N/A | #N/A
2022-09-21 21:00 | 9 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 50 | 51 | 57 | 59 | 72 | 59 | 50 | 72 | #N/A | #N/A
2022-09-21 22:00 | 9 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 49 | 51 | 57 | 57 | 71 | 60 | 49 | 72 | #N/A | #N/A
2022-09-21 23:00 | 9 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 47 | 51 | 56 | 57 | 71 | 59 | 47 | 71 | #N/A | #N/A
2022-09-22 | 9 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 46 | 50 | 57 | 54 | 71 | 59 | 46 | 71 | #N/A | #N/A
2022-09-22 01:00 | 9 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 46 | 50 | 50 | 54 | 71 | 59 | 46 | 71 | #N/A | #N/A
2022-09-22 02:00 | 9 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 46 | 50 | 50 | 52 | 71 | 58 | 46 | 72 | #N/A | #N/A
2022-09-22 03:00 | 9 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 46 | 49 | 49 | 54 | 70 | 58 | 46 | 71 | #N/A | #N/A
2022-09-22 04:00 | 9 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 46 | 49 | 48 | 55 | 70 | 58 | 47 | 70 | #N/A | #N/A
2022-09-22 05:00 | 9 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 46 | 50 | 49 | 54 | 71 | 58 | 47 | 68 | #N/A | #N/A
2022-09-22 06:00 | 9 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 46 | 50 | 50 | 54 | 70 | 58 | 48 | 66 | #N/A | #N/A
2022-09-22 07:00 | 9 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 47 | 51 | 54 | 57 | 70 | 57 | 50 | 66 | #N/A | #N/A
2022-09-22 08:00 | 9 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 49 | 53 | 58 | 61 | 69 | 58 | 52 | 67 | #N/A | #N/A
2022-09-22 09:00 | 9 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 58 | 50 | 55 | 59 | 65 | 70 | 58 | 54 | 67 | #N/A | #N/A
2022-09-22 10:00 | 9 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 51 | 58 | 59 | 67 | 69 | 60 | 56 | 67 | #N/A | #N/A
2022-09-22 11:00 | 9 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 61 | 52 | 59 | 62 | 68 | 73 | 60 | 58 | 66 | #N/A | #N/A
2022-09-22 12:00 | 9 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 53 | 62 | 64 | 66 | 73 | 62 | 60 | 65 | #N/A | #N/A
2022-09-22 13:00 | 9 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 52 | 62 | 66 | 67 | 72 | 61 | 60 | 65 | #N/A | #N/A
2022-09-22 14:00 | 9 | 4 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 52 | 61 | 67 | 57 | 75 | 63 | 59 | 66 | #N/A | #N/A
2022-09-22 15:00 | 9 | 4 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 51 | 61 | 63 | 61 | 75 | 62 | 59 | 64 | #N/A | #N/A
2022-09-22 16:00 | 9 | 4 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 50 | 60 | 62 | 60 | 75 | 62 | 58 | 63 | #N/A | #N/A
2022-09-22 17:00 | 9 | 4 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 49 | 58 | 61 | 59 | 66 | 61 | 56 | 61 | #N/A | #N/A
2022-09-22 18:00 | 9 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 48 | 57 | 61 | 58 | 65 | 60 | 55 | 59 | #N/A | #N/A
2022-09-22 19:00 | 9 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 47 | 58 | 59 | 57 | 63 | 58 | 53 | 62 | #N/A | #N/A
2022-09-22 20:00 | 9 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 45 | 58 | 58 | 56 | 63 | 57 | 50 | 59 | #N/A | #N/A
2022-09-22 21:00 | 9 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 44 | 60 | 57 | 55 | 60 | 55 | 48 | 57 | #N/A | #N/A
2022-09-22 22:00 | 9 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 43 | 61 | 61 | 55 | 59 | 54 | 46 | 53 | #N/A | #N/A
2022-09-22 23:00 | 9 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 41 | 62 | 63 | 53 | 58 | 51 | 45 | 53 | #N/A | #N/A
2022-09-23 | 9 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 40 | 59 | 64 | 52 | 58 | 49 | 43 | 52 | #N/A | #N/A
2022-09-23 01:00 | 9 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 43 | 39 | 60 | 64 | 51 | 58 | 48 | 43 | 52 | #N/A | #N/A
2022-09-23 02:00 | 9 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 39 | 62 | 61 | 52 | 56 | 46 | 42 | 51 | #N/A | #N/A
2022-09-23 03:00 | 9 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 40 | 38 | 60 | 61 | 53 | 56 | 45 | 42 | 51 | #N/A | #N/A
2022-09-23 04:00 | 9 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 41 | 40 | 61 | 62 | 53 | 55 | 44 | 42 | 51 | #N/A | #N/A
2022-09-23 05:00 | 9 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 41 | 42 | 62 | 64 | 52 | 55 | 43 | 42 | 49 | #N/A | #N/A
2022-09-23 06:00 | 9 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 44 | 62 | 67 | 54 | 55 | 44 | 42 | 50 | #N/A | #N/A
2022-09-23 07:00 | 9 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 48 | 46 | 63 | 66 | 58 | 55 | 47 | 47 | 51 | #N/A | #N/A
2022-09-23 08:00 | 9 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 54 | 48 | 64 | 65 | 61 | 56 | 51 | 51 | 56 | #N/A | #N/A
2022-09-23 09:00 | 9 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 50 | 64 | 66 | 64 | 57 | 55 | 56 | 60 | #N/A | #N/A
2022-09-23 10:00 | 9 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 52 | 64 | 69 | 65 | 57 | 58 | 60 | 64 | #N/A | #N/A
2022-09-23 11:00 | 9 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 55 | 62 | 70 | 68 | 58 | 60 | 64 | 64 | #N/A | #N/A
2022-09-23 12:00 | 9 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 57 | 63 | 71 | 68 | 59 | 63 | 68 | 67 | #N/A | #N/A
2022-09-23 13:00 | 9 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 58 | 60 | 71 | 68 | 60 | 64 | 69 | 67 | #N/A | #N/A
2022-09-23 14:00 | 9 | 5 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 73 | 60 | 60 | 73 | 67 | 59 | 65 | 70 | 68 | #N/A | #N/A
2022-09-23 15:00 | 9 | 5 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 74 | 61 | 61 | 74 | 68 | 59 | 65 | 71 | 68 | #N/A | #N/A
2022-09-23 16:00 | 9 | 5 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 60 | 61 | 73 | 67 | 59 | 64 | 70 | 68 | #N/A | #N/A
2022-09-23 17:00 | 9 | 5 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 60 | 57 | 72 | 65 | 59 | 61 | 69 | 63 | #N/A | #N/A
2022-09-23 18:00 | 9 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 59 | 52 | 71 | 62 | 57 | 58 | 68 | 59 | #N/A | #N/A
2022-09-23 19:00 | 9 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 56 | 50 | 71 | 61 | 56 | 56 | 67 | 57 | #N/A | #N/A
2022-09-23 20:00 | 9 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 53 | 49 | 69 | 60 | 56 | 54 | 65 | 55 | #N/A | #N/A
2022-09-23 21:00 | 9 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 50 | 47 | 70 | 62 | 55 | 53 | 64 | 53 | #N/A | #N/A
2022-09-23 22:00 | 9 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 48 | 46 | 67 | 59 | 54 | 49 | 62 | 52 | #N/A | #N/A
2022-09-23 23:00 | 9 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 47 | 42 | 63 | 60 | 55 | 48 | 60 | 52 | #N/A | #N/A
2022-09-24 | 9 | 6 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 45 | 46 | 59 | 58 | 54 | 47 | 58 | 52 | #N/A | #N/A
2022-09-24 01:00 | 9 | 6 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 44 | 42 | 57 | 58 | 53 | 46 | 56 | 50 | #N/A | #N/A
2022-09-24 02:00 | 9 | 6 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 43 | 41 | 59 | 56 | 52 | 44 | 55 | 50 | #N/A | #N/A
2022-09-24 03:00 | 9 | 6 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 42 | 40 | 57 | 56 | 51 | 44 | 53 | 50 | #N/A | #N/A
2022-09-24 04:00 | 9 | 6 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 42 | 40 | 56 | 56 | 50 | 43 | 51 | 48 | #N/A | #N/A
2022-09-24 05:00 | 9 | 6 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 41 | 39 | 57 | 54 | 51 | 43 | 50 | 47 | #N/A | #N/A
2022-09-24 06:00 | 9 | 6 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 41 | 39 | 57 | 55 | 53 | 44 | 48 | 48 | #N/A | #N/A
2022-09-24 07:00 | 9 | 6 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 44 | 44 | 57 | 58 | 56 | 47 | 50 | 50 | #N/A | #N/A
2022-09-24 08:00 | 9 | 6 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 46 | 50 | 58 | 64 | 60 | 53 | 52 | 52 | #N/A | #N/A
2022-09-24 09:00 | 9 | 6 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 58 | 49 | 57 | 57 | 68 | 61 | 59 | 54 | 57 | #N/A | #N/A
2022-09-24 10:00 | 9 | 6 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 50 | 59 | 56 | 70 | 62 | 61 | 56 | 62 | #N/A | #N/A
2022-09-24 11:00 | 9 | 6 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 63 | 52 | 60 | 57 | 72 | 64 | 64 | 57 | 64 | #N/A | #N/A
2022-09-24 12:00 | 9 | 6 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 65 | 53 | 62 | 57 | 74 | 67 | 66 | 59 | 66 | #N/A | #N/A
2022-09-24 13:00 | 9 | 6 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 53 | 61 | 60 | 75 | 67 | 67 | 59 | 68 | #N/A | #N/A
2022-09-24 14:00 | 9 | 6 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 54 | 61 | 58 | 74 | 66 | 69 | 60 | 68 | #N/A | #N/A
2022-09-24 15:00 | 9 | 6 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 54 | 60 | 58 | 74 | 65 | 68 | 60 | 69 | #N/A | #N/A
2022-09-24 16:00 | 9 | 6 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 51 | 58 | 59 | 73 | 64 | 68 | 58 | 68 | #N/A | #N/A
2022-09-24 17:00 | 9 | 6 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 60 | 48 | 54 | 57 | 69 | 63 | 64 | 55 | 68 | #N/A | #N/A
2022-09-24 18:00 | 9 | 6 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 45 | 53 | 52 | 67 | 60 | 62 | 53 | 67 | #N/A | #N/A
2022-09-24 19:00 | 9 | 6 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 43 | 49 | 55 | 66 | 60 | 57 | 51 | 64 | #N/A | #N/A
2022-09-24 20:00 | 9 | 6 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 42 | 48 | 56 | 62 | 59 | 55 | 50 | 64 | #N/A | #N/A
2022-09-24 21:00 | 9 | 6 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 40 | 48 | 55 | 62 | 59 | 55 | 48 | 63 | #N/A | #N/A
2022-09-24 22:00 | 9 | 6 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 39 | 47 | 53 | 61 | 59 | 54 | 46 | 63 | #N/A | #N/A
2022-09-24 23:00 | 9 | 6 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 39 | 45 | 54 | 60 | 59 | 52 | 45 | 62 | #N/A | #N/A
2022-09-25 | 9 | 7 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 38 | 44 | 52 | 59 | 58 | 49 | 43 | 60 | #N/A | #N/A
2022-09-25 01:00 | 9 | 7 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 46 | 38 | 43 | 51 | 58 | 59 | 51 | 42 | 60 | #N/A | #N/A
2022-09-25 02:00 | 9 | 7 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 38 | 40 | 50 | 54 | 59 | 49 | 42 | 58 | #N/A | #N/A
2022-09-25 03:00 | 9 | 7 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 38 | 41 | 50 | 50 | 59 | 46 | 41 | 56 | #N/A | #N/A
2022-09-25 04:00 | 9 | 7 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 38 | 40 | 49 | 48 | 59 | 46 | 40 | 57 | #N/A | #N/A
2022-09-25 05:00 | 9 | 7 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 37 | 42 | 48 | 49 | 59 | 45 | 40 | 57 | #N/A | #N/A
2022-09-25 06:00 | 9 | 7 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 37 | 42 | 48 | 50 | 60 | 47 | 39 | 57 | #N/A | #N/A
2022-09-25 07:00 | 9 | 7 | 8 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 40 | 41 | 49 | 55 | 61 | 50 | 44 | 59 | #N/A | #N/A
2022-09-25 08:00 | 9 | 7 | 9 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 44 | 51 | 50 | 57 | 62 | 54 | 48 | 64 | #N/A | #N/A
2022-09-25 09:00 | 9 | 7 | 10 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 47 | 56 | 52 | 60 | 64 | 60 | 53 | 68 | #N/A | #N/A
2022-09-25 10:00 | 9 | 7 | 11 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 51 | 58 | 53 | 60 | 66 | 66 | 57 | 70 | #N/A | #N/A
2022-09-25 11:00 | 9 | 7 | 12 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 54 | 58 | 53 | 64 | 66 | 67 | 60 | 70 | #N/A | #N/A
2022-09-25 12:00 | 9 | 7 | 13 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 58 | 58 | 54 | 64 | 64 | 70 | 64 | 71 | #N/A | #N/A
2022-09-25 13:00 | 9 | 7 | 14 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 58 | 58 | 53 | 65 | 63 | 71 | 65 | 71 | #N/A | #N/A
2022-09-25 14:00 | 9 | 7 | 15 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 59 | 58 | 53 | 64 | 63 | 71 | 65 | 71 | #N/A | #N/A
2022-09-25 15:00 | 9 | 7 | 16 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 69 | 59 | 58 | 53 | 65 | 63 | 71 | 66 | 70 | #N/A | #N/A
2022-09-25 16:00 | 9 | 7 | 17 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 57 | 58 | 53 | 64 | 63 | 70 | 62 | 68 | #N/A | #N/A
2022-09-25 17:00 | 9 | 7 | 18 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 56 | 54 | 52 | 61 | 62 | 69 | 59 | 65 | #N/A | #N/A
2022-09-25 18:00 | 9 | 7 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 61 | 54 | 50 | 51 | 56 | 62 | 65 | 55 | 60 | #N/A | #N/A
2022-09-25 19:00 | 9 | 7 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 52 | 46 | 51 | 53 | 62 | 62 | 56 | 59 | #N/A | #N/A
2022-09-25 20:00 | 9 | 7 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 51 | 45 | 50 | 52 | 62 | 61 | 56 | 58 | #N/A | #N/A
2022-09-25 21:00 | 9 | 7 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 49 | 44 | 50 | 53 | 61 | 60 | 57 | 55 | #N/A | #N/A
2022-09-25 22:00 | 9 | 7 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 47 | 43 | 50 | 51 | 61 | 59 | 55 | 54 | #N/A | #N/A
2022-09-25 23:00 | 9 | 7 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 46 | 42 | 49 | 48 | 61 | 58 | 52 | 50 | #N/A | #N/A
2022-09-26 | 9 | 1 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 44 | 39 | 48 | 46 | 61 | 57 | 50 | 49 | #N/A | #N/A
2022-09-26 01:00 | 9 | 1 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 45 | 41 | 48 | 46 | 60 | 57 | 50 | 47 | #N/A | #N/A
2022-09-26 02:00 | 9 | 1 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 45 | 43 | 46 | 45 | 60 | 56 | 49 | 46 | #N/A | #N/A
2022-09-26 03:00 | 9 | 1 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 46 | 45 | 46 | 44 | 60 | 55 | 49 | 46 | #N/A | #N/A
2022-09-26 04:00 | 9 | 1 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 46 | 44 | 45 | 43 | 60 | 55 | 49 | 47 | #N/A | #N/A
2022-09-26 05:00 | 9 | 1 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 47 | 44 | 46 | 43 | 61 | 55 | 50 | 45 | #N/A | #N/A
2022-09-26 06:00 | 9 | 1 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 47 | 45 | 47 | 44 | 60 | 54 | 50 | 46 | #N/A | #N/A
2022-09-26 07:00 | 9 | 1 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 54 | 48 | 48 | 49 | 51 | 62 | 57 | 52 | 46 | #N/A | #N/A
2022-09-26 08:00 | 9 | 1 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 50 | 52 | 54 | 54 | 64 | 62 | 54 | 49 | #N/A | #N/A
2022-09-26 09:00 | 9 | 1 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 51 | 54 | 57 | 59 | 64 | 65 | 56 | 52 | #N/A | #N/A
2022-09-26 10:00 | 9 | 1 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 53 | 58 | 57 | 65 | 64 | 68 | 57 | 55 | #N/A | #N/A
2022-09-26 11:00 | 9 | 1 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 54 | 60 | 58 | 68 | 63 | 71 | 59 | 59 | #N/A | #N/A
2022-09-26 12:00 | 9 | 1 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 56 | 64 | 58 | 69 | 64 | 73 | 60 | 61 | #N/A | #N/A
2022-09-26 13:00 | 9 | 1 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 57 | 65 | 58 | 71 | 64 | 74 | 60 | 63 | #N/A | #N/A
2022-09-26 14:00 | 9 | 1 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 57 | 65 | 58 | 71 | 65 | 74 | 60 | 65 | #N/A | #N/A
2022-09-26 15:00 | 9 | 1 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 58 | 65 | 57 | 72 | 64 | 74 | 60 | 65 | #N/A | #N/A
2022-09-26 16:00 | 9 | 1 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 58 | 64 | 57 | 71 | 64 | 74 | 61 | 65 | #N/A | #N/A
2022-09-26 17:00 | 9 | 1 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 59 | 57 | 56 | 64 | 64 | 71 | 62 | 60 | #N/A | #N/A
2022-09-26 18:00 | 9 | 1 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 59 | 50 | 52 | 59 | 64 | 67 | 63 | 56 | #N/A | #N/A
2022-09-26 19:00 | 9 | 1 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 59 | 47 | 50 | 57 | 63 | 62 | 63 | 51 | #N/A | #N/A
2022-09-26 20:00 | 9 | 1 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 46 | 50 | 55 | 62 | 58 | 62 | 51 | #N/A | #N/A
2022-09-26 21:00 | 9 | 1 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 44 | 50 | 54 | 61 | 56 | 62 | 51 | #N/A | #N/A
2022-09-26 22:00 | 9 | 1 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 43 | 48 | 55 | 59 | 55 | 62 | 49 | #N/A | #N/A
2022-09-26 23:00 | 9 | 1 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 42 | 49 | 55 | 58 | 53 | 63 | 48 | #N/A | #N/A
2022-09-27 | 9 | 2 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 41 | 50 | 55 | 56 | 51 | 63 | 45 | #N/A | #N/A
2022-09-27 01:00 | 9 | 2 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 60 | 42 | 51 | 54 | 55 | 53 | 63 | 47 | #N/A | #N/A
2022-09-27 02:00 | 9 | 2 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 40 | 51 | 53 | 58 | 51 | 63 | 46 | #N/A | #N/A
2022-09-27 03:00 | 9 | 2 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 59 | 41 | 50 | 51 | 58 | 53 | 63 | 46 | #N/A | #N/A
2022-09-27 04:00 | 9 | 2 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 58 | 40 | 50 | 49 | 56 | 50 | 63 | 46 | #N/A | #N/A
2022-09-27 05:00 | 9 | 2 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 57 | 43 | 50 | 49 | 56 | 51 | 62 | 45 | #N/A | #N/A
2022-09-27 06:00 | 9 | 2 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 66 | 56 | 44 | 50 | 50 | 56 | 51 | 62 | 45 | #N/A | #N/A
2022-09-27 07:00 | 9 | 2 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 67 | 56 | 53 | 55 | 57 | 57 | 55 | 62 | 48 | #N/A | #N/A
2022-09-27 08:00 | 9 | 2 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 56 | 58 | 58 | 63 | 58 | 60 | 63 | 54 | #N/A | #N/A
2022-09-27 09:00 | 9 | 2 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 56 | 61 | 62 | 67 | 65 | 66 | 63 | 57 | #N/A | #N/A
2022-09-27 10:00 | 9 | 2 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 56 | 65 | 65 | 71 | 69 | 69 | 63 | 61 | #N/A | #N/A
2022-09-27 11:00 | 9 | 2 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 57 | 68 | 68 | 74 | 71 | 73 | 63 | 65 | #N/A | #N/A
2022-09-27 12:00 | 9 | 2 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 72 | 57 | 70 | 67 | 75 | 74 | 74 | 63 | 67 | #N/A | #N/A
2022-09-27 13:00 | 9 | 2 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 71 | 56 | 72 | 68 | 77 | 75 | 75 | 63 | 70 | #N/A | #N/A
2022-09-27 14:00 | 9 | 2 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 70 | 56 | 72 | 67 | 78 | 76 | 74 | 64 | 71 | #N/A | #N/A
2022-09-27 15:00 | 9 | 2 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 55 | 72 | 67 | 78 | 75 | 72 | 64 | 70 | #N/A | #N/A
2022-09-27 16:00 | 9 | 2 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 69 | 54 | 67 | 66 | 76 | 74 | 70 | 63 | 70 | #N/A | #N/A
2022-09-27 17:00 | 9 | 2 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 68 | 54 | 65 | 64 | 72 | 70 | 68 | 63 | 69 | #N/A | #N/A
2022-09-27 18:00 | 9 | 2 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 53 | 63 | 61 | 71 | 69 | 67 | 62 | 68 | #N/A | #N/A
2022-09-27 19:00 | 9 | 2 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 68 | 52 | 63 | 60 | 65 | 67 | 65 | 61 | 65 | #N/A | #N/A
2022-09-27 20:00 | 9 | 2 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 52 | 62 | 62 | 61 | 64 | 65 | 59 | 64 | #N/A | #N/A
2022-09-27 21:00 | 9 | 2 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 67 | 51 | 57 | 59 | 61 | 63 | 64 | 58 | 63 | #N/A | #N/A
2022-09-27 22:00 | 9 | 2 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 64 | 50 | 54 | 58 | 59 | 63 | 62 | 57 | 62 | #N/A | #N/A
2022-09-27 23:00 | 9 | 2 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 62 | 49 | 54 | 54 | 57 | 62 | 61 | 56 | 61 | #N/A | #N/A
2022-09-28 | 9 | 3 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 59 | 48 | 56 | 54 | 56 | 62 | 61 | 55 | 60 | #N/A | #N/A
2022-09-28 01:00 | 9 | 3 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 48 | 57 | 51 | 56 | 60 | 61 | 54 | 60 | #N/A | #N/A
2022-09-28 02:00 | 9 | 3 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 47 | 53 | 51 | 54 | 60 | 60 | 53 | 60 | #N/A | #N/A
2022-09-28 03:00 | 9 | 3 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 47 | 50 | 50 | 54 | 59 | 59 | 52 | 59 | #N/A | #N/A
2022-09-28 04:00 | 9 | 3 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 53 | 48 | 49 | 49 | 53 | 60 | 59 | 52 | 58 | #N/A | #N/A
2022-09-28 05:00 | 9 | 3 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 48 | 51 | 49 | 52 | 60 | 59 | 51 | 58 | #N/A | #N/A
2022-09-28 06:00 | 9 | 3 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 49 | 54 | 49 | 53 | 62 | 59 | 51 | 60 | #N/A | #N/A
2022-09-28 07:00 | 9 | 3 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 49 | 55 | 49 | 58 | 66 | 60 | 52 | 63 | #N/A | #N/A
2022-09-28 08:00 | 9 | 3 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 48 | 57 | 50 | 64 | 69 | 60 | 54 | 62 | #N/A | #N/A
2022-09-28 09:00 | 9 | 3 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 48 | 60 | 51 | 69 | 70 | 61 | 55 | 62 | #N/A | #N/A
2022-09-28 10:00 | 9 | 3 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 48 | 58 | 51 | 72 | 74 | 61 | 55 | 63 | #N/A | #N/A
2022-09-28 11:00 | 9 | 3 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 48 | 58 | 50 | 75 | 75 | 62 | 56 | 64 | #N/A | #N/A
2022-09-28 12:00 | 9 | 3 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 48 | 57 | 51 | 80 | 76 | 63 | 56 | 66 | #N/A | #N/A
2022-09-28 13:00 | 9 | 3 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 49 | 54 | 50 | 81 | 77 | 64 | 55 | 66 | #N/A | #N/A
2022-09-28 14:00 | 9 | 3 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 49 | 59 | 51 | 81 | 79 | 64 | 55 | 67 | #N/A | #N/A
2022-09-28 15:00 | 9 | 3 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 50 | 56 | 49 | 80 | 76 | 64 | 54 | 66 | #N/A | #N/A
2022-09-28 16:00 | 9 | 3 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 47 | 54 | 49 | 78 | 74 | 65 | 52 | 65 | #N/A | #N/A
2022-09-28 17:00 | 9 | 3 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 45 | 49 | 47 | 75 | 72 | 65 | 51 | 60 | #N/A | #N/A
2022-09-28 18:00 | 9 | 3 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 42 | 45 | 44 | 69 | 69 | 65 | 49 | 56 | #N/A | #N/A
2022-09-28 19:00 | 9 | 3 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 42 | 43 | 41 | 73 | 64 | 65 | 47 | 53 | #N/A | #N/A
2022-09-28 20:00 | 9 | 3 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 42 | 41 | 39 | 72 | 62 | 65 | 46 | 49 | #N/A | #N/A
2022-09-28 21:00 | 9 | 3 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 47 | 42 | 40 | 40 | 69 | 60 | 65 | 44 | 46 | #N/A | #N/A
2022-09-28 22:00 | 9 | 3 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 45 | 40 | 39 | 39 | 62 | 61 | 65 | 43 | 45 | #N/A | #N/A
2022-09-28 23:00 | 9 | 3 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 44 | 39 | 37 | 39 | 61 | 58 | 65 | 42 | 43 | #N/A | #N/A
2022-09-29 | 9 | 4 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 37 | 36 | 38 | 58 | 59 | 64 | 41 | 43 | #N/A | #N/A
2022-09-29 01:00 | 9 | 4 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 42 | 37 | 36 | 38 | 58 | 59 | 65 | 40 | 42 | #N/A | #N/A
2022-09-29 02:00 | 9 | 4 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 41 | 36 | 35 | 38 | 57 | 57 | 64 | 39 | 41 | #N/A | #N/A
2022-09-29 03:00 | 9 | 4 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 41 | 36 | 35 | 37 | 57 | 57 | 64 | 38 | 40 | #N/A | #N/A
2022-09-29 04:00 | 9 | 4 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 41 | 37 | 33 | 38 | 56 | 56 | 64 | 38 | 40 | #N/A | #N/A
2022-09-29 05:00 | 9 | 4 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 41 | 37 | 36 | 38 | 55 | 56 | 64 | 38 | 40 | #N/A | #N/A
2022-09-29 06:00 | 9 | 4 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 41 | 38 | 40 | 39 | 56 | 58 | 64 | 38 | 41 | #N/A | #N/A
2022-09-29 07:00 | 9 | 4 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 46 | 42 | 43 | 44 | 62 | 60 | 64 | 42 | 41 | #N/A | #N/A
2022-09-29 08:00 | 9 | 4 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 52 | 47 | 46 | 49 | 66 | 63 | 64 | 45 | 44 | #N/A | #N/A
2022-09-29 09:00 | 9 | 4 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 57 | 51 | 48 | 53 | 72 | 67 | 65 | 49 | 50 | #N/A | #N/A
2022-09-29 10:00 | 9 | 4 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 59 | 53 | 48 | 57 | 75 | 69 | 65 | 53 | 54 | #N/A | #N/A
2022-09-29 11:00 | 9 | 4 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 62 | 56 | 53 | 60 | 77 | 70 | 65 | 56 | 59 | #N/A | #N/A
2022-09-29 12:00 | 9 | 4 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 64 | 58 | 56 | 59 | 78 | 71 | 65 | 60 | 62 | #N/A | #N/A
2022-09-29 13:00 | 9 | 4 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 59 | 59 | 60 | 77 | 72 | 65 | 61 | 64 | #N/A | #N/A
2022-09-29 14:00 | 9 | 4 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 65 | 59 | 60 | 60 | 77 | 71 | 65 | 62 | 64 | #N/A | #N/A
2022-09-29 15:00 | 9 | 4 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 66 | 60 | 60 | 60 | 77 | 70 | 66 | 63 | 65 | #N/A | #N/A
2022-09-29 16:00 | 9 | 4 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 63 | 58 | 58 | 59 | 75 | 67 | 66 | 61 | 65 | #N/A | #N/A
2022-09-29 17:00 | 9 | 4 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 60 | 56 | 55 | 56 | 73 | 63 | 65 | 58 | 58 | #N/A | #N/A
2022-09-29 18:00 | 9 | 4 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 57 | 54 | 52 | 52 | 71 | 60 | 64 | 56 | 53 | #N/A | #N/A
2022-09-29 19:00 | 9 | 4 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 52 | 50 | 51 | 69 | 59 | 63 | 54 | 52 | #N/A | #N/A
2022-09-29 20:00 | 9 | 4 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 54 | 50 | 49 | 50 | 68 | 58 | 63 | 53 | 49 | #N/A | #N/A
2022-09-29 21:00 | 9 | 4 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 52 | 48 | 48 | 50 | 68 | 57 | 63 | 51 | 48 | #N/A | #N/A
2022-09-29 22:00 | 9 | 4 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 47 | 48 | 50 | 66 | 57 | 63 | 50 | 46 | #N/A | #N/A
2022-09-29 23:00 | 9 | 4 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 47 | 48 | 52 | 65 | 57 | 62 | 49 | 46 | #N/A | #N/A
2022-09-30 | 9 | 5 | 1 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 46 | 48 | 52 | 64 | 56 | 62 | 48 | 45 | #N/A | #N/A
2022-09-30 01:00 | 9 | 5 | 2 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 48 | 46 | 48 | 52 | 63 | 55 | 63 | 47 | 45 | #N/A | #N/A
2022-09-30 02:00 | 9 | 5 | 3 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 47 | 48 | 51 | 63 | 54 | 62 | 46 | 50 | #N/A | #N/A
2022-09-30 03:00 | 9 | 5 | 4 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 49 | 47 | 47 | 50 | 62 | 53 | 61 | 45 | 51 | #N/A | #N/A
2022-09-30 04:00 | 9 | 5 | 5 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 47 | 47 | 49 | 62 | 53 | 60 | 45 | 52 | #N/A | #N/A
2022-09-30 05:00 | 9 | 5 | 6 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 50 | 46 | 47 | 49 | 62 | 53 | 60 | 46 | 53 | #N/A | #N/A
2022-09-30 06:00 | 9 | 5 | 7 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 51 | 46 | 47 | 50 | 62 | 56 | 60 | 46 | 55 | #N/A | #N/A
2022-09-30 07:00 | 9 | 5 | 8 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 53 | 48 | 49 | 52 | 63 | 59 | 61 | 47 | 56 | #N/A | #N/A
2022-09-30 08:00 | 9 | 5 | 9 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 54 | 50 | 52 | 59 | 65 | 62 | 62 | 48 | 57 | #N/A | #N/A
2022-09-30 09:00 | 9 | 5 | 10 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 52 | 59 | 62 | 68 | 66 | 62 | 49 | 60 | #N/A | #N/A
2022-09-30 10:00 | 9 | 5 | 11 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 54 | 64 | 65 | 70 | 68 | 63 | 49 | 63 | #N/A | #N/A
2022-09-30 11:00 | 9 | 5 | 12 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 56 | 68 | 67 | 68 | 69 | 66 | 50 | 65 | #N/A | #N/A
2022-09-30 12:00 | 9 | 5 | 13 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 58 | 71 | 68 | 68 | 70 | 67 | 50 | 66 | #N/A | #N/A
2022-09-30 13:00 | 9 | 5 | 14 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 56 | 57 | 71 | 70 | 69 | 72 | 69 | 51 | 68 | #N/A | #N/A
2022-09-30 14:00 | 9 | 5 | 15 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 57 | 72 | 71 | 70 | 73 | 71 | 52 | 70 | #N/A | #N/A
2022-09-30 15:00 | 9 | 5 | 16 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 56 | 70 | 66 | 68 | 71 | 70 | 53 | 68 | #N/A | #N/A
2022-09-30 16:00 | 9 | 5 | 17 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 55 | 69 | 63 | 68 | 69 | 70 | 53 | 67 | #N/A | #N/A
2022-09-30 17:00 | 9 | 5 | 18 | 0 | #N/A | Cooling | 72 | 77 | #N/A | #N/A | 0 | 0 | 55 | 53 | 67 | 61 | 65 | 63 | 69 | 53 | 66 | #N/A | #N/A
2022-09-30 18:00 | 9 | 5 | 19 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 52 | 64 | 57 | 62 | 63 | 65 | 53 | 65 | #N/A | #N/A
2022-09-30 19:00 | 9 | 5 | 20 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 52 | 63 | 57 | 58 | 60 | 64 | 53 | 62 | #N/A | #N/A
2022-09-30 20:00 | 9 | 5 | 21 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 56 | 51 | 63 | 56 | 57 | 56 | 62 | 52 | 59 | #N/A | #N/A
2022-09-30 21:00 | 9 | 5 | 22 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 54 | 60 | 56 | 59 | 57 | 61 | 53 | 60 | #N/A | #N/A
2022-09-30 22:00 | 9 | 5 | 23 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 56 | 57 | 56 | 61 | 57 | 60 | 53 | 60 | #N/A | #N/A
2022-09-30 23:00 | 9 | 5 | 24 | 0 | #N/A | Cooling | 78 | 80 | #N/A | #N/A | 0 | 0 | 55 | 58 | 54 | 56 | 63 | 58 | 59 | 53 | 61 | #N/A | #N/A
2022-10-01 | 10 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 60 | 51 | 56 | 65 | 59 | 58 | 53 | 62 | 0 | 0
2022-10-01 01:00 | 10 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 62 | 48 | 56 | 67 | 60 | 57 | 53 | 63 | 0 | 0
2022-10-01 02:00 | 10 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 65 | 45 | 56 | 69 | 60 | 56 | 54 | 63 | 0 | 0
2022-10-01 03:00 | 10 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 67 | 42 | 56 | 71 | 61 | 55 | 54 | 64 | 0 | 0
2022-10-01 04:00 | 10 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 65 | 43 | 56 | 72 | 62 | 57 | 52 | 64 | 0 | 0
2022-10-01 05:00 | 10 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 62 | 42 | 56 | 72 | 60 | 54 | 55 | 63 | 0 | 0
2022-10-01 06:00 | 10 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 61 | 42 | 56 | 71 | 63 | 53 | 54 | 63 | 0 | 0
2022-10-01 07:00 | 10 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 59 | 43 | 57 | 73 | 67 | 56 | 59 | 64 | 0 | 0
2022-10-01 08:00 | 10 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 59 | 46 | 57 | 78 | 69 | 62 | 61 | 64 | 0 | 0
2022-10-01 09:00 | 10 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 72 | 62 | 46 | 58 | 80 | 72 | 69 | 67 | 65 | 0 | 0
2022-10-01 10:00 | 10 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 74 | 64 | 49 | 59 | 81 | 74 | 71 | 69 | 66 | 0 | 0
2022-10-01 11:00 | 10 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 76 | 66 | 48 | 59 | 82 | 76 | 72 | 72 | 66 | 0 | 0
2022-10-01 12:00 | 10 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 78 | 66 | 49 | 60 | 82 | 77 | 71 | 75 | 68 | 0 | 0
2022-10-01 13:00 | 10 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 80 | 66 | 53 | 59 | 84 | 77 | 71 | 75 | 68 | 0 | 0
2022-10-01 14:00 | 10 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 78 | 65 | 51 | 58 | 81 | 75 | 69 | 74 | 68 | 0 | 0
2022-10-01 15:00 | 10 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 78 | 64 | 52 | 57 | 81 | 75 | 70 | 72 | 68 | 0 | 0
2022-10-01 16:00 | 10 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 77 | 62 | 51 | 57 | 77 | 71 | 68 | 71 | 68 | 0 | 0
2022-10-01 17:00 | 10 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 74 | 62 | 48 | 56 | 71 | 68 | 66 | 69 | 66 | 0 | 0
2022-10-01 18:00 | 10 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 72 | 61 | 43 | 56 | 69 | 65 | 63 | 68 | 62 | 0 | 0
2022-10-01 19:00 | 10 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 69 | 61 | 43 | 56 | 68 | 63 | 60 | 66 | 62 | 0 | 0
2022-10-01 20:00 | 10 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 59 | 44 | 55 | 68 | 63 | 58 | 66 | 62 | 0 | 0
2022-10-01 21:00 | 10 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 58 | 44 | 55 | 69 | 61 | 53 | 64 | 60 | 0 | 0
2022-10-01 22:00 | 10 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 58 | 43 | 55 | 69 | 61 | 53 | 63 | 58 | 0 | 0
2022-10-01 23:00 | 10 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 58 | 43 | 54 | 68 | 60 | 47 | 62 | 57 | 0 | 0
2022-10-02 | 10 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 58 | 44 | 54 | 68 | 62 | 47 | 61 | 55 | 0 | 0
2022-10-02 01:00 | 10 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 58 | 44 | 54 | 68 | 62 | 49 | 59 | 54 | 0 | 0
2022-10-02 02:00 | 10 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 59 | 43 | 54 | 66 | 63 | 49 | 58 | 54 | 0 | 0
2022-10-02 03:00 | 10 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 59 | 43 | 54 | 65 | 63 | 48 | 57 | 54 | 0 | 0
2022-10-02 04:00 | 10 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 58 | 45 | 54 | 65 | 63 | 46 | 55 | 53 | 0 | 0
2022-10-02 05:00 | 10 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 58 | 46 | 54 | 65 | 63 | 44 | 54 | 52 | 0 | 0
2022-10-02 06:00 | 10 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 58 | 46 | 54 | 63 | 63 | 44 | 54 | 53 | 0 | 0
2022-10-02 07:00 | 10 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 59 | 50 | 55 | 67 | 63 | 43 | 54 | 54 | 0 | 0
2022-10-02 08:00 | 10 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 62 | 54 | 55 | 73 | 65 | 42 | 53 | 55 | 0 | 0
2022-10-02 09:00 | 10 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 62 | 55 | 56 | 78 | 68 | 42 | 54 | 56 | 0 | 0
2022-10-02 10:00 | 10 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 64 | 57 | 57 | 80 | 69 | 42 | 52 | 59 | 0 | 0
2022-10-02 11:00 | 10 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 71 | 64 | 50 | 58 | 81 | 69 | 44 | 53 | 60 | 0 | 0
2022-10-02 12:00 | 10 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 73 | 63 | 49 | 59 | 83 | 73 | 42 | 53 | 60 | 0 | 0
2022-10-02 13:00 | 10 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 76 | 64 | 49 | 59 | 84 | 76 | 42 | 54 | 60 | 0 | 0
2022-10-02 14:00 | 10 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 76 | 62 | 49 | 59 | 82 | 77 | 42 | 53 | 61 | 0 | 0
2022-10-02 15:00 | 10 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 61 | 48 | 59 | 82 | 76 | 42 | 53 | 61 | 0 | 0
2022-10-02 16:00 | 10 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 61 | 46 | 56 | 79 | 75 | 42 | 53 | 60 | 0 | 0
2022-10-02 17:00 | 10 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 59 | 47 | 52 | 76 | 71 | 42 | 53 | 59 | 0 | 0
2022-10-02 18:00 | 10 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 58 | 46 | 49 | 72 | 62 | 41 | 53 | 57 | 0 | 0
2022-10-02 19:00 | 10 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 57 | 45 | 47 | 73 | 59 | 41 | 53 | 51 | 0 | 0
2022-10-02 20:00 | 10 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 56 | 45 | 46 | 73 | 60 | 42 | 53 | 49 | 0 | 0
2022-10-02 21:00 | 10 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 54 | 43 | 44 | 71 | 59 | 42 | 53 | 48 | 0 | 0
2022-10-02 22:00 | 10 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 54 | 43 | 45 | 68 | 59 | 42 | 53 | 48 | 0 | 0
2022-10-02 23:00 | 10 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 52 | 44 | 46 | 66 | 58 | 41 | 53 | 47 | 0 | 0
2022-10-03 | 10 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 52 | 44 | 47 | 64 | 58 | 42 | 53 | 61 | 0 | 0
2022-10-03 01:00 | 10 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 52 | 45 | 46 | 64 | 57 | 42 | 52 | 46 | 0 | 0
2022-10-03 02:00 | 10 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 52 | 43 | 46 | 63 | 57 | 42 | 51 | 46 | 0 | 0
2022-10-03 03:00 | 10 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 52 | 41 | 45 | 61 | 56 | 42 | 51 | 62 | 0 | 0
2022-10-03 04:00 | 10 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 50 | 40 | 45 | 61 | 57 | 42 | 51 | 45 | 0 | 0
2022-10-03 05:00 | 10 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 50 | 39 | 46 | 61 | 56 | 42 | 51 | 44 | 0 | 0
2022-10-03 06:00 | 10 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 51 | 36 | 46 | 62 | 56 | 42 | 51 | 44 | 0 | 0
2022-10-03 07:00 | 10 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 52 | 36 | 49 | 62 | 57 | 43 | 50 | 44 | 0 | 0
2022-10-03 08:00 | 10 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 53 | 38 | 53 | 62 | 60 | 44 | 50 | 45 | 0 | 0
2022-10-03 09:00 | 10 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 53 | 38 | 56 | 62 | 59 | 45 | 50 | 46 | 0 | 0
2022-10-03 10:00 | 10 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 55 | 40 | 58 | 63 | 61 | 45 | 51 | 49 | 0 | 0
2022-10-03 11:00 | 10 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 55 | 39 | 61 | 61 | 61 | 46 | 54 | 54 | 0 | 0
2022-10-03 12:00 | 10 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 57 | 39 | 63 | 62 | 61 | 46 | 56 | 64 | 0 | 0
2022-10-03 13:00 | 10 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 56 | 39 | 63 | 63 | 61 | 49 | 56 | 62 | 0 | 0
2022-10-03 14:00 | 10 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 57 | 38 | 62 | 64 | 61 | 48 | 56 | 65 | 0 | 0
2022-10-03 15:00 | 10 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 59 | 38 | 62 | 64 | 58 | 47 | 55 | 60 | 0 | 0
2022-10-03 16:00 | 10 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 60 | 37 | 62 | 63 | 58 | 46 | 55 | 64 | 0 | 0
2022-10-03 17:00 | 10 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 61 | 36 | 61 | 64 | 56 | 46 | 54 | 62 | 0 | 0
2022-10-03 18:00 | 10 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 62 | 36 | 61 | 64 | 56 | 43 | 55 | 58 | 0 | 0
2022-10-03 19:00 | 10 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 63 | 36 | 60 | 64 | 55 | 42 | 55 | 61 | 0 | 0
2022-10-03 20:00 | 10 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 63 | 36 | 58 | 63 | 55 | 40 | 55 | 60 | 0 | 0
2022-10-03 21:00 | 10 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 63 | 34 | 57 | 63 | 56 | 37 | 55 | 60 | 0 | 0
2022-10-03 22:00 | 10 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 65 | 34 | 55 | 64 | 55 | 37 | 55 | 60 | 0 | 0
2022-10-03 23:00 | 10 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 65 | 33 | 54 | 65 | 54 | 36 | 55 | 60 | 0 | 0
2022-10-04 | 10 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 65 | 32 | 52 | 67 | 53 | 35 | 55 | 47 | 0 | 0
2022-10-04 01:00 | 10 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 65 | 32 | 52 | 69 | 51 | 34 | 55 | 62 | 0 | 0
2022-10-04 02:00 | 10 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 65 | 32 | 51 | 69 | 50 | 34 | 54 | 61 | 0 | 0
2022-10-04 03:00 | 10 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 65 | 32 | 51 | 69 | 52 | 34 | 55 | 45 | 0 | 0
2022-10-04 04:00 | 10 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 64 | 32 | 51 | 69 | 53 | 33 | 55 | 62 | 0 | 0
2022-10-04 05:00 | 10 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 64 | 32 | 50 | 71 | 52 | 33 | 55 | 60 | 0 | 0
2022-10-04 06:00 | 10 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 62 | 32 | 50 | 70 | 51 | 34 | 55 | 59 | 0 | 0
2022-10-04 07:00 | 10 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 62 | 33 | 53 | 71 | 56 | 35 | 57 | 60 | 0 | 0
2022-10-04 08:00 | 10 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 61 | 38 | 55 | 73 | 57 | 43 | 59 | 60 | 0 | 0
2022-10-04 09:00 | 10 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 61 | 41 | 58 | 75 | 60 | 46 | 60 | 60 | 0 | 0
2022-10-04 10:00 | 10 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 63 | 44 | 58 | 76 | 62 | 49 | 61 | 62 | 0 | 0
2022-10-04 11:00 | 10 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 65 | 45 | 58 | 76 | 62 | 50 | 61 | 65 | 0 | 0
2022-10-04 12:00 | 10 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 63 | 46 | 58 | 78 | 64 | 54 | 63 | 61 | 0 | 0
2022-10-04 13:00 | 10 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 62 | 48 | 56 | 74 | 64 | 56 | 63 | 66 | 0 | 0
2022-10-04 14:00 | 10 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 62 | 51 | 54 | 75 | 62 | 59 | 63 | 65 | 0 | 0
2022-10-04 15:00 | 10 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 63 | 50 | 52 | 77 | 62 | 57 | 64 | 65 | 0 | 0
2022-10-04 16:00 | 10 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 64 | 49 | 52 | 76 | 61 | 56 | 63 | 62 | 0 | 0
2022-10-04 17:00 | 10 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 66 | 45 | 53 | 76 | 57 | 55 | 62 | 59 | 0 | 0
2022-10-04 18:00 | 10 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 64 | 42 | 53 | 77 | 54 | 54 | 61 | 62 | 0 | 0
2022-10-04 19:00 | 10 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 59 | 41 | 52 | 75 | 53 | 54 | 62 | 55 | 0 | 0
2022-10-04 20:00 | 10 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 57 | 40 | 50 | 74 | 51 | 54 | 61 | 55 | 0 | 0
2022-10-04 21:00 | 10 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 55 | 39 | 49 | 72 | 50 | 54 | 60 | 55 | 0 | 0
2022-10-04 22:00 | 10 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 54 | 39 | 49 | 68 | 50 | 54 | 59 | 55 | 0 | 0
2022-10-04 23:00 | 10 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 52 | 39 | 48 | 69 | 51 | 53 | 62 | 55 | 0 | 0
2022-10-05 | 10 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 51 | 40 | 48 | 69 | 51 | 56 | 63 | 55 | 0 | 0
2022-10-05 01:00 | 10 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 50 | 38 | 47 | 68 | 51 | 57 | 63 | 55 | 0 | 0
2022-10-05 02:00 | 10 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 50 | 37 | 47 | 66 | 51 | 57 | 64 | 54 | 0 | 0
2022-10-05 03:00 | 10 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 50 | 37 | 46 | 63 | 50 | 58 | 65 | 54 | 0 | 0
2022-10-05 04:00 | 10 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 49 | 37 | 46 | 60 | 49 | 58 | 64 | 54 | 0 | 0
2022-10-05 05:00 | 10 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 49 | 37 | 47 | 60 | 49 | 58 | 62 | 54 | 0 | 0
2022-10-05 06:00 | 10 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 49 | 37 | 47 | 59 | 50 | 57 | 62 | 54 | 0 | 0
2022-10-05 07:00 | 10 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 49 | 40 | 50 | 63 | 51 | 59 | 56 | 54 | 0 | 0
2022-10-05 08:00 | 10 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 50 | 45 | 53 | 65 | 53 | 61 | 56 | 56 | 0 | 0
2022-10-05 09:00 | 10 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 53 | 53 | 56 | 68 | 55 | 65 | 56 | 57 | 0 | 0
2022-10-05 10:00 | 10 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 53 | 56 | 59 | 69 | 58 | 68 | 56 | 58 | 0 | 0
2022-10-05 11:00 | 10 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 53 | 60 | 61 | 68 | 60 | 70 | 54 | 63 | 0 | 0
2022-10-05 12:00 | 10 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 54 | 62 | 64 | 70 | 61 | 73 | 54 | 64 | 0 | 0
2022-10-05 13:00 | 10 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 54 | 63 | 64 | 70 | 62 | 73 | 56 | 64 | 0 | 0
2022-10-05 14:00 | 10 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 54 | 62 | 64 | 70 | 63 | 74 | 60 | 64 | 0 | 0
2022-10-05 15:00 | 10 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 55 | 63 | 64 | 68 | 63 | 73 | 60 | 65 | 0 | 0
2022-10-05 16:00 | 10 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 55 | 60 | 62 | 66 | 61 | 72 | 59 | 64 | 0 | 0
2022-10-05 17:00 | 10 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 52 | 58 | 61 | 63 | 57 | 68 | 56 | 64 | 0 | 0
2022-10-05 18:00 | 10 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 50 | 54 | 59 | 60 | 54 | 66 | 56 | 63 | 0 | 0
2022-10-05 19:00 | 10 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 49 | 52 | 56 | 57 | 55 | 63 | 55 | 62 | 0 | 0
2022-10-05 20:00 | 10 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 49 | 51 | 52 | 56 | 54 | 62 | 54 | 61 | 0 | 0
2022-10-05 21:00 | 10 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 49 | 51 | 49 | 57 | 55 | 61 | 52 | 64 | 0 | 0
2022-10-05 22:00 | 10 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 50 | 49 | 48 | 56 | 54 | 60 | 51 | 65 | 0 | 0
2022-10-05 23:00 | 10 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 50 | 48 | 48 | 57 | 53 | 59 | 50 | 65 | 0 | 0
2022-10-06 | 10 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 50 | 48 | 47 | 55 | 52 | 59 | 49 | 65 | 0 | 0
2022-10-06 01:00 | 10 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 48 | 51 | 47 | 58 | 52 | 59 | 48 | 64 | 0 | 0
2022-10-06 02:00 | 10 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 47 | 49 | 46 | 59 | 50 | 61 | 48 | 60 | 0 | 0
2022-10-06 03:00 | 10 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 46 | 48 | 46 | 56 | 50 | 62 | 48 | 58 | 0 | 0
2022-10-06 04:00 | 10 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 45 | 49 | 46 | 55 | 48 | 62 | 48 | 57 | 0 | 0
2022-10-06 05:00 | 10 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 43 | 47 | 46 | 52 | 48 | 63 | 49 | 56 | 0 | 0
2022-10-06 06:00 | 10 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 43 | 48 | 46 | 51 | 48 | 63 | 48 | 55 | 0 | 0
2022-10-06 07:00 | 10 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 44 | 51 | 48 | 53 | 51 | 64 | 49 | 57 | 0 | 0
2022-10-06 08:00 | 10 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 46 | 54 | 49 | 54 | 55 | 64 | 50 | 59 | 0 | 0
2022-10-06 09:00 | 10 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 42 | 57 | 51 | 54 | 59 | 65 | 51 | 61 | 0 | 0
2022-10-06 10:00 | 10 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 45 | 60 | 51 | 57 | 61 | 66 | 54 | 63 | 0 | 0
2022-10-06 11:00 | 10 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 46 | 60 | 51 | 58 | 63 | 67 | 55 | 62 | 0 | 0
2022-10-06 12:00 | 10 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 45 | 55 | 51 | 58 | 63 | 66 | 55 | 63 | 0 | 0
2022-10-06 13:00 | 10 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 47 | 53 | 50 | 59 | 64 | 69 | 57 | 63 | 0 | 0
2022-10-06 14:00 | 10 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 46 | 52 | 49 | 60 | 63 | 65 | 55 | 62 | 0 | 0
2022-10-06 15:00 | 10 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 47 | 51 | 48 | 57 | 63 | 64 | 53 | 61 | 0 | 0
2022-10-06 16:00 | 10 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 43 | 49 | 49 | 57 | 60 | 60 | 53 | 59 | 0 | 0
2022-10-06 17:00 | 10 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 41 | 48 | 50 | 54 | 56 | 56 | 52 | 58 | 0 | 0
2022-10-06 18:00 | 10 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 42 | 48 | 51 | 51 | 54 | 55 | 49 | 58 | 0 | 0
2022-10-06 19:00 | 10 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 42 | 48 | 50 | 51 | 51 | 54 | 49 | 58 | 0 | 0
2022-10-06 20:00 | 10 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 40 | 49 | 49 | 50 | 49 | 54 | 49 | 58 | 0 | 0
2022-10-06 21:00 | 10 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 38 | 49 | 48 | 49 | 49 | 53 | 48 | 58 | 0 | 0
2022-10-06 22:00 | 10 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 38 | 49 | 48 | 48 | 48 | 52 | 46 | 57 | 0 | 0
2022-10-06 23:00 | 10 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 37 | 48 | 48 | 47 | 47 | 51 | 44 | 57 | 0 | 0
2022-10-07 | 10 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 36 | 48 | 48 | 42 | 46 | 49 | 42 | 56 | 0 | 0
2022-10-07 01:00 | 10 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 35 | 47 | 48 | 39 | 46 | 48 | 42 | 55 | 0 | 0
2022-10-07 02:00 | 10 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 37 | 47 | 47 | 42 | 49 | 46 | 42 | 55 | 0 | 0
2022-10-07 03:00 | 10 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 37 | 46 | 47 | 40 | 50 | 45 | 40 | 55 | 0 | 0
2022-10-07 04:00 | 10 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 37 | 46 | 46 | 40 | 49 | 44 | 40 | 55 | 0 | 0
2022-10-07 05:00 | 10 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 38 | 46 | 46 | 40 | 50 | 43 | 38 | 53 | 0 | 0
2022-10-07 06:00 | 10 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 38 | 46 | 45 | 40 | 49 | 43 | 42 | 53 | 0 | 0
2022-10-07 07:00 | 10 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 40 | 46 | 46 | 45 | 50 | 44 | 44 | 53 | 0 | 0
2022-10-07 08:00 | 10 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 43 | 43 | 48 | 48 | 56 | 44 | 48 | 55 | 0 | 0
2022-10-07 09:00 | 10 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 46 | 42 | 49 | 52 | 60 | 45 | 51 | 57 | 0 | 0
2022-10-07 10:00 | 10 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 48 | 42 | 49 | 54 | 62 | 45 | 53 | 56 | 0 | 0
2022-10-07 11:00 | 10 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 50 | 44 | 48 | 57 | 63 | 46 | 56 | 57 | 0 | 0
2022-10-07 12:00 | 10 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 53 | 45 | 48 | 58 | 62 | 47 | 58 | 56 | 0 | 0
2022-10-07 13:00 | 10 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 54 | 47 | 47 | 59 | 63 | 47 | 59 | 55 | 0 | 0
2022-10-07 14:00 | 10 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 55 | 47 | 47 | 60 | 64 | 47 | 59 | 54 | 0 | 0
2022-10-07 15:00 | 10 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 55 | 45 | 46 | 61 | 62 | 48 | 58 | 56 | 0 | 0
2022-10-07 16:00 | 10 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 54 | 41 | 46 | 59 | 61 | 48 | 58 | 55 | 0 | 0
2022-10-07 17:00 | 10 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 51 | 42 | 45 | 52 | 58 | 48 | 56 | 52 | 0 | 0
2022-10-07 18:00 | 10 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 50 | 40 | 45 | 48 | 56 | 48 | 51 | 52 | 0 | 0
2022-10-07 19:00 | 10 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 48 | 39 | 44 | 46 | 55 | 47 | 49 | 52 | 0 | 0
2022-10-07 20:00 | 10 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 48 | 38 | 44 | 46 | 53 | 47 | 47 | 50 | 0 | 0
2022-10-07 21:00 | 10 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 48 | 38 | 43 | 44 | 52 | 47 | 45 | 48 | 0 | 0
2022-10-07 22:00 | 10 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 46 | 39 | 43 | 43 | 52 | 47 | 44 | 48 | 0 | 0
2022-10-07 23:00 | 10 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 46 | 39 | 44 | 45 | 52 | 46 | 43 | 48 | 0 | 0
2022-10-08 | 10 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 46 | 38 | 44 | 41 | 51 | 46 | 42 | 46 | 0 | 0
2022-10-08 01:00 | 10 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 44 | 38 | 44 | 41 | 51 | 46 | 42 | 45 | 0 | 0
2022-10-08 02:00 | 10 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 44 | 40 | 44 | 42 | 50 | 46 | 41 | 45 | 0 | 0
2022-10-08 03:00 | 10 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 45 | 40 | 44 | 42 | 49 | 45 | 41 | 43 | 0 | 0
2022-10-08 04:00 | 10 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 43 | 40 | 43 | 39 | 50 | 45 | 40 | 44 | 0 | 0
2022-10-08 05:00 | 10 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 43 | 41 | 43 | 39 | 48 | 45 | 40 | 44 | 0 | 0
2022-10-08 06:00 | 10 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 45 | 40 | 42 | 40 | 48 | 44 | 42 | 44 | 0 | 0
2022-10-08 07:00 | 10 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 49 | 40 | 43 | 48 | 53 | 45 | 47 | 47 | 0 | 0
2022-10-08 08:00 | 10 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 52 | 40 | 44 | 53 | 57 | 46 | 53 | 49 | 0 | 0
2022-10-08 09:00 | 10 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 56 | 41 | 45 | 58 | 61 | 47 | 58 | 50 | 0 | 0
2022-10-08 10:00 | 10 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 60 | 41 | 45 | 64 | 66 | 45 | 64 | 40 | 0 | 0
2022-10-08 11:00 | 10 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 62 | 41 | 44 | 68 | 69 | 49 | 64 | 49 | 0 | 0
2022-10-08 12:00 | 10 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 71 | 65 | 42 | 44 | 70 | 71 | 48 | 65 | 48 | 0 | 0
2022-10-08 13:00 | 10 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 72 | 68 | 43 | 44 | 71 | 71 | 48 | 65 | 51 | 0 | 0
2022-10-08 14:00 | 10 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 73 | 67 | 38 | 45 | 71 | 72 | 49 | 67 | 52 | 0 | 0
2022-10-08 15:00 | 10 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 72 | 67 | 37 | 45 | 71 | 71 | 49 | 65 | 52 | 0 | 0
2022-10-08 16:00 | 10 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 64 | 37 | 45 | 70 | 68 | 49 | 62 | 50 | 0 | 0
2022-10-08 17:00 | 10 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 61 | 36 | 46 | 63 | 64 | 49 | 59 | 48 | 0 | 0
2022-10-08 18:00 | 10 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 61 | 36 | 46 | 60 | 63 | 47 | 58 | 47 | 0 | 0
2022-10-08 19:00 | 10 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 60 | 36 | 46 | 62 | 62 | 43 | 58 | 44 | 0 | 0
2022-10-08 20:00 | 10 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 58 | 35 | 46 | 64 | 58 | 42 | 56 | 43 | 0 | 0
2022-10-08 21:00 | 10 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 58 | 34 | 46 | 57 | 58 | 39 | 56 | 42 | 0 | 0
2022-10-08 22:00 | 10 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 56 | 34 | 45 | 56 | 58 | 38 | 55 | 43 | 0 | 0
2022-10-08 23:00 | 10 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 56 | 34 | 45 | 54 | 57 | 38 | 54 | 39 | 0 | 0
2022-10-09 | 10 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 56 | 34 | 44 | 53 | 56 | 37 | 55 | 39 | 0 | 0
2022-10-09 01:00 | 10 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 55 | 33 | 42 | 52 | 56 | 37 | 54 | 38 | 0 | 0
2022-10-09 02:00 | 10 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 55 | 31 | 40 | 51 | 55 | 36 | 53 | 37 | 0 | 0
2022-10-09 03:00 | 10 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 55 | 31 | 38 | 51 | 55 | 33 | 52 | 37 | 0 | 0
2022-10-09 04:00 | 10 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 54 | 32 | 39 | 50 | 55 | 33 | 53 | 38 | 0 | 0
2022-10-09 05:00 | 10 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 53 | 31 | 41 | 50 | 55 | 33 | 54 | 38 | 0 | 0
2022-10-09 06:00 | 10 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 53 | 33 | 42 | 50 | 56 | 34 | 54 | 39 | 0 | 0
2022-10-09 07:00 | 10 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 56 | 34 | 45 | 52 | 58 | 35 | 57 | 40 | 0 | 0
2022-10-09 08:00 | 10 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 57 | 38 | 47 | 58 | 63 | 40 | 59 | 41 | 0 | 0
2022-10-09 09:00 | 10 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 56 | 41 | 50 | 65 | 68 | 45 | 62 | 45 | 0 | 0
2022-10-09 10:00 | 10 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 52 | 47 | 52 | 71 | 66 | 50 | 65 | 52 | 0 | 0
2022-10-09 11:00 | 10 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 50 | 48 | 53 | 74 | 70 | 51 | 67 | 56 | 0 | 0
2022-10-09 12:00 | 10 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 69 | 49 | 53 | 55 | 74 | 71 | 54 | 69 | 57 | 0 | 0
2022-10-09 13:00 | 10 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 48 | 50 | 55 | 76 | 71 | 55 | 71 | 58 | 0 | 0
2022-10-09 14:00 | 10 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 72 | 46 | 50 | 55 | 76 | 71 | 55 | 72 | 60 | 0 | 0
2022-10-09 15:00 | 10 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 46 | 50 | 55 | 73 | 72 | 55 | 72 | 61 | 0 | 0
2022-10-09 16:00 | 10 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 44 | 50 | 52 | 70 | 68 | 55 | 69 | 58 | 0 | 0
2022-10-09 17:00 | 10 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 43 | 50 | 49 | 65 | 64 | 51 | 66 | 54 | 0 | 0
2022-10-09 18:00 | 10 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 42 | 50 | 46 | 60 | 63 | 50 | 62 | 47 | 0 | 0
2022-10-09 19:00 | 10 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 41 | 48 | 47 | 56 | 61 | 47 | 60 | 47 | 0 | 0
2022-10-09 20:00 | 10 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 40 | 47 | 49 | 53 | 59 | 46 | 60 | 44 | 0 | 0
2022-10-09 21:00 | 10 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 38 | 46 | 50 | 51 | 57 | 41 | 58 | 43 | 0 | 0
2022-10-09 22:00 | 10 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 37 | 47 | 50 | 49 | 55 | 45 | 57 | 41 | 0 | 0
2022-10-09 23:00 | 10 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 35 | 46 | 51 | 48 | 54 | 44 | 56 | 40 | 0 | 0
2022-10-10 | 10 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 34 | 46 | 51 | 47 | 52 | 42 | 54 | 40 | 0 | 0
2022-10-10 01:00 | 10 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 33 | 45 | 51 | 45 | 53 | 41 | 53 | 39 | 0 | 0
2022-10-10 02:00 | 10 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 32 | 45 | 50 | 43 | 51 | 40 | 53 | 40 | 0 | 0
2022-10-10 03:00 | 10 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 31 | 40 | 50 | 42 | 50 | 39 | 52 | 40 | 0 | 0
2022-10-10 04:00 | 10 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 30 | 40 | 49 | 41 | 49 | 39 | 50 | 40 | 0 | 0
2022-10-10 05:00 | 10 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 29 | 38 | 49 | 39 | 48 | 37 | 51 | 40 | 0 | 0
2022-10-10 06:00 | 10 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 30 | 37 | 48 | 38 | 48 | 38 | 51 | 41 | 0 | 0
2022-10-10 07:00 | 10 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 33 | 44 | 51 | 40 | 50 | 40 | 54 | 42 | 0 | 0
2022-10-10 08:00 | 10 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 35 | 45 | 54 | 43 | 53 | 44 | 57 | 45 | 0 | 0
2022-10-10 09:00 | 10 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 38 | 48 | 57 | 45 | 57 | 49 | 64 | 51 | 0 | 0
2022-10-10 10:00 | 10 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 42 | 47 | 59 | 49 | 61 | 52 | 66 | 55 | 0 | 0
2022-10-10 11:00 | 10 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 45 | 50 | 61 | 51 | 62 | 56 | 69 | 58 | 0 | 0
2022-10-10 12:00 | 10 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 46 | 48 | 63 | 53 | 61 | 57 | 71 | 66 | 0 | 0
2022-10-10 13:00 | 10 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 48 | 48 | 63 | 54 | 60 | 58 | 72 | 69 | 0 | 0
2022-10-10 14:00 | 10 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 48 | 49 | 62 | 55 | 59 | 58 | 71 | 70 | 0 | 0
2022-10-10 15:00 | 10 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 50 | 48 | 62 | 54 | 58 | 57 | 69 | 70 | 0 | 0
2022-10-10 16:00 | 10 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 47 | 47 | 58 | 53 | 57 | 57 | 68 | 67 | 0 | 0
2022-10-10 17:00 | 10 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 43 | 46 | 55 | 50 | 57 | 55 | 68 | 63 | 0 | 0
2022-10-10 18:00 | 10 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 41 | 43 | 51 | 46 | 57 | 53 | 68 | 58 | 0 | 0
2022-10-10 19:00 | 10 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 39 | 40 | 51 | 44 | 57 | 52 | 64 | 54 | 0 | 0
2022-10-10 20:00 | 10 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 38 | 40 | 52 | 39 | 57 | 51 | 63 | 53 | 0 | 0
2022-10-10 21:00 | 10 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 35 | 40 | 52 | 38 | 57 | 49 | 62 | 52 | 0 | 0
2022-10-10 22:00 | 10 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 35 | 39 | 51 | 37 | 57 | 47 | 54 | 50 | 0 | 0
2022-10-10 23:00 | 10 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 35 | 39 | 51 | 35 | 57 | 46 | 53 | 49 | 0 | 0
2022-10-11 | 10 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 33 | 39 | 50 | 33 | 59 | 45 | 52 | 47 | 0 | 0
2022-10-11 01:00 | 10 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 34 | 40 | 49 | 33 | 62 | 45 | 51 | 47 | 0 | 0
2022-10-11 02:00 | 10 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 32 | 39 | 48 | 33 | 64 | 44 | 50 | 48 | 0 | 0
2022-10-11 03:00 | 10 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 32 | 38 | 47 | 35 | 64 | 45 | 49 | 48 | 0 | 0
2022-10-11 04:00 | 10 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 32 | 35 | 47 | 35 | 63 | 44 | 49 | 48 | 0 | 0
2022-10-11 05:00 | 10 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 32 | 35 | 47 | 36 | 61 | 44 | 48 | 47 | 0 | 0
2022-10-11 06:00 | 10 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 33 | 35 | 47 | 39 | 61 | 44 | 47 | 47 | 0 | 0
2022-10-11 07:00 | 10 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 37 | 34 | 51 | 40 | 60 | 46 | 48 | 47 | 0 | 0
2022-10-11 08:00 | 10 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 42 | 35 | 56 | 44 | 62 | 47 | 48 | 48 | 0 | 0
2022-10-11 09:00 | 10 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 46 | 37 | 60 | 47 | 62 | 52 | 50 | 50 | 0 | 0
2022-10-11 10:00 | 10 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 49 | 37 | 63 | 54 | 62 | 56 | 50 | 53 | 0 | 0
2022-10-11 11:00 | 10 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 51 | 40 | 65 | 56 | 62 | 59 | 52 | 61 | 0 | 0
2022-10-11 12:00 | 10 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 52 | 39 | 68 | 56 | 63 | 60 | 53 | 70 | 0 | 0
2022-10-11 13:00 | 10 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 55 | 41 | 68 | 56 | 65 | 62 | 53 | 71 | 0 | 0
2022-10-11 14:00 | 10 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 55 | 40 | 69 | 58 | 66 | 62 | 54 | 72 | 0 | 0
2022-10-11 15:00 | 10 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 55 | 40 | 69 | 57 | 63 | 62 | 54 | 72 | 0 | 0
2022-10-11 16:00 | 10 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 53 | 39 | 66 | 56 | 59 | 61 | 52 | 70 | 0 | 0
2022-10-11 17:00 | 10 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 49 | 38 | 62 | 56 | 57 | 58 | 49 | 69 | 0 | 0
2022-10-11 18:00 | 10 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 47 | 37 | 59 | 55 | 56 | 57 | 48 | 64 | 0 | 0
2022-10-11 19:00 | 10 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 45 | 36 | 58 | 54 | 53 | 53 | 45 | 65 | 0 | 0
2022-10-11 20:00 | 10 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 45 | 36 | 56 | 54 | 52 | 52 | 44 | 65 | 0 | 0
2022-10-11 21:00 | 10 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 43 | 35 | 55 | 53 | 52 | 51 | 42 | 64 | 0 | 0
2022-10-11 22:00 | 10 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 42 | 35 | 55 | 52 | 51 | 49 | 40 | 59 | 0 | 0
2022-10-11 23:00 | 10 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 41 | 35 | 54 | 52 | 51 | 48 | 38 | 58 | 0 | 0
2022-10-12 | 10 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 41 | 36 | 54 | 51 | 49 | 47 | 38 | 56 | 0 | 0
2022-10-12 01:00 | 10 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 41 | 35 | 54 | 49 | 47 | 45 | 36 | 55 | 0 | 0
2022-10-12 02:00 | 10 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 40 | 34 | 55 | 48 | 46 | 44 | 35 | 57 | 0 | 0
2022-10-12 03:00 | 10 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 42 | 35 | 55 | 45 | 44 | 43 | 34 | 57 | 0 | 0
2022-10-12 04:00 | 10 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 42 | 34 | 55 | 44 | 45 | 42 | 34 | 58 | 0 | 0
2022-10-12 05:00 | 10 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 43 | 34 | 55 | 42 | 44 | 42 | 32 | 58 | 0 | 0
2022-10-12 06:00 | 10 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 43 | 35 | 55 | 44 | 47 | 42 | 31 | 58 | 0 | 0
2022-10-12 07:00 | 10 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 47 | 35 | 56 | 48 | 50 | 44 | 36 | 59 | 0 | 0
2022-10-12 08:00 | 10 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 49 | 36 | 58 | 53 | 53 | 47 | 41 | 61 | 0 | 0
2022-10-12 09:00 | 10 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 54 | 38 | 59 | 55 | 57 | 51 | 46 | 63 | 0 | 0
2022-10-12 10:00 | 10 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 57 | 42 | 60 | 57 | 58 | 55 | 51 | 66 | 0 | 0
2022-10-12 11:00 | 10 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 60 | 42 | 62 | 58 | 58 | 57 | 54 | 70 | 0 | 0
2022-10-12 12:00 | 10 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 62 | 42 | 63 | 60 | 60 | 59 | 56 | 72 | 0 | 0
2022-10-12 13:00 | 10 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 64 | 43 | 62 | 60 | 59 | 59 | 56 | 73 | 0 | 0
2022-10-12 14:00 | 10 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 63 | 43 | 62 | 61 | 57 | 59 | 58 | 74 | 0 | 0
2022-10-12 15:00 | 10 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 61 | 41 | 61 | 60 | 57 | 61 | 57 | 73 | 0 | 0
2022-10-12 16:00 | 10 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 60 | 41 | 59 | 60 | 55 | 59 | 55 | 72 | 0 | 0
2022-10-12 17:00 | 10 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 58 | 40 | 58 | 59 | 54 | 56 | 53 | 69 | 0 | 0
2022-10-12 18:00 | 10 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 57 | 39 | 56 | 58 | 52 | 53 | 52 | 67 | 0 | 0
2022-10-12 19:00 | 10 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 54 | 39 | 55 | 58 | 51 | 51 | 50 | 64 | 0 | 0
2022-10-12 20:00 | 10 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 54 | 37 | 55 | 58 | 49 | 49 | 46 | 65 | 0 | 0
2022-10-12 21:00 | 10 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 53 | 36 | 54 | 58 | 48 | 49 | 47 | 69 | 0 | 0
2022-10-12 22:00 | 10 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 54 | 36 | 53 | 59 | 47 | 47 | 46 | 67 | 0 | 0
2022-10-12 23:00 | 10 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 55 | 36 | 51 | 58 | 47 | 46 | 45 | 67 | 0 | 0
2022-10-13 | 10 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 54 | 35 | 50 | 58 | 46 | 45 | 46 | 65 | 0 | 0
2022-10-13 01:00 | 10 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 54 | 34 | 50 | 58 | 45 | 45 | 48 | 64 | 0 | 0
2022-10-13 02:00 | 10 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 54 | 30 | 50 | 58 | 47 | 42 | 48 | 64 | 0 | 0
2022-10-13 03:00 | 10 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 55 | 29 | 50 | 59 | 46 | 39 | 48 | 64 | 0 | 0
2022-10-13 04:00 | 10 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 56 | 28 | 50 | 58 | 43 | 39 | 49 | 65 | 0 | 0
2022-10-13 05:00 | 10 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 56 | 27 | 49 | 58 | 41 | 39 | 50 | 61 | 0 | 0
2022-10-13 06:00 | 10 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 55 | 27 | 49 | 58 | 43 | 39 | 50 | 60 | 0 | 0
2022-10-13 07:00 | 10 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 55 | 30 | 49 | 60 | 49 | 42 | 51 | 61 | 0 | 0
2022-10-13 08:00 | 10 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 56 | 36 | 49 | 61 | 50 | 47 | 53 | 64 | 0 | 0
2022-10-13 09:00 | 10 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 57 | 43 | 49 | 61 | 52 | 53 | 54 | 66 | 0 | 0
2022-10-13 10:00 | 10 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 58 | 43 | 50 | 61 | 52 | 55 | 54 | 65 | 0 | 0
2022-10-13 11:00 | 10 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 59 | 47 | 51 | 63 | 53 | 57 | 55 | 65 | 0 | 0
2022-10-13 12:00 | 10 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 59 | 50 | 52 | 63 | 49 | 59 | 55 | 65 | 0 | 0
2022-10-13 13:00 | 10 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 61 | 52 | 52 | 63 | 52 | 60 | 57 | 65 | 0 | 0
2022-10-13 14:00 | 10 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 62 | 50 | 51 | 64 | 51 | 61 | 58 | 63 | 0 | 0
2022-10-13 15:00 | 10 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 61 | 49 | 51 | 63 | 52 | 61 | 58 | 62 | 0 | 0
2022-10-13 16:00 | 10 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 61 | 49 | 51 | 63 | 52 | 61 | 58 | 62 | 0 | 0
2022-10-13 17:00 | 10 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 61 | 46 | 51 | 63 | 48 | 56 | 58 | 62 | 0 | 0
2022-10-13 18:00 | 10 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 60 | 37 | 51 | 62 | 47 | 53 | 58 | 59 | 0 | 0
2022-10-13 19:00 | 10 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 60 | 34 | 50 | 63 | 44 | 53 | 59 | 57 | 0 | 0
2022-10-13 20:00 | 10 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 58 | 34 | 49 | 63 | 42 | 49 | 57 | 57 | 0 | 0
2022-10-13 21:00 | 10 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 58 | 30 | 48 | 62 | 39 | 46 | 55 | 56 | 0 | 0
2022-10-13 22:00 | 10 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 58 | 29 | 47 | 62 | 40 | 46 | 56 | 55 | 0 | 0
2022-10-13 23:00 | 10 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 58 | 30 | 46 | 62 | 42 | 45 | 56 | 55 | 0 | 0
2022-10-14 | 10 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 59 | 27 | 45 | 62 | 42 | 44 | 55 | 54 | 0 | 0
2022-10-14 01:00 | 10 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 59 | 27 | 45 | 62 | 42 | 42 | 57 | 54 | 0 | 0
2022-10-14 02:00 | 10 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 59 | 26 | 44 | 62 | 42 | 41 | 55 | 54 | 0 | 0
2022-10-14 03:00 | 10 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 59 | 25 | 44 | 62 | 40 | 41 | 56 | 53 | 0 | 0
2022-10-14 04:00 | 10 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 59 | 25 | 44 | 62 | 39 | 37 | 56 | 54 | 0 | 0
2022-10-14 05:00 | 10 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 60 | 27 | 43 | 63 | 37 | 38 | 56 | 53 | 0 | 0
2022-10-14 06:00 | 10 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 60 | 29 | 43 | 62 | 37 | 37 | 56 | 53 | 0 | 0
2022-10-14 07:00 | 10 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 61 | 33 | 43 | 64 | 44 | 42 | 57 | 52 | 0 | 0
2022-10-14 08:00 | 10 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 61 | 44 | 43 | 65 | 47 | 47 | 59 | 51 | 0 | 0
2022-10-14 09:00 | 10 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 62 | 47 | 43 | 66 | 49 | 52 | 60 | 50 | 0 | 0
2022-10-14 10:00 | 10 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 63 | 50 | 43 | 67 | 51 | 59 | 61 | 51 | 0 | 0
2022-10-14 11:00 | 10 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 63 | 53 | 43 | 68 | 54 | 62 | 62 | 52 | 0 | 0
2022-10-14 12:00 | 10 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 63 | 55 | 43 | 66 | 55 | 66 | 64 | 52 | 0 | 0
2022-10-14 13:00 | 10 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 63 | 56 | 43 | 69 | 57 | 67 | 66 | 51 | 0 | 0
2022-10-14 14:00 | 10 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 63 | 57 | 43 | 68 | 57 | 69 | 65 | 51 | 0 | 0
2022-10-14 15:00 | 10 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 64 | 57 | 43 | 67 | 57 | 69 | 64 | 51 | 0 | 0
2022-10-14 16:00 | 10 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 60 | 56 | 43 | 64 | 55 | 65 | 63 | 50 | 0 | 0
2022-10-14 17:00 | 10 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 54 | 49 | 42 | 57 | 47 | 64 | 63 | 50 | 0 | 0
2022-10-14 18:00 | 10 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 51 | 46 | 42 | 52 | 48 | 57 | 62 | 50 | 0 | 0
2022-10-14 19:00 | 10 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 48 | 41 | 43 | 50 | 46 | 52 | 63 | 50 | 0 | 0
2022-10-14 20:00 | 10 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 47 | 37 | 43 | 48 | 49 | 52 | 62 | 48 | 0 | 0
2022-10-14 21:00 | 10 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 45 | 37 | 44 | 44 | 49 | 51 | 62 | 48 | 0 | 0
2022-10-14 22:00 | 10 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 42 | 33 | 43 | 45 | 49 | 52 | 62 | 48 | 0 | 0
2022-10-14 23:00 | 10 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 41 | 33 | 42 | 47 | 49 | 52 | 62 | 48 | 0 | 0
2022-10-15 | 10 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 40 | 33 | 41 | 44 | 49 | 51 | 62 | 48 | 0 | 0
2022-10-15 01:00 | 10 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 39 | 32 | 41 | 41 | 48 | 50 | 61 | 42 | 0 | 0
2022-10-15 02:00 | 10 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 38 | 32 | 41 | 41 | 48 | 49 | 60 | 41 | 0 | 0
2022-10-15 03:00 | 10 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 37 | 31 | 41 | 41 | 48 | 46 | 62 | 40 | 0 | 0
2022-10-15 04:00 | 10 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 38 | 31 | 41 | 41 | 46 | 44 | 61 | 40 | 0 | 0
2022-10-15 05:00 | 10 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 38 | 31 | 42 | 43 | 48 | 42 | 62 | 40 | 0 | 0
2022-10-15 06:00 | 10 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 39 | 32 | 42 | 42 | 48 | 42 | 66 | 40 | 0 | 0
2022-10-15 07:00 | 10 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 40 | 36 | 42 | 45 | 51 | 47 | 66 | 41 | 0 | 0
2022-10-15 08:00 | 10 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 42 | 48 | 42 | 48 | 54 | 51 | 67 | 44 | 0 | 0
2022-10-15 09:00 | 10 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 44 | 55 | 42 | 52 | 59 | 58 | 68 | 48 | 0 | 0
2022-10-15 10:00 | 10 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 47 | 58 | 42 | 53 | 60 | 60 | 70 | 50 | 0 | 0
2022-10-15 11:00 | 10 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 47 | 60 | 42 | 57 | 61 | 61 | 72 | 53 | 0 | 0
2022-10-15 12:00 | 10 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 47 | 63 | 42 | 57 | 62 | 64 | 71 | 54 | 0 | 0
2022-10-15 13:00 | 10 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 47 | 65 | 41 | 57 | 62 | 63 | 70 | 56 | 0 | 0
2022-10-15 14:00 | 10 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 47 | 65 | 41 | 56 | 62 | 63 | 70 | 55 | 0 | 0
2022-10-15 15:00 | 10 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 48 | 66 | 40 | 55 | 61 | 63 | 69 | 54 | 0 | 0
2022-10-15 16:00 | 10 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 46 | 64 | 40 | 54 | 59 | 62 | 69 | 53 | 0 | 0
2022-10-15 17:00 | 10 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 45 | 56 | 40 | 53 | 58 | 61 | 68 | 48 | 0 | 0
2022-10-15 18:00 | 10 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 44 | 50 | 40 | 52 | 56 | 59 | 66 | 50 | 0 | 0
2022-10-15 19:00 | 10 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 43 | 47 | 40 | 50 | 55 | 58 | 65 | 47 | 0 | 0
2022-10-15 20:00 | 10 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 44 | 48 | 39 | 50 | 55 | 58 | 63 | 43 | 0 | 0
2022-10-15 21:00 | 10 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 43 | 43 | 39 | 50 | 54 | 57 | 60 | 43 | 0 | 0
2022-10-15 22:00 | 10 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 44 | 42 | 38 | 49 | 51 | 56 | 57 | 42 | 0 | 0
2022-10-15 23:00 | 10 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 43 | 41 | 38 | 48 | 53 | 55 | 55 | 41 | 0 | 0
2022-10-16 | 10 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 43 | 40 | 37 | 45 | 50 | 54 | 53 | 42 | 0 | 0
2022-10-16 01:00 | 10 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 43 | 40 | 36 | 43 | 49 | 55 | 51 | 42 | 0 | 0
2022-10-16 02:00 | 10 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 43 | 40 | 35 | 39 | 47 | 54 | 49 | 41 | 0 | 0
2022-10-16 03:00 | 10 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 43 | 40 | 34 | 43 | 49 | 55 | 48 | 42 | 0 | 0
2022-10-16 04:00 | 10 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 43 | 37 | 34 | 38 | 46 | 52 | 48 | 42 | 0 | 0
2022-10-16 05:00 | 10 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 43 | 36 | 35 | 38 | 46 | 50 | 49 | 42 | 0 | 0
2022-10-16 06:00 | 10 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 43 | 37 | 35 | 38 | 48 | 49 | 50 | 42 | 0 | 0
2022-10-16 07:00 | 10 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 43 | 44 | 37 | 44 | 51 | 49 | 51 | 43 | 0 | 0
2022-10-16 08:00 | 10 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 44 | 51 | 40 | 48 | 56 | 48 | 55 | 44 | 0 | 0
2022-10-16 09:00 | 10 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 45 | 62 | 42 | 53 | 59 | 48 | 59 | 45 | 0 | 0
2022-10-16 10:00 | 10 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 47 | 63 | 43 | 56 | 64 | 49 | 61 | 48 | 0 | 0
2022-10-16 11:00 | 10 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 47 | 66 | 43 | 56 | 68 | 50 | 62 | 50 | 0 | 0
2022-10-16 12:00 | 10 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 71 | 47 | 67 | 44 | 56 | 70 | 49 | 62 | 53 | 0 | 0
2022-10-16 13:00 | 10 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 75 | 48 | 67 | 44 | 58 | 73 | 51 | 58 | 53 | 0 | 0
2022-10-16 14:00 | 10 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 75 | 47 | 68 | 45 | 55 | 73 | 51 | 60 | 54 | 0 | 0
2022-10-16 15:00 | 10 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 75 | 47 | 68 | 45 | 55 | 73 | 51 | 58 | 52 | 0 | 0
2022-10-16 16:00 | 10 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 73 | 46 | 66 | 44 | 54 | 68 | 50 | 56 | 50 | 0 | 0
2022-10-16 17:00 | 10 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 45 | 61 | 43 | 52 | 64 | 47 | 50 | 48 | 0 | 0
2022-10-16 18:00 | 10 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 45 | 57 | 42 | 49 | 64 | 45 | 49 | 47 | 0 | 0
2022-10-16 19:00 | 10 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 46 | 53 | 41 | 48 | 63 | 45 | 48 | 47 | 0 | 0
2022-10-16 20:00 | 10 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 46 | 53 | 39 | 47 | 59 | 41 | 45 | 47 | 0 | 0
2022-10-16 21:00 | 10 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 45 | 53 | 38 | 46 | 58 | 41 | 44 | 45 | 0 | 0
2022-10-16 22:00 | 10 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 45 | 53 | 36 | 45 | 57 | 37 | 42 | 44 | 0 | 0
2022-10-16 23:00 | 10 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 45 | 51 | 34 | 43 | 56 | 36 | 39 | 44 | 0 | 0
2022-10-17 | 10 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 43 | 52 | 32 | 44 | 56 | 35 | 38 | 44 | 0 | 0
2022-10-17 01:00 | 10 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 43 | 50 | 30 | 44 | 55 | 33 | 37 | 44 | 0 | 0
2022-10-17 02:00 | 10 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 41 | 50 | 29 | 45 | 54 | 34 | 36 | 43 | 0 | 0
2022-10-17 03:00 | 10 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 41 | 50 | 27 | 45 | 53 | 32 | 34 | 41 | 0 | 0
2022-10-17 04:00 | 10 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 41 | 49 | 27 | 46 | 52 | 33 | 34 | 38 | 0 | 0
2022-10-17 05:00 | 10 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 42 | 49 | 26 | 47 | 51 | 34 | 33 | 36 | 0 | 0
2022-10-17 06:00 | 10 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 43 | 48 | 26 | 46 | 54 | 33 | 33 | 36 | 0 | 0
2022-10-17 07:00 | 10 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 43 | 51 | 31 | 46 | 59 | 33 | 34 | 39 | 0 | 0
2022-10-17 08:00 | 10 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 43 | 54 | 37 | 47 | 62 | 41 | 38 | 41 | 0 | 0
2022-10-17 09:00 | 10 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 67 | 44 | 60 | 42 | 48 | 67 | 47 | 45 | 45 | 0 | 0
2022-10-17 10:00 | 10 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 45 | 63 | 44 | 49 | 71 | 50 | 49 | 47 | 0 | 0
2022-10-17 11:00 | 10 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 76 | 45 | 63 | 46 | 50 | 75 | 54 | 52 | 51 | 0 | 0
2022-10-17 12:00 | 10 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 78 | 46 | 66 | 48 | 50 | 77 | 56 | 53 | 54 | 0 | 0
2022-10-17 13:00 | 10 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 79 | 46 | 66 | 48 | 51 | 77 | 57 | 55 | 56 | 0 | 0
2022-10-17 14:00 | 10 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 78 | 45 | 65 | 48 | 51 | 76 | 58 | 58 | 58 | 0 | 0
2022-10-17 15:00 | 10 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 76 | 46 | 52 | 48 | 49 | 75 | 59 | 57 | 58 | 0 | 0
2022-10-17 16:00 | 10 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 75 | 45 | 50 | 43 | 48 | 71 | 58 | 55 | 55 | 0 | 0
2022-10-17 17:00 | 10 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 72 | 45 | 49 | 39 | 48 | 68 | 55 | 50 | 46 | 0 | 0
2022-10-17 18:00 | 10 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 72 | 44 | 49 | 34 | 48 | 66 | 51 | 48 | 42 | 0 | 0
2022-10-17 19:00 | 10 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 71 | 44 | 48 | 34 | 47 | 65 | 50 | 46 | 40 | 0 | 0
2022-10-17 20:00 | 10 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 43 | 48 | 35 | 47 | 65 | 49 | 45 | 38 | 0 | 0
2022-10-17 21:00 | 10 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 69 | 43 | 48 | 35 | 47 | 65 | 49 | 41 | 37 | 0 | 0
2022-10-17 22:00 | 10 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 43 | 46 | 35 | 46 | 65 | 51 | 43 | 35 | 0 | 0
2022-10-17 23:00 | 10 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 42 | 44 | 35 | 48 | 65 | 53 | 38 | 34 | 0 | 0
2022-10-18 | 10 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 43 | 42 | 35 | 48 | 66 | 56 | 41 | 34 | 0 | 0
2022-10-18 01:00 | 10 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 42 | 40 | 35 | 47 | 67 | 56 | 42 | 33 | 0 | 0
2022-10-18 02:00 | 10 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 41 | 43 | 35 | 46 | 67 | 54 | 39 | 32 | 0 | 0
2022-10-18 03:00 | 10 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 67 | 40 | 42 | 35 | 46 | 68 | 54 | 40 | 32 | 0 | 0
2022-10-18 04:00 | 10 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 68 | 40 | 42 | 37 | 47 | 68 | 56 | 38 | 32 | 0 | 0
2022-10-18 05:00 | 10 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 70 | 40 | 43 | 38 | 47 | 68 | 57 | 41 | 31 | 0 | 0
2022-10-18 06:00 | 10 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 69 | 40 | 44 | 40 | 47 | 68 | 59 | 41 | 31 | 0 | 0
2022-10-18 07:00 | 10 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 69 | 40 | 44 | 42 | 48 | 69 | 58 | 46 | 33 | 0 | 0
2022-10-18 08:00 | 10 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 70 | 42 | 45 | 45 | 51 | 70 | 61 | 51 | 36 | 0 | 0
2022-10-18 09:00 | 10 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 71 | 45 | 46 | 47 | 51 | 70 | 58 | 55 | 39 | 0 | 0
2022-10-18 10:00 | 10 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 72 | 48 | 47 | 47 | 52 | 72 | 54 | 56 | 42 | 0 | 0
2022-10-18 11:00 | 10 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 72 | 49 | 49 | 48 | 54 | 71 | 58 | 58 | 45 | 0 | 0
2022-10-18 12:00 | 10 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 49 | 51 | 48 | 53 | 74 | 60 | 59 | 49 | 0 | 0
2022-10-18 13:00 | 10 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 75 | 50 | 51 | 49 | 57 | 75 | 60 | 62 | 50 | 0 | 0
2022-10-18 14:00 | 10 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 50 | 51 | 49 | 57 | 74 | 58 | 62 | 51 | 0 | 0
2022-10-18 15:00 | 10 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 49 | 51 | 50 | 55 | 71 | 56 | 61 | 51 | 0 | 0
2022-10-18 16:00 | 10 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 48 | 48 | 50 | 53 | 60 | 53 | 59 | 50 | 0 | 0
2022-10-18 17:00 | 10 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 44 | 45 | 49 | 51 | 60 | 50 | 58 | 50 | 0 | 0
2022-10-18 18:00 | 10 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 42 | 41 | 49 | 43 | 59 | 47 | 57 | 50 | 0 | 0
2022-10-18 19:00 | 10 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 39 | 37 | 48 | 42 | 59 | 47 | 57 | 49 | 0 | 0
2022-10-18 20:00 | 10 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 38 | 36 | 48 | 40 | 59 | 45 | 56 | 49 | 0 | 0
2022-10-18 21:00 | 10 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 37 | 35 | 47 | 40 | 59 | 44 | 56 | 48 | 0 | 0
2022-10-18 22:00 | 10 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 37 | 35 | 47 | 38 | 59 | 43 | 55 | 48 | 0 | 0
2022-10-18 23:00 | 10 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 35 | 33 | 47 | 34 | 59 | 42 | 57 | 48 | 0 | 0
2022-10-19 | 10 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 34 | 32 | 47 | 34 | 59 | 42 | 58 | 47 | 0 | 0
2022-10-19 01:00 | 10 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 34 | 30 | 47 | 33 | 59 | 40 | 57 | 47 | 0 | 0
2022-10-19 02:00 | 10 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 35 | 33 | 48 | 33 | 59 | 39 | 58 | 47 | 0 | 0
2022-10-19 03:00 | 10 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 35 | 30 | 48 | 33 | 58 | 38 | 58 | 47 | 0 | 0
2022-10-19 04:00 | 10 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 34 | 30 | 48 | 32 | 57 | 38 | 56 | 47 | 0 | 0
2022-10-19 05:00 | 10 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 30 | 31 | 47 | 33 | 58 | 38 | 58 | 48 | 0 | 0
2022-10-19 06:00 | 10 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 31 | 30 | 47 | 33 | 57 | 38 | 58 | 48 | 0 | 0
2022-10-19 07:00 | 10 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 34 | 34 | 48 | 39 | 58 | 38 | 59 | 48 | 0 | 0
2022-10-19 08:00 | 10 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 39 | 41 | 49 | 46 | 57 | 39 | 60 | 50 | 0 | 0
2022-10-19 09:00 | 10 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 44 | 50 | 50 | 47 | 60 | 45 | 60 | 53 | 0 | 0
2022-10-19 10:00 | 10 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 47 | 55 | 50 | 50 | 63 | 45 | 63 | 55 | 0 | 0
2022-10-19 11:00 | 10 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 52 | 59 | 50 | 53 | 64 | 43 | 63 | 56 | 0 | 0
2022-10-19 12:00 | 10 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 69 | 53 | 61 | 50 | 56 | 66 | 41 | 64 | 57 | 0 | 0
2022-10-19 13:00 | 10 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 70 | 55 | 62 | 50 | 58 | 67 | 42 | 65 | 57 | 0 | 0
2022-10-19 14:00 | 10 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 70 | 55 | 63 | 50 | 59 | 69 | 42 | 64 | 57 | 0 | 0
2022-10-19 15:00 | 10 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 70 | 54 | 62 | 50 | 59 | 67 | 41 | 62 | 57 | 0 | 0
2022-10-19 16:00 | 10 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 52 | 61 | 50 | 57 | 63 | 41 | 61 | 56 | 0 | 0
2022-10-19 17:00 | 10 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 48 | 57 | 49 | 48 | 60 | 41 | 60 | 56 | 0 | 0
2022-10-19 18:00 | 10 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 48 | 51 | 49 | 45 | 59 | 40 | 59 | 56 | 0 | 0
2022-10-19 19:00 | 10 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 47 | 54 | 50 | 44 | 58 | 38 | 58 | 54 | 0 | 0
2022-10-19 20:00 | 10 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 46 | 53 | 51 | 40 | 60 | 37 | 58 | 53 | 0 | 0
2022-10-19 21:00 | 10 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 45 | 51 | 52 | 38 | 57 | 35 | 57 | 52 | 0 | 0
2022-10-19 22:00 | 10 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 45 | 51 | 51 | 36 | 57 | 31 | 55 | 52 | 0 | 0
2022-10-19 23:00 | 10 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 44 | 52 | 50 | 35 | 57 | 32 | 52 | 52 | 0 | 0
2022-10-20 | 10 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 42 | 52 | 49 | 36 | 55 | 32 | 52 | 53 | 0 | 0
2022-10-20 01:00 | 10 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 42 | 51 | 48 | 35 | 53 | 31 | 51 | 53 | 0 | 0
2022-10-20 02:00 | 10 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 41 | 52 | 47 | 35 | 49 | 31 | 50 | 52 | 0 | 0
2022-10-20 03:00 | 10 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 39 | 51 | 46 | 33 | 48 | 30 | 49 | 51 | 0 | 0
2022-10-20 04:00 | 10 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 36 | 51 | 45 | 33 | 48 | 29 | 48 | 50 | 0 | 0
2022-10-20 05:00 | 10 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 38 | 51 | 43 | 39 | 47 | 29 | 48 | 50 | 0 | 0
2022-10-20 06:00 | 10 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 41 | 51 | 42 | 31 | 46 | 33 | 48 | 50 | 0 | 0
2022-10-20 07:00 | 10 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 42 | 53 | 44 | 39 | 49 | 34 | 49 | 50 | 0 | 0
2022-10-20 08:00 | 10 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 43 | 53 | 47 | 47 | 52 | 40 | 51 | 51 | 0 | 0
2022-10-20 09:00 | 10 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 45 | 54 | 49 | 53 | 55 | 46 | 52 | 52 | 0 | 0
2022-10-20 10:00 | 10 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 49 | 52 | 50 | 55 | 57 | 50 | 53 | 53 | 0 | 0
2022-10-20 11:00 | 10 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 52 | 51 | 52 | 57 | 57 | 55 | 55 | 54 | 0 | 0
2022-10-20 12:00 | 10 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 54 | 51 | 53 | 60 | 60 | 58 | 55 | 56 | 0 | 0
2022-10-20 13:00 | 10 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 57 | 51 | 53 | 61 | 60 | 61 | 53 | 56 | 0 | 0
2022-10-20 14:00 | 10 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 58 | 51 | 52 | 62 | 58 | 61 | 52 | 57 | 0 | 0
2022-10-20 15:00 | 10 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 57 | 52 | 52 | 62 | 57 | 61 | 52 | 58 | 0 | 0
2022-10-20 16:00 | 10 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 56 | 51 | 49 | 60 | 55 | 60 | 51 | 57 | 0 | 0
2022-10-20 17:00 | 10 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 53 | 50 | 47 | 50 | 53 | 57 | 49 | 50 | 0 | 0
2022-10-20 18:00 | 10 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 53 | 51 | 44 | 48 | 53 | 55 | 49 | 47 | 0 | 0
2022-10-20 19:00 | 10 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 51 | 49 | 44 | 46 | 50 | 52 | 47 | 46 | 0 | 0
2022-10-20 20:00 | 10 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 48 | 48 | 43 | 42 | 47 | 52 | 45 | 43 | 0 | 0
2022-10-20 21:00 | 10 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 49 | 47 | 43 | 40 | 47 | 52 | 45 | 42 | 0 | 0
2022-10-20 22:00 | 10 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 46 | 46 | 44 | 40 | 45 | 54 | 43 | 41 | 0 | 0
2022-10-20 23:00 | 10 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 46 | 45 | 46 | 38 | 47 | 50 | 42 | 41 | 0 | 0
2022-10-21 | 10 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 45 | 43 | 47 | 37 | 49 | 50 | 42 | 39 | 0 | 0
2022-10-21 01:00 | 10 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 43 | 43 | 47 | 38 | 45 | 49 | 41 | 37 | 0 | 0
2022-10-21 02:00 | 10 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 43 | 42 | 47 | 35 | 44 | 49 | 41 | 37 | 0 | 0
2022-10-21 03:00 | 10 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 41 | 40 | 47 | 35 | 47 | 47 | 40 | 37 | 0 | 0
2022-10-21 04:00 | 10 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 42 | 40 | 47 | 35 | 48 | 47 | 41 | 39 | 0 | 0
2022-10-21 05:00 | 10 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 43 | 38 | 47 | 34 | 49 | 45 | 41 | 38 | 0 | 0
2022-10-21 06:00 | 10 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 43 | 38 | 47 | 39 | 48 | 45 | 42 | 38 | 0 | 0
2022-10-21 07:00 | 10 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 45 | 38 | 51 | 43 | 50 | 49 | 46 | 39 | 0 | 0
2022-10-21 08:00 | 10 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 48 | 39 | 55 | 48 | 57 | 57 | 50 | 40 | 0 | 0
2022-10-21 09:00 | 10 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 53 | 39 | 59 | 54 | 60 | 60 | 51 | 41 | 0 | 0
2022-10-21 10:00 | 10 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 57 | 39 | 62 | 60 | 64 | 60 | 54 | 48 | 0 | 0
2022-10-21 11:00 | 10 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 60 | 39 | 65 | 64 | 67 | 62 | 56 | 56 | 0 | 0
2022-10-21 12:00 | 10 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 64 | 38 | 68 | 67 | 69 | 65 | 57 | 62 | 0 | 0
2022-10-21 13:00 | 10 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 64 | 38 | 68 | 67 | 69 | 65 | 57 | 65 | 0 | 0
2022-10-21 14:00 | 10 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 64 | 38 | 68 | 67 | 70 | 66 | 59 | 68 | 0 | 0
2022-10-21 15:00 | 10 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 62 | 38 | 68 | 66 | 67 | 66 | 57 | 69 | 0 | 0
2022-10-21 16:00 | 10 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 58 | 35 | 65 | 63 | 65 | 65 | 54 | 65 | 0 | 0
2022-10-21 17:00 | 10 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 58 | 34 | 62 | 62 | 62 | 60 | 52 | 56 | 0 | 0
2022-10-21 18:00 | 10 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 57 | 32 | 59 | 59 | 62 | 56 | 47 | 54 | 0 | 0
2022-10-21 19:00 | 10 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 54 | 33 | 59 | 58 | 59 | 55 | 46 | 52 | 0 | 0
2022-10-21 20:00 | 10 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 52 | 32 | 58 | 58 | 60 | 55 | 45 | 50 | 0 | 0
2022-10-21 21:00 | 10 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 52 | 33 | 58 | 57 | 56 | 54 | 45 | 48 | 0 | 0
2022-10-21 22:00 | 10 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 52 | 33 | 57 | 57 | 57 | 52 | 42 | 47 | 0 | 0
2022-10-21 23:00 | 10 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 51 | 33 | 57 | 54 | 57 | 53 | 43 | 45 | 0 | 0
2022-10-22 | 10 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 50 | 33 | 56 | 52 | 55 | 52 | 45 | 45 | 0 | 0
2022-10-22 01:00 | 10 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 50 | 32 | 56 | 51 | 54 | 53 | 44 | 44 | 0 | 0
2022-10-22 02:00 | 10 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 50 | 33 | 56 | 51 | 53 | 53 | 44 | 43 | 0 | 0
2022-10-22 03:00 | 10 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 48 | 33 | 56 | 53 | 52 | 51 | 45 | 44 | 0 | 0
2022-10-22 04:00 | 10 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 45 | 33 | 55 | 53 | 50 | 51 | 46 | 44 | 0 | 0
2022-10-22 05:00 | 10 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 43 | 34 | 55 | 53 | 49 | 51 | 44 | 44 | 0 | 0
2022-10-22 06:00 | 10 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 45 | 32 | 54 | 53 | 50 | 51 | 43 | 43 | 0 | 0
2022-10-22 07:00 | 10 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 45 | 32 | 57 | 54 | 51 | 52 | 45 | 42 | 0 | 0
2022-10-22 08:00 | 10 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 46 | 34 | 61 | 59 | 55 | 57 | 53 | 44 | 0 | 0
2022-10-22 09:00 | 10 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 47 | 37 | 64 | 63 | 56 | 59 | 55 | 45 | 0 | 0
2022-10-22 10:00 | 10 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 49 | 37 | 66 | 66 | 58 | 64 | 59 | 50 | 0 | 0
2022-10-22 11:00 | 10 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 55 | 40 | 68 | 69 | 59 | 65 | 61 | 59 | 0 | 0
2022-10-22 12:00 | 10 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 60 | 42 | 70 | 70 | 61 | 66 | 63 | 68 | 0 | 0
2022-10-22 13:00 | 10 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 63 | 45 | 71 | 72 | 61 | 65 | 65 | 71 | 0 | 0
2022-10-22 14:00 | 10 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 63 | 45 | 71 | 73 | 61 | 65 | 66 | 73 | 0 | 0
2022-10-22 15:00 | 10 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 65 | 43 | 72 | 71 | 61 | 64 | 65 | 73 | 0 | 0
2022-10-22 16:00 | 10 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 63 | 40 | 70 | 67 | 58 | 62 | 63 | 67 | 0 | 0
2022-10-22 17:00 | 10 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 60 | 40 | 68 | 60 | 55 | 61 | 58 | 60 | 0 | 0
2022-10-22 18:00 | 10 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 59 | 40 | 66 | 55 | 52 | 58 | 55 | 57 | 0 | 0
2022-10-22 19:00 | 10 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 57 | 40 | 66 | 53 | 51 | 54 | 54 | 53 | 0 | 0
2022-10-22 20:00 | 10 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 57 | 40 | 65 | 53 | 49 | 53 | 53 | 53 | 0 | 0
2022-10-22 21:00 | 10 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 57 | 41 | 65 | 52 | 47 | 52 | 51 | 53 | 0 | 0
2022-10-22 22:00 | 10 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 57 | 38 | 64 | 51 | 46 | 51 | 50 | 51 | 0 | 0
2022-10-22 23:00 | 10 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 57 | 33 | 64 | 51 | 44 | 51 | 49 | 51 | 0 | 0
2022-10-23 | 10 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 55 | 33 | 63 | 51 | 42 | 50 | 46 | 48 | 0 | 0
2022-10-23 01:00 | 10 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 56 | 34 | 60 | 50 | 40 | 50 | 47 | 48 | 0 | 0
2022-10-23 02:00 | 10 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 56 | 35 | 57 | 50 | 39 | 50 | 48 | 47 | 0 | 0
2022-10-23 03:00 | 10 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 55 | 37 | 54 | 49 | 39 | 48 | 48 | 45 | 0 | 0
2022-10-23 04:00 | 10 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 56 | 37 | 53 | 48 | 41 | 46 | 48 | 46 | 0 | 0
2022-10-23 05:00 | 10 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 55 | 38 | 52 | 48 | 39 | 44 | 48 | 46 | 0 | 0
2022-10-23 06:00 | 10 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 56 | 38 | 51 | 50 | 37 | 44 | 47 | 45 | 0 | 0
2022-10-23 07:00 | 10 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 57 | 39 | 50 | 55 | 43 | 43 | 50 | 50 | 0 | 0
2022-10-23 08:00 | 10 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 59 | 43 | 50 | 58 | 46 | 43 | 54 | 53 | 0 | 0
2022-10-23 09:00 | 10 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 60 | 46 | 49 | 64 | 47 | 42 | 57 | 55 | 0 | 0
2022-10-23 10:00 | 10 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 60 | 48 | 47 | 70 | 49 | 42 | 60 | 59 | 0 | 0
2022-10-23 11:00 | 10 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 59 | 50 | 46 | 69 | 50 | 43 | 63 | 62 | 0 | 0
2022-10-23 12:00 | 10 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 62 | 52 | 44 | 69 | 51 | 46 | 66 | 67 | 0 | 0
2022-10-23 13:00 | 10 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 60 | 55 | 44 | 69 | 52 | 49 | 70 | 66 | 0 | 0
2022-10-23 14:00 | 10 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 62 | 51 | 43 | 69 | 53 | 47 | 69 | 64 | 0 | 0
2022-10-23 15:00 | 10 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 62 | 51 | 43 | 68 | 51 | 48 | 68 | 57 | 0 | 0
2022-10-23 16:00 | 10 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 56 | 50 | 43 | 67 | 50 | 46 | 65 | 53 | 0 | 0
2022-10-23 17:00 | 10 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 54 | 47 | 42 | 62 | 46 | 43 | 62 | 51 | 0 | 0
2022-10-23 18:00 | 10 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 53 | 42 | 42 | 60 | 47 | 43 | 59 | 50 | 0 | 0
2022-10-23 19:00 | 10 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 52 | 45 | 41 | 61 | 46 | 39 | 58 | 49 | 0 | 0
2022-10-23 20:00 | 10 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 50 | 42 | 40 | 60 | 46 | 36 | 54 | 48 | 0 | 0
2022-10-23 21:00 | 10 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 48 | 38 | 39 | 58 | 44 | 37 | 54 | 45 | 0 | 0
2022-10-23 22:00 | 10 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 48 | 35 | 38 | 56 | 44 | 35 | 53 | 45 | 0 | 0
2022-10-23 23:00 | 10 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 45 | 32 | 38 | 56 | 43 | 33 | 53 | 45 | 0 | 0
2022-10-24 | 10 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 43 | 35 | 37 | 58 | 43 | 31 | 52 | 45 | 0 | 0
2022-10-24 01:00 | 10 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 43 | 37 | 36 | 57 | 44 | 30 | 51 | 45 | 0 | 0
2022-10-24 02:00 | 10 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 42 | 37 | 36 | 55 | 44 | 28 | 53 | 44 | 0 | 0
2022-10-24 03:00 | 10 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 39 | 40 | 35 | 53 | 43 | 27 | 55 | 43 | 0 | 0
2022-10-24 04:00 | 10 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 39 | 43 | 35 | 54 | 42 | 26 | 57 | 41 | 0 | 0
2022-10-24 05:00 | 10 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 38 | 42 | 35 | 50 | 41 | 25 | 58 | 35 | 0 | 0
2022-10-24 06:00 | 10 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 39 | 41 | 35 | 50 | 41 | 24 | 59 | 37 | 0 | 0
2022-10-24 07:00 | 10 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 40 | 46 | 37 | 54 | 43 | 27 | 60 | 40 | 0 | 0
2022-10-24 08:00 | 10 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 43 | 49 | 38 | 57 | 46 | 30 | 60 | 43 | 0 | 0
2022-10-24 09:00 | 10 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 46 | 53 | 40 | 60 | 50 | 35 | 61 | 45 | 0 | 0
2022-10-24 10:00 | 10 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 47 | 56 | 42 | 59 | 52 | 38 | 61 | 47 | 0 | 0
2022-10-24 11:00 | 10 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 49 | 55 | 45 | 59 | 53 | 40 | 61 | 49 | 0 | 0
2022-10-24 12:00 | 10 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 51 | 59 | 47 | 62 | 57 | 44 | 61 | 50 | 0 | 0
2022-10-24 13:00 | 10 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 51 | 59 | 47 | 62 | 58 | 44 | 60 | 52 | 0 | 0
2022-10-24 14:00 | 10 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 52 | 59 | 47 | 63 | 58 | 42 | 60 | 53 | 0 | 0
2022-10-24 15:00 | 10 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 50 | 59 | 47 | 63 | 54 | 42 | 62 | 53 | 0 | 0
2022-10-24 16:00 | 10 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 48 | 58 | 45 | 59 | 53 | 41 | 62 | 52 | 0 | 0
2022-10-24 17:00 | 10 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 44 | 58 | 42 | 55 | 52 | 38 | 61 | 49 | 0 | 0
2022-10-24 18:00 | 10 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 43 | 57 | 40 | 50 | 51 | 37 | 63 | 46 | 0 | 0
2022-10-24 19:00 | 10 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 42 | 52 | 40 | 47 | 51 | 36 | 63 | 44 | 0 | 0
2022-10-24 20:00 | 10 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 39 | 45 | 39 | 49 | 51 | 35 | 63 | 42 | 0 | 0
2022-10-24 21:00 | 10 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 39 | 41 | 39 | 49 | 51 | 34 | 62 | 41 | 0 | 0
2022-10-24 22:00 | 10 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 37 | 38 | 39 | 48 | 50 | 33 | 61 | 39 | 0 | 0
2022-10-24 23:00 | 10 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 35 | 38 | 39 | 45 | 50 | 33 | 61 | 36 | 0 | 0
2022-10-25 | 10 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 35 | 37 | 39 | 42 | 51 | 33 | 62 | 36 | 0 | 0
2022-10-25 01:00 | 10 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 34 | 35 | 39 | 40 | 52 | 32 | 62 | 36 | 0 | 0
2022-10-25 02:00 | 10 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 35 | 35 | 39 | 39 | 53 | 33 | 61 | 34 | 0 | 0
2022-10-25 03:00 | 10 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 35 | 36 | 39 | 40 | 54 | 32 | 61 | 34 | 0 | 0
2022-10-25 04:00 | 10 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 32 | 36 | 39 | 43 | 54 | 33 | 59 | 34 | 0 | 0
2022-10-25 05:00 | 10 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 29 | 36 | 38 | 43 | 55 | 34 | 57 | 33 | 0 | 0
2022-10-25 06:00 | 10 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 30 | 36 | 38 | 42 | 56 | 33 | 55 | 33 | 0 | 0
2022-10-25 07:00 | 10 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 34 | 36 | 42 | 43 | 56 | 32 | 57 | 37 | 0 | 0
2022-10-25 08:00 | 10 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 38 | 36 | 46 | 44 | 57 | 38 | 59 | 45 | 0 | 0
2022-10-25 09:00 | 10 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 42 | 39 | 50 | 47 | 58 | 45 | 60 | 50 | 0 | 0
2022-10-25 10:00 | 10 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 47 | 38 | 53 | 49 | 61 | 50 | 61 | 52 | 0 | 0
2022-10-25 11:00 | 10 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 49 | 41 | 56 | 52 | 65 | 53 | 60 | 55 | 0 | 0
2022-10-25 12:00 | 10 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 52 | 41 | 59 | 51 | 67 | 54 | 61 | 59 | 0 | 0
2022-10-25 13:00 | 10 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 52 | 41 | 60 | 51 | 63 | 57 | 61 | 62 | 0 | 0
2022-10-25 14:00 | 10 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 52 | 40 | 60 | 52 | 61 | 56 | 61 | 63 | 0 | 0
2022-10-25 15:00 | 10 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 53 | 42 | 61 | 52 | 59 | 55 | 60 | 63 | 0 | 0
2022-10-25 16:00 | 10 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 51 | 40 | 61 | 51 | 54 | 54 | 57 | 63 | 0 | 0
2022-10-25 17:00 | 10 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 50 | 39 | 61 | 51 | 51 | 52 | 54 | 62 | 0 | 0
2022-10-25 18:00 | 10 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 50 | 33 | 61 | 51 | 49 | 50 | 52 | 63 | 0 | 0
2022-10-25 19:00 | 10 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 50 | 32 | 58 | 50 | 46 | 50 | 48 | 62 | 0 | 0
2022-10-25 20:00 | 10 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 49 | 30 | 56 | 51 | 46 | 49 | 46 | 62 | 0 | 0
2022-10-25 21:00 | 10 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 47 | 27 | 53 | 51 | 46 | 49 | 46 | 60 | 0 | 0
2022-10-25 22:00 | 10 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 48 | 26 | 54 | 51 | 46 | 49 | 45 | 60 | 0 | 0
2022-10-25 23:00 | 10 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 47 | 25 | 55 | 51 | 44 | 50 | 46 | 60 | 0 | 0
2022-10-26 | 10 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 47 | 24 | 56 | 50 | 42 | 50 | 46 | 60 | 0 | 0
2022-10-26 01:00 | 10 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 46 | 23 | 56 | 49 | 43 | 50 | 43 | 60 | 0 | 0
2022-10-26 02:00 | 10 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 46 | 23 | 57 | 49 | 43 | 50 | 44 | 59 | 0 | 0
2022-10-26 03:00 | 10 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 46 | 22 | 57 | 49 | 42 | 50 | 42 | 58 | 0 | 0
2022-10-26 04:00 | 10 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 45 | 21 | 57 | 49 | 40 | 50 | 41 | 56 | 0 | 0
2022-10-26 05:00 | 10 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 45 | 23 | 58 | 50 | 40 | 51 | 40 | 56 | 0 | 0
2022-10-26 06:00 | 10 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 46 | 20 | 58 | 50 | 40 | 51 | 40 | 56 | 0 | 0
2022-10-26 07:00 | 10 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 46 | 26 | 57 | 49 | 42 | 52 | 44 | 56 | 0 | 0
2022-10-26 08:00 | 10 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 47 | 32 | 57 | 50 | 44 | 53 | 49 | 57 | 0 | 0
2022-10-26 09:00 | 10 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 47 | 39 | 56 | 51 | 45 | 54 | 51 | 57 | 0 | 0
2022-10-26 10:00 | 10 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 48 | 44 | 54 | 52 | 48 | 55 | 55 | 57 | 0 | 0
2022-10-26 11:00 | 10 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 49 | 47 | 52 | 53 | 47 | 56 | 58 | 57 | 0 | 0
2022-10-26 12:00 | 10 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 49 | 51 | 50 | 54 | 48 | 56 | 60 | 58 | 0 | 0
2022-10-26 13:00 | 10 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 49 | 52 | 48 | 53 | 47 | 58 | 61 | 58 | 0 | 0
2022-10-26 14:00 | 10 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 50 | 53 | 47 | 53 | 47 | 57 | 62 | 59 | 0 | 0
2022-10-26 15:00 | 10 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 49 | 53 | 45 | 53 | 47 | 58 | 61 | 60 | 0 | 0
2022-10-26 16:00 | 10 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 49 | 49 | 45 | 52 | 46 | 57 | 60 | 62 | 0 | 0
2022-10-26 17:00 | 10 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 49 | 47 | 46 | 52 | 45 | 57 | 56 | 61 | 0 | 0
2022-10-26 18:00 | 10 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 49 | 45 | 46 | 53 | 44 | 57 | 52 | 62 | 0 | 0
2022-10-26 19:00 | 10 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 48 | 44 | 46 | 52 | 43 | 58 | 52 | 59 | 0 | 0
2022-10-26 20:00 | 10 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 48 | 43 | 46 | 53 | 43 | 58 | 53 | 59 | 0 | 0
2022-10-26 21:00 | 10 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 48 | 42 | 46 | 53 | 43 | 58 | 49 | 60 | 0 | 0
2022-10-26 22:00 | 10 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 48 | 41 | 45 | 52 | 42 | 59 | 49 | 59 | 0 | 0
2022-10-26 23:00 | 10 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 48 | 41 | 45 | 53 | 42 | 59 | 44 | 56 | 0 | 0
2022-10-27 | 10 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 48 | 41 | 44 | 52 | 43 | 59 | 48 | 54 | 0 | 0
2022-10-27 01:00 | 10 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 48 | 41 | 44 | 52 | 42 | 59 | 40 | 53 | 0 | 0
2022-10-27 02:00 | 10 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 48 | 41 | 44 | 52 | 42 | 59 | 41 | 51 | 0 | 0
2022-10-27 03:00 | 10 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 48 | 41 | 44 | 52 | 42 | 59 | 40 | 49 | 0 | 0
2022-10-27 04:00 | 10 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 48 | 40 | 44 | 51 | 42 | 58 | 42 | 47 | 0 | 0
2022-10-27 05:00 | 10 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 48 | 41 | 44 | 52 | 42 | 58 | 43 | 46 | 0 | 0
2022-10-27 06:00 | 10 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 49 | 41 | 44 | 52 | 40 | 59 | 43 | 48 | 0 | 0
2022-10-27 07:00 | 10 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 49 | 42 | 45 | 51 | 43 | 60 | 48 | 50 | 0 | 0
2022-10-27 08:00 | 10 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 51 | 43 | 45 | 53 | 46 | 61 | 54 | 50 | 0 | 0
2022-10-27 09:00 | 10 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 52 | 47 | 46 | 53 | 47 | 62 | 57 | 52 | 0 | 0
2022-10-27 10:00 | 10 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 53 | 46 | 48 | 55 | 49 | 62 | 62 | 55 | 0 | 0
2022-10-27 11:00 | 10 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 53 | 44 | 51 | 57 | 49 | 62 | 65 | 56 | 0 | 0
2022-10-27 12:00 | 10 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 55 | 42 | 53 | 58 | 49 | 61 | 69 | 58 | 0 | 0
2022-10-27 13:00 | 10 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 56 | 42 | 53 | 59 | 51 | 62 | 70 | 57 | 0 | 0
2022-10-27 14:00 | 10 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 57 | 41 | 53 | 60 | 51 | 62 | 70 | 58 | 0 | 0
2022-10-27 15:00 | 10 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 57 | 42 | 53 | 59 | 49 | 62 | 68 | 58 | 0 | 0
2022-10-27 16:00 | 10 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 56 | 42 | 52 | 57 | 46 | 62 | 66 | 54 | 0 | 0
2022-10-27 17:00 | 10 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 57 | 42 | 50 | 56 | 46 | 60 | 64 | 52 | 0 | 0
2022-10-27 18:00 | 10 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 53 | 41 | 49 | 55 | 46 | 57 | 62 | 46 | 0 | 0
2022-10-27 19:00 | 10 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 52 | 41 | 48 | 53 | 45 | 54 | 61 | 44 | 0 | 0
2022-10-27 20:00 | 10 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 53 | 41 | 48 | 53 | 45 | 52 | 58 | 43 | 0 | 0
2022-10-27 21:00 | 10 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 52 | 40 | 47 | 53 | 45 | 51 | 56 | 42 | 0 | 0
2022-10-27 22:00 | 10 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 51 | 39 | 46 | 53 | 46 | 51 | 52 | 40 | 0 | 0
2022-10-27 23:00 | 10 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 51 | 39 | 46 | 53 | 46 | 50 | 49 | 39 | 0 | 0
2022-10-28 | 10 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 51 | 38 | 45 | 53 | 46 | 50 | 47 | 38 | 0 | 0
2022-10-28 01:00 | 10 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 51 | 37 | 45 | 53 | 46 | 50 | 46 | 37 | 0 | 0
2022-10-28 02:00 | 10 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 51 | 36 | 44 | 51 | 46 | 51 | 44 | 35 | 0 | 0
2022-10-28 03:00 | 10 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 51 | 34 | 44 | 51 | 47 | 51 | 43 | 35 | 0 | 0
2022-10-28 04:00 | 10 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 51 | 33 | 43 | 52 | 48 | 51 | 42 | 35 | 0 | 0
2022-10-28 05:00 | 10 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 51 | 32 | 43 | 51 | 49 | 51 | 41 | 36 | 0 | 0
2022-10-28 06:00 | 10 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 50 | 30 | 42 | 52 | 49 | 50 | 41 | 36 | 0 | 0
2022-10-28 07:00 | 10 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 50 | 34 | 44 | 55 | 51 | 50 | 42 | 36 | 0 | 0
2022-10-28 08:00 | 10 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 51 | 37 | 47 | 59 | 52 | 50 | 43 | 37 | 0 | 0
2022-10-28 09:00 | 10 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 51 | 41 | 49 | 61 | 53 | 51 | 44 | 40 | 0 | 0
2022-10-28 10:00 | 10 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 52 | 41 | 49 | 63 | 53 | 51 | 45 | 46 | 0 | 0
2022-10-28 11:00 | 10 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 53 | 41 | 48 | 63 | 54 | 52 | 47 | 54 | 0 | 0
2022-10-28 12:00 | 10 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 54 | 42 | 48 | 64 | 54 | 55 | 48 | 58 | 0 | 0
2022-10-28 13:00 | 10 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 56 | 37 | 48 | 64 | 54 | 56 | 49 | 61 | 0 | 0
2022-10-28 14:00 | 10 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 56 | 37 | 49 | 66 | 55 | 58 | 48 | 63 | 0 | 0
2022-10-28 15:00 | 10 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 57 | 38 | 49 | 65 | 55 | 58 | 46 | 65 | 0 | 0
2022-10-28 16:00 | 10 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 55 | 37 | 48 | 62 | 53 | 57 | 44 | 61 | 0 | 0
2022-10-28 17:00 | 10 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 52 | 37 | 46 | 57 | 53 | 53 | 41 | 58 | 0 | 0
2022-10-28 18:00 | 10 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 50 | 36 | 45 | 53 | 53 | 53 | 39 | 55 | 0 | 0
2022-10-28 19:00 | 10 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 49 | 33 | 44 | 51 | 51 | 52 | 37 | 52 | 0 | 0
2022-10-28 20:00 | 10 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 50 | 32 | 42 | 51 | 50 | 49 | 35 | 52 | 0 | 0
2022-10-28 21:00 | 10 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 48 | 32 | 41 | 47 | 47 | 47 | 34 | 54 | 0 | 0
2022-10-28 22:00 | 10 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 48 | 30 | 40 | 45 | 47 | 45 | 33 | 50 | 0 | 0
2022-10-28 23:00 | 10 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 48 | 30 | 39 | 42 | 45 | 43 | 32 | 47 | 0 | 0
2022-10-29 | 10 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 48 | 28 | 38 | 43 | 43 | 43 | 32 | 46 | 0 | 0
2022-10-29 01:00 | 10 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 48 | 31 | 36 | 41 | 42 | 42 | 32 | 44 | 0 | 0
2022-10-29 02:00 | 10 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 47 | 32 | 35 | 41 | 42 | 41 | 31 | 43 | 0 | 0
2022-10-29 03:00 | 10 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 49 | 32 | 33 | 39 | 40 | 39 | 29 | 42 | 0 | 0
2022-10-29 04:00 | 10 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 47 | 32 | 32 | 38 | 37 | 38 | 27 | 40 | 0 | 0
2022-10-29 05:00 | 10 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 47 | 32 | 32 | 38 | 36 | 38 | 26 | 40 | 0 | 0
2022-10-29 06:00 | 10 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 47 | 33 | 31 | 37 | 37 | 38 | 27 | 38 | 0 | 0
2022-10-29 07:00 | 10 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 49 | 33 | 35 | 41 | 37 | 39 | 31 | 40 | 0 | 0
2022-10-29 08:00 | 10 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 52 | 34 | 40 | 46 | 44 | 40 | 34 | 46 | 0 | 0
2022-10-29 09:00 | 10 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 55 | 33 | 44 | 53 | 45 | 42 | 39 | 49 | 0 | 0
2022-10-29 10:00 | 10 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 59 | 34 | 45 | 60 | 46 | 48 | 41 | 52 | 0 | 0
2022-10-29 11:00 | 10 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 62 | 37 | 47 | 63 | 47 | 52 | 43 | 53 | 0 | 0
2022-10-29 12:00 | 10 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 64 | 36 | 48 | 68 | 51 | 54 | 46 | 55 | 0 | 0
2022-10-29 13:00 | 10 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 66 | 34 | 47 | 69 | 50 | 55 | 49 | 55 | 0 | 0
2022-10-29 14:00 | 10 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 64 | 36 | 46 | 69 | 49 | 57 | 50 | 57 | 0 | 0
2022-10-29 15:00 | 10 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 63 | 34 | 45 | 68 | 46 | 56 | 48 | 56 | 0 | 0
2022-10-29 16:00 | 10 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 61 | 34 | 43 | 64 | 45 | 55 | 45 | 54 | 0 | 0
2022-10-29 17:00 | 10 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 60 | 33 | 40 | 63 | 44 | 50 | 43 | 49 | 0 | 0
2022-10-29 18:00 | 10 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 58 | 33 | 38 | 61 | 42 | 50 | 38 | 47 | 0 | 0
2022-10-29 19:00 | 10 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 59 | 32 | 38 | 60 | 42 | 48 | 37 | 43 | 0 | 0
2022-10-29 20:00 | 10 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 58 | 32 | 37 | 57 | 37 | 46 | 37 | 44 | 0 | 0
2022-10-29 21:00 | 10 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 55 | 32 | 37 | 57 | 37 | 45 | 35 | 41 | 0 | 0
2022-10-29 22:00 | 10 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 53 | 31 | 37 | 53 | 40 | 44 | 36 | 39 | 0 | 0
2022-10-29 23:00 | 10 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 53 | 32 | 37 | 52 | 39 | 43 | 34 | 38 | 0 | 0
2022-10-30 | 10 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 54 | 32 | 37 | 49 | 39 | 42 | 34 | 37 | 0 | 0
2022-10-30 01:00 | 10 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 51 | 32 | 37 | 49 | 38 | 42 | 32 | 36 | 0 | 0
2022-10-30 02:00 | 10 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 50 | 32 | 37 | 47 | 37 | 41 | 30 | 35 | 0 | 0
2022-10-30 03:00 | 10 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 47 | 32 | 37 | 49 | 37 | 40 | 31 | 34 | 0 | 0
2022-10-30 04:00 | 10 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 46 | 31 | 36 | 50 | 37 | 40 | 31 | 34 | 0 | 0
2022-10-30 05:00 | 10 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 45 | 30 | 36 | 50 | 37 | 40 | 33 | 32 | 0 | 0
2022-10-30 06:00 | 10 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 44 | 33 | 35 | 52 | 36 | 40 | 35 | 32 | 0 | 0
2022-10-30 07:00 | 10 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 44 | 35 | 39 | 57 | 39 | 42 | 36 | 33 | 0 | 0
2022-10-30 08:00 | 10 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 45 | 35 | 43 | 58 | 46 | 46 | 38 | 36 | 0 | 0
2022-10-30 09:00 | 10 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 44 | 37 | 47 | 59 | 48 | 51 | 39 | 41 | 0 | 0
2022-10-30 10:00 | 10 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 44 | 41 | 51 | 61 | 48 | 55 | 43 | 49 | 0 | 0
2022-10-30 11:00 | 10 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 44 | 42 | 54 | 62 | 51 | 59 | 44 | 53 | 0 | 0
2022-10-30 12:00 | 10 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 43 | 45 | 58 | 62 | 52 | 61 | 46 | 55 | 0 | 0
2022-10-30 13:00 | 10 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 41 | 47 | 59 | 62 | 52 | 62 | 48 | 56 | 0 | 0
2022-10-30 14:00 | 10 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 41 | 51 | 59 | 62 | 53 | 63 | 49 | 57 | 0 | 0
2022-10-30 15:00 | 10 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 41 | 53 | 60 | 62 | 51 | 63 | 49 | 57 | 0 | 0
2022-10-30 16:00 | 10 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 40 | 51 | 57 | 58 | 48 | 60 | 49 | 55 | 0 | 0
2022-10-30 17:00 | 10 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 40 | 50 | 54 | 55 | 44 | 56 | 48 | 49 | 0 | 0
2022-10-30 18:00 | 10 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 38 | 50 | 51 | 53 | 43 | 54 | 47 | 51 | 0 | 0
2022-10-30 19:00 | 10 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 35 | 49 | 51 | 51 | 41 | 50 | 47 | 44 | 0 | 0
2022-10-30 20:00 | 10 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 33 | 50 | 50 | 50 | 40 | 48 | 47 | 47 | 0 | 0
2022-10-30 21:00 | 10 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 33 | 49 | 50 | 47 | 39 | 46 | 45 | 43 | 0 | 0
2022-10-30 22:00 | 10 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 34 | 47 | 49 | 46 | 38 | 44 | 44 | 43 | 0 | 0
2022-10-30 23:00 | 10 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 32 | 43 | 47 | 43 | 36 | 43 | 43 | 42 | 0 | 0
2022-10-31 | 10 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 33 | 41 | 46 | 42 | 35 | 42 | 44 | 41 | 0 | 0
2022-10-31 01:00 | 10 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 31 | 41 | 45 | 40 | 36 | 42 | 44 | 38 | 0 | 0
2022-10-31 02:00 | 10 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 29 | 38 | 45 | 39 | 36 | 41 | 44 | 36 | 0 | 0
2022-10-31 03:00 | 10 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 29 | 38 | 44 | 38 | 38 | 40 | 45 | 37 | 0 | 0
2022-10-31 04:00 | 10 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 28 | 37 | 44 | 36 | 37 | 39 | 43 | 36 | 0 | 0
2022-10-31 05:00 | 10 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 26 | 40 | 44 | 35 | 36 | 39 | 44 | 36 | 0 | 0
2022-10-31 06:00 | 10 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 27 | 40 | 44 | 34 | 38 | 38 | 44 | 33 | 0 | 0
2022-10-31 07:00 | 10 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 30 | 40 | 48 | 38 | 40 | 41 | 45 | 35 | 0 | 0
2022-10-31 08:00 | 10 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 33 | 42 | 53 | 41 | 45 | 44 | 46 | 37 | 0 | 0
2022-10-31 09:00 | 10 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 38 | 43 | 57 | 44 | 49 | 50 | 47 | 39 | 0 | 0
2022-10-31 10:00 | 10 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 40 | 45 | 58 | 45 | 54 | 53 | 50 | 46 | 0 | 0
2022-10-31 11:00 | 10 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 45 | 49 | 59 | 47 | 56 | 56 | 55 | 54 | 0 | 0
2022-10-31 12:00 | 10 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 47 | 50 | 60 | 48 | 58 | 59 | 57 | 57 | 0 | 0
2022-10-31 13:00 | 10 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 49 | 53 | 58 | 50 | 60 | 61 | 57 | 59 | 0 | 0
2022-10-31 14:00 | 10 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 50 | 53 | 56 | 51 | 61 | 60 | 57 | 63 | 0 | 0
2022-10-31 15:00 | 10 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 49 | 54 | 54 | 51 | 60 | 62 | 55 | 63 | 0 | 0
2022-10-31 16:00 | 10 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 47 | 52 | 52 | 49 | 56 | 60 | 51 | 56 | 0 | 0
2022-10-31 17:00 | 10 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 44 | 45 | 50 | 45 | 53 | 55 | 48 | 54 | 0 | 0
2022-10-31 18:00 | 10 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 43 | 39 | 48 | 44 | 50 | 51 | 47 | 50 | 0 | 0
2022-10-31 19:00 | 10 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 42 | 38 | 48 | 41 | 49 | 50 | 46 | 47 | 0 | 0
2022-10-31 20:00 | 10 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 41 | 37 | 48 | 41 | 48 | 47 | 45 | 45 | 0 | 0
2022-10-31 21:00 | 10 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 39 | 37 | 47 | 40 | 49 | 46 | 45 | 44 | 0 | 0
2022-10-31 22:00 | 10 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 38 | 38 | 47 | 40 | 50 | 45 | 46 | 42 | 0 | 0
2022-10-31 23:00 | 10 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 36 | 38 | 46 | 39 | 51 | 44 | 46 | 41 | 0 | 0
2022-11-01 | 11 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 35 | 39 | 45 | 38 | 52 | 44 | 46 | 39 | 0 | 0
2022-11-01 01:00 | 11 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 33 | 39 | 44 | 37 | 53 | 43 | 46 | 38 | 0 | 0
2022-11-01 02:00 | 11 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 32 | 40 | 44 | 37 | 54 | 42 | 47 | 37 | 0 | 0
2022-11-01 03:00 | 11 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 30 | 40 | 43 | 36 | 55 | 41 | 47 | 35 | 0 | 0
2022-11-01 04:00 | 11 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 31 | 39 | 44 | 36 | 53 | 42 | 47 | 38 | 0 | 0
2022-11-01 05:00 | 11 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 33 | 40 | 43 | 35 | 54 | 42 | 47 | 38 | 0 | 0
2022-11-01 06:00 | 11 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 33 | 40 | 42 | 35 | 52 | 42 | 47 | 38 | 0 | 0
2022-11-01 07:00 | 11 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 34 | 42 | 45 | 39 | 52 | 43 | 48 | 41 | 0 | 0
2022-11-01 08:00 | 11 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 36 | 47 | 46 | 45 | 53 | 46 | 50 | 40 | 0 | 0
2022-11-01 09:00 | 11 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 39 | 49 | 48 | 49 | 55 | 49 | 50 | 42 | 0 | 0
2022-11-01 10:00 | 11 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 40 | 50 | 49 | 53 | 56 | 50 | 52 | 43 | 0 | 0
2022-11-01 11:00 | 11 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 41 | 50 | 49 | 59 | 57 | 53 | 54 | 44 | 0 | 0
2022-11-01 12:00 | 11 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 42 | 55 | 48 | 60 | 56 | 54 | 54 | 45 | 0 | 0
2022-11-01 13:00 | 11 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 42 | 56 | 49 | 63 | 58 | 55 | 56 | 46 | 0 | 0
2022-11-01 14:00 | 11 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 42 | 59 | 48 | 64 | 58 | 53 | 55 | 45 | 0 | 0
2022-11-01 15:00 | 11 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 42 | 59 | 45 | 62 | 56 | 52 | 55 | 46 | 0 | 0
2022-11-01 16:00 | 11 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 41 | 58 | 44 | 60 | 53 | 50 | 55 | 46 | 0 | 0
2022-11-01 17:00 | 11 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 40 | 57 | 44 | 58 | 50 | 49 | 51 | 44 | 0 | 0
2022-11-01 18:00 | 11 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 38 | 54 | 42 | 57 | 49 | 47 | 50 | 40 | 0 | 0
2022-11-01 19:00 | 11 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 38 | 54 | 42 | 57 | 50 | 44 | 51 | 38 | 0 | 0
2022-11-01 20:00 | 11 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 39 | 54 | 40 | 56 | 47 | 43 | 51 | 38 | 0 | 0
2022-11-01 21:00 | 11 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 39 | 54 | 40 | 56 | 46 | 41 | 49 | 37 | 0 | 0
2022-11-01 22:00 | 11 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 38 | 54 | 41 | 54 | 46 | 40 | 48 | 36 | 0 | 0
2022-11-01 23:00 | 11 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 38 | 54 | 41 | 54 | 45 | 38 | 44 | 36 | 0 | 0
2022-11-02 | 11 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 38 | 54 | 41 | 54 | 42 | 38 | 43 | 35 | 0 | 0
2022-11-02 01:00 | 11 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 38 | 54 | 40 | 54 | 43 | 37 | 41 | 35 | 0 | 0
2022-11-02 02:00 | 11 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 38 | 51 | 41 | 53 | 42 | 36 | 41 | 35 | 0 | 0
2022-11-02 03:00 | 11 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 36 | 46 | 41 | 52 | 44 | 37 | 41 | 35 | 0 | 0
2022-11-02 04:00 | 11 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 36 | 45 | 42 | 51 | 44 | 36 | 39 | 37 | 0 | 0
2022-11-02 05:00 | 11 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 36 | 43 | 42 | 50 | 44 | 37 | 39 | 38 | 0 | 0
2022-11-02 06:00 | 11 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 36 | 42 | 43 | 50 | 46 | 37 | 39 | 40 | 0 | 0
2022-11-02 07:00 | 11 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 34 | 41 | 43 | 52 | 48 | 38 | 40 | 41 | 0 | 0
2022-11-02 08:00 | 11 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 33 | 39 | 43 | 53 | 50 | 39 | 42 | 42 | 0 | 0
2022-11-02 09:00 | 11 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 34 | 38 | 43 | 54 | 53 | 41 | 44 | 44 | 0 | 0
2022-11-02 10:00 | 11 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 35 | 38 | 43 | 56 | 55 | 42 | 51 | 45 | 0 | 0
2022-11-02 11:00 | 11 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 35 | 38 | 43 | 56 | 56 | 43 | 59 | 46 | 0 | 0
2022-11-02 12:00 | 11 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 37 | 40 | 43 | 57 | 58 | 42 | 60 | 48 | 0 | 0
2022-11-02 13:00 | 11 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 35 | 40 | 44 | 60 | 58 | 41 | 63 | 49 | 0 | 0
2022-11-02 14:00 | 11 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 34 | 40 | 43 | 59 | 57 | 41 | 65 | 49 | 0 | 0
2022-11-02 15:00 | 11 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 37 | 40 | 43 | 57 | 56 | 41 | 66 | 48 | 0 | 0
2022-11-02 16:00 | 11 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 37 | 39 | 42 | 55 | 56 | 41 | 63 | 47 | 0 | 0
2022-11-02 17:00 | 11 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 37 | 35 | 42 | 53 | 55 | 41 | 60 | 46 | 0 | 0
2022-11-02 18:00 | 11 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 37 | 34 | 42 | 51 | 52 | 40 | 58 | 45 | 0 | 0
2022-11-02 19:00 | 11 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 36 | 30 | 41 | 50 | 51 | 41 | 57 | 45 | 0 | 0
2022-11-02 20:00 | 11 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 36 | 28 | 41 | 48 | 50 | 41 | 56 | 45 | 0 | 0
2022-11-02 21:00 | 11 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 36 | 28 | 41 | 46 | 50 | 40 | 54 | 44 | 0 | 0
2022-11-02 22:00 | 11 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 35 | 28 | 41 | 46 | 49 | 39 | 53 | 43 | 0 | 0
2022-11-02 23:00 | 11 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 35 | 25 | 41 | 45 | 49 | 38 | 52 | 42 | 0 | 0
2022-11-03 | 11 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 35 | 24 | 40 | 44 | 49 | 38 | 50 | 41 | 0 | 0
2022-11-03 01:00 | 11 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 34 | 24 | 40 | 44 | 50 | 36 | 48 | 40 | 0 | 0
2022-11-03 02:00 | 11 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 34 | 23 | 39 | 44 | 49 | 34 | 47 | 41 | 0 | 0
2022-11-03 03:00 | 11 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 33 | 23 | 39 | 45 | 49 | 33 | 46 | 41 | 0 | 0
2022-11-03 04:00 | 11 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 33 | 22 | 39 | 44 | 49 | 34 | 44 | 40 | 0 | 0
2022-11-03 05:00 | 11 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 33 | 23 | 39 | 42 | 49 | 32 | 42 | 38 | 0 | 0
2022-11-03 06:00 | 11 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 33 | 22 | 38 | 42 | 48 | 31 | 41 | 36 | 0 | 0
2022-11-03 07:00 | 11 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 33 | 24 | 38 | 46 | 48 | 31 | 43 | 39 | 0 | 0
2022-11-03 08:00 | 11 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 34 | 32 | 41 | 49 | 49 | 37 | 46 | 41 | 0 | 0
2022-11-03 09:00 | 11 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 38 | 39 | 44 | 50 | 50 | 42 | 48 | 45 | 0 | 0
2022-11-03 10:00 | 11 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 40 | 41 | 46 | 53 | 50 | 48 | 50 | 47 | 0 | 0
2022-11-03 11:00 | 11 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 43 | 42 | 49 | 55 | 50 | 50 | 53 | 49 | 0 | 0
2022-11-03 12:00 | 11 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 46 | 46 | 51 | 56 | 50 | 52 | 55 | 52 | 0 | 0
2022-11-03 13:00 | 11 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 48 | 46 | 54 | 57 | 46 | 53 | 56 | 55 | 0 | 0
2022-11-03 14:00 | 11 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 48 | 47 | 55 | 59 | 47 | 56 | 57 | 56 | 0 | 0
2022-11-03 15:00 | 11 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 48 | 46 | 54 | 60 | 45 | 54 | 56 | 56 | 0 | 0
2022-11-03 16:00 | 11 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 45 | 45 | 52 | 58 | 44 | 52 | 54 | 47 | 0 | 0
2022-11-03 17:00 | 11 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 45 | 44 | 51 | 52 | 42 | 50 | 51 | 45 | 0 | 0
2022-11-03 18:00 | 11 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 43 | 44 | 50 | 50 | 38 | 51 | 46 | 40 | 0 | 0
2022-11-03 19:00 | 11 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 41 | 43 | 50 | 48 | 38 | 49 | 46 | 38 | 0 | 0
2022-11-03 20:00 | 11 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 41 | 43 | 51 | 48 | 40 | 49 | 43 | 38 | 0 | 0
2022-11-03 21:00 | 11 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 40 | 43 | 52 | 47 | 39 | 50 | 42 | 34 | 0 | 0
2022-11-03 22:00 | 11 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 40 | 41 | 47 | 47 | 37 | 47 | 40 | 33 | 0 | 0
2022-11-03 23:00 | 11 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 39 | 41 | 47 | 46 | 37 | 46 | 39 | 33 | 0 | 0
2022-11-04 | 11 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 36 | 40 | 50 | 45 | 34 | 47 | 37 | 35 | 0 | 0
2022-11-04 01:00 | 11 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 36 | 40 | 51 | 44 | 34 | 48 | 37 | 34 | 0 | 0
2022-11-04 02:00 | 11 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 37 | 40 | 51 | 44 | 33 | 48 | 37 | 35 | 0 | 0
2022-11-04 03:00 | 11 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 36 | 40 | 51 | 44 | 33 | 50 | 35 | 37 | 0 | 0
2022-11-04 04:00 | 11 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 38 | 41 | 53 | 44 | 31 | 50 | 35 | 37 | 0 | 0
2022-11-04 05:00 | 11 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 39 | 41 | 55 | 43 | 31 | 50 | 34 | 38 | 0 | 0
2022-11-04 06:00 | 11 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 42 | 40 | 56 | 40 | 31 | 50 | 33 | 37 | 0 | 0
2022-11-04 07:00 | 11 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 42 | 40 | 57 | 43 | 35 | 52 | 36 | 39 | 0 | 0
2022-11-04 08:00 | 11 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 42 | 40 | 59 | 50 | 39 | 55 | 40 | 43 | 0 | 0
2022-11-04 09:00 | 11 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 44 | 37 | 59 | 60 | 41 | 59 | 47 | 44 | 0 | 0
2022-11-04 10:00 | 11 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 50 | 36 | 61 | 66 | 44 | 62 | 53 | 49 | 0 | 0
2022-11-04 11:00 | 11 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 70 | 54 | 38 | 64 | 68 | 46 | 65 | 57 | 51 | 0 | 0
2022-11-04 12:00 | 11 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 72 | 59 | 40 | 66 | 73 | 47 | 68 | 61 | 55 | 0 | 0
2022-11-04 13:00 | 11 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 62 | 42 | 63 | 75 | 48 | 70 | 63 | 57 | 0 | 0
2022-11-04 14:00 | 11 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 73 | 60 | 42 | 65 | 74 | 48 | 69 | 63 | 60 | 0 | 0
2022-11-04 15:00 | 11 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 71 | 61 | 40 | 64 | 75 | 47 | 70 | 63 | 60 | 0 | 0
2022-11-04 16:00 | 11 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 67 | 58 | 37 | 63 | 71 | 44 | 69 | 60 | 55 | 0 | 0
2022-11-04 17:00 | 11 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 56 | 35 | 62 | 71 | 43 | 63 | 55 | 59 | 0 | 0
2022-11-04 18:00 | 11 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 66 | 55 | 33 | 62 | 71 | 40 | 66 | 55 | 54 | 0 | 0
2022-11-04 19:00 | 11 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 54 | 32 | 62 | 70 | 41 | 65 | 49 | 53 | 0 | 0
2022-11-04 20:00 | 11 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 54 | 30 | 62 | 67 | 40 | 63 | 47 | 57 | 0 | 0
2022-11-04 21:00 | 11 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 53 | 29 | 61 | 60 | 40 | 62 | 46 | 52 | 0 | 0
2022-11-04 22:00 | 11 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 54 | 28 | 61 | 58 | 39 | 59 | 45 | 56 | 0 | 0
2022-11-04 23:00 | 11 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 54 | 28 | 61 | 57 | 38 | 59 | 44 | 60 | 0 | 0
2022-11-05 | 11 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 54 | 28 | 61 | 53 | 40 | 60 | 42 | 59 | 0 | 0
2022-11-05 01:00 | 11 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 55 | 28 | 61 | 50 | 38 | 60 | 42 | 60 | 0 | 0
2022-11-05 02:00 | 11 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 57 | 28 | 61 | 52 | 38 | 62 | 42 | 59 | 0 | 0
2022-11-05 03:00 | 11 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 56 | 28 | 61 | 52 | 38 | 62 | 41 | 59 | 0 | 0
2022-11-05 04:00 | 11 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 56 | 29 | 62 | 51 | 36 | 63 | 39 | 59 | 0 | 0
2022-11-05 05:00 | 11 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 55 | 29 | 62 | 51 | 39 | 63 | 38 | 60 | 0 | 0
2022-11-05 06:00 | 11 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 56 | 30 | 62 | 55 | 40 | 63 | 36 | 60 | 0 | 0
2022-11-05 07:00 | 11 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 56 | 30 | 63 | 61 | 44 | 61 | 40 | 61 | 0 | 0
2022-11-05 08:00 | 11 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 57 | 30 | 64 | 63 | 47 | 61 | 47 | 62 | 0 | 0
2022-11-05 09:00 | 11 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 58 | 31 | 65 | 58 | 51 | 61 | 53 | 63 | 0 | 0
2022-11-05 10:00 | 11 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 58 | 31 | 65 | 58 | 57 | 61 | 57 | 63 | 0 | 0
2022-11-05 11:00 | 11 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 60 | 32 | 63 | 58 | 59 | 55 | 60 | 62 | 0 | 0
2022-11-05 12:00 | 11 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 58 | 33 | 63 | 57 | 59 | 53 | 64 | 62 | 0 | 0
2022-11-05 13:00 | 11 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 57 | 33 | 55 | 57 | 58 | 55 | 67 | 62 | 0 | 0
2022-11-05 14:00 | 11 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 57 | 33 | 54 | 57 | 58 | 56 | 67 | 63 | 0 | 0
2022-11-05 15:00 | 11 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 57 | 33 | 55 | 53 | 57 | 53 | 64 | 61 | 0 | 0
2022-11-05 16:00 | 11 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 57 | 33 | 54 | 52 | 54 | 52 | 62 | 55 | 0 | 0
2022-11-05 17:00 | 11 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 57 | 33 | 51 | 50 | 52 | 51 | 60 | 55 | 0 | 0
2022-11-05 18:00 | 11 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 57 | 34 | 49 | 49 | 51 | 50 | 59 | 52 | 0 | 0
2022-11-05 19:00 | 11 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 52 | 34 | 49 | 45 | 49 | 49 | 59 | 50 | 0 | 0
2022-11-05 20:00 | 11 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 53 | 35 | 49 | 43 | 49 | 49 | 57 | 48 | 0 | 0
2022-11-05 21:00 | 11 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 50 | 35 | 50 | 44 | 48 | 49 | 58 | 50 | 0 | 0
2022-11-05 22:00 | 11 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 52 | 34 | 49 | 43 | 47 | 47 | 56 | 51 | 0 | 0
2022-11-05 23:00 | 11 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 50 | 35 | 48 | 41 | 48 | 47 | 55 | 50 | 0 | 0
2022-11-06 | 11 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 50 | 35 | 48 | 41 | 47 | 48 | 51 | 51 | 0 | 0
2022-11-06 01:00 | 11 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 48 | 35 | 48 | 39 | 46 | 48 | 50 | 50 | 0 | 0
2022-11-06 02:00 | 11 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 47 | 35 | 48 | 38 | 45 | 47 | 50 | 51 | 0 | 0
2022-11-06 03:00 | 11 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 47 | 35 | 47 | 37 | 47 | 45 | 50 | 51 | 0 | 0
2022-11-06 04:00 | 11 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 46 | 35 | 45 | 38 | 49 | 41 | 51 | 50 | 0 | 0
2022-11-06 05:00 | 11 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 45 | 35 | 44 | 38 | 53 | 41 | 51 | 50 | 0 | 0
2022-11-06 06:00 | 11 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 45 | 36 | 42 | 38 | 55 | 39 | 51 | 49 | 0 | 0
2022-11-06 07:00 | 11 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 46 | 37 | 41 | 39 | 56 | 40 | 51 | 50 | 0 | 0
2022-11-06 08:00 | 11 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 48 | 38 | 43 | 39 | 57 | 40 | 52 | 50 | 0 | 0
2022-11-06 09:00 | 11 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 50 | 40 | 44 | 42 | 59 | 41 | 53 | 52 | 0 | 0
2022-11-06 10:00 | 11 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 51 | 40 | 40 | 44 | 60 | 39 | 53 | 53 | 0 | 0
2022-11-06 11:00 | 11 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 52 | 44 | 42 | 45 | 60 | 40 | 53 | 55 | 0 | 0
2022-11-06 12:00 | 11 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 51 | 46 | 41 | 46 | 59 | 38 | 51 | 55 | 0 | 0
2022-11-06 13:00 | 11 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 51 | 46 | 41 | 45 | 60 | 40 | 51 | 56 | 0 | 0
2022-11-06 14:00 | 11 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 52 | 47 | 39 | 46 | 60 | 40 | 51 | 56 | 0 | 0
2022-11-06 15:00 | 11 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 52 | 48 | 39 | 44 | 60 | 39 | 50 | 48 | 0 | 0
2022-11-06 16:00 | 11 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 51 | 44 | 40 | 42 | 59 | 38 | 47 | 46 | 0 | 0
2022-11-06 17:00 | 11 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 45 | 37 | 39 | 41 | 55 | 37 | 44 | 46 | 0 | 0
2022-11-06 18:00 | 11 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 42 | 36 | 35 | 39 | 54 | 37 | 43 | 46 | 0 | 0
2022-11-06 19:00 | 11 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 42 | 34 | 34 | 37 | 55 | 34 | 41 | 45 | 0 | 0
2022-11-06 20:00 | 11 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 41 | 31 | 35 | 37 | 51 | 33 | 39 | 45 | 0 | 0
2022-11-06 21:00 | 11 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 40 | 31 | 35 | 37 | 48 | 33 | 38 | 44 | 0 | 0
2022-11-06 22:00 | 11 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 41 | 31 | 35 | 33 | 48 | 33 | 38 | 44 | 0 | 0
2022-11-06 23:00 | 11 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 39 | 34 | 34 | 33 | 49 | 33 | 38 | 44 | 0 | 0
2022-11-07 | 11 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 38 | 32 | 35 | 36 | 46 | 33 | 36 | 43 | 0 | 0
2022-11-07 01:00 | 11 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 38 | 30 | 35 | 38 | 45 | 33 | 35 | 38 | 0 | 0
2022-11-07 02:00 | 11 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 37 | 32 | 34 | 38 | 46 | 33 | 35 | 37 | 0 | 0
2022-11-07 03:00 | 11 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 35 | 32 | 34 | 37 | 44 | 33 | 35 | 37 | 0 | 0
2022-11-07 04:00 | 11 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 34 | 35 | 35 | 36 | 46 | 33 | 35 | 37 | 0 | 0
2022-11-07 05:00 | 11 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 34 | 36 | 34 | 33 | 45 | 34 | 34 | 37 | 0 | 0
2022-11-07 06:00 | 11 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 32 | 36 | 36 | 31 | 45 | 33 | 33 | 37 | 0 | 0
2022-11-07 07:00 | 11 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 33 | 38 | 35 | 37 | 50 | 34 | 34 | 39 | 0 | 0
2022-11-07 08:00 | 11 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 34 | 40 | 37 | 42 | 53 | 34 | 34 | 39 | 0 | 0
2022-11-07 09:00 | 11 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 35 | 42 | 40 | 50 | 55 | 35 | 34 | 39 | 0 | 0
2022-11-07 10:00 | 11 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 35 | 43 | 40 | 53 | 55 | 36 | 34 | 41 | 0 | 0
2022-11-07 11:00 | 11 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 35 | 43 | 40 | 56 | 58 | 36 | 33 | 41 | 0 | 0
2022-11-07 12:00 | 11 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 35 | 45 | 41 | 58 | 59 | 39 | 33 | 41 | 0 | 0
2022-11-07 13:00 | 11 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 37 | 45 | 42 | 60 | 59 | 39 | 35 | 41 | 0 | 0
2022-11-07 14:00 | 11 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 36 | 45 | 42 | 61 | 57 | 39 | 39 | 41 | 0 | 0
2022-11-07 15:00 | 11 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 36 | 44 | 42 | 61 | 56 | 40 | 42 | 41 | 0 | 0
2022-11-07 16:00 | 11 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 36 | 44 | 43 | 56 | 55 | 40 | 41 | 40 | 0 | 0
2022-11-07 17:00 | 11 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 37 | 44 | 40 | 54 | 55 | 40 | 40 | 40 | 0 | 0
2022-11-07 18:00 | 11 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 36 | 43 | 40 | 51 | 55 | 40 | 40 | 40 | 0 | 0
2022-11-07 19:00 | 11 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 35 | 44 | 41 | 48 | 56 | 40 | 40 | 41 | 0 | 0
2022-11-07 20:00 | 11 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 35 | 44 | 41 | 46 | 56 | 40 | 40 | 41 | 0 | 0
2022-11-07 21:00 | 11 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 35 | 45 | 42 | 45 | 57 | 38 | 40 | 41 | 0 | 0
2022-11-07 22:00 | 11 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 36 | 44 | 41 | 46 | 57 | 36 | 40 | 41 | 0 | 0
2022-11-07 23:00 | 11 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 36 | 44 | 42 | 43 | 57 | 36 | 40 | 41 | 0 | 0
2022-11-08 | 11 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 36 | 45 | 41 | 44 | 57 | 35 | 39 | 40 | 0 | 0
2022-11-08 01:00 | 11 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 33 | 45 | 40 | 46 | 57 | 34 | 38 | 40 | 0 | 0
2022-11-08 02:00 | 11 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 33 | 45 | 40 | 44 | 53 | 35 | 38 | 40 | 0 | 0
2022-11-08 03:00 | 11 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 33 | 45 | 39 | 46 | 53 | 36 | 37 | 40 | 0 | 0
2022-11-08 04:00 | 11 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 35 | 45 | 41 | 43 | 52 | 36 | 32 | 40 | 0 | 0
2022-11-08 05:00 | 11 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 36 | 45 | 42 | 43 | 52 | 37 | 34 | 40 | 0 | 0
2022-11-08 06:00 | 11 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 36 | 46 | 42 | 43 | 51 | 39 | 32 | 38 | 0 | 0
2022-11-08 07:00 | 11 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 37 | 47 | 41 | 42 | 55 | 40 | 35 | 41 | 0 | 0
2022-11-08 08:00 | 11 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 38 | 48 | 42 | 49 | 57 | 42 | 38 | 43 | 0 | 0
2022-11-08 09:00 | 11 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 41 | 50 | 42 | 53 | 58 | 45 | 42 | 44 | 0 | 0
2022-11-08 10:00 | 11 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 41 | 50 | 43 | 58 | 59 | 48 | 45 | 45 | 0 | 0
2022-11-08 11:00 | 11 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 42 | 52 | 44 | 62 | 62 | 50 | 49 | 45 | 0 | 0
2022-11-08 12:00 | 11 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 41 | 55 | 45 | 65 | 63 | 50 | 51 | 43 | 0 | 0
2022-11-08 13:00 | 11 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 40 | 56 | 46 | 67 | 65 | 50 | 54 | 44 | 0 | 0
2022-11-08 14:00 | 11 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 39 | 57 | 46 | 68 | 61 | 51 | 54 | 44 | 0 | 0
2022-11-08 15:00 | 11 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 40 | 60 | 46 | 66 | 57 | 46 | 55 | 45 | 0 | 0
2022-11-08 16:00 | 11 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 40 | 61 | 45 | 64 | 56 | 45 | 53 | 45 | 0 | 0
2022-11-08 17:00 | 11 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 40 | 61 | 45 | 65 | 56 | 45 | 49 | 44 | 0 | 0
2022-11-08 18:00 | 11 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 40 | 61 | 44 | 66 | 57 | 44 | 48 | 43 | 0 | 0
2022-11-08 19:00 | 11 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 40 | 61 | 44 | 64 | 57 | 43 | 47 | 41 | 0 | 0
2022-11-08 20:00 | 11 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 41 | 60 | 44 | 54 | 57 | 43 | 42 | 43 | 0 | 0
2022-11-08 21:00 | 11 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 41 | 59 | 44 | 51 | 57 | 42 | 45 | 44 | 0 | 0
2022-11-08 22:00 | 11 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 40 | 58 | 44 | 51 | 58 | 42 | 46 | 46 | 0 | 0
2022-11-08 23:00 | 11 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 40 | 58 | 44 | 62 | 58 | 42 | 43 | 46 | 0 | 0
2022-11-09 | 11 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 39 | 57 | 44 | 56 | 59 | 42 | 42 | 46 | 0 | 0
2022-11-09 01:00 | 11 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 39 | 56 | 44 | 56 | 60 | 41 | 44 | 45 | 0 | 0
2022-11-09 02:00 | 11 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 38 | 55 | 44 | 57 | 64 | 41 | 40 | 44 | 0 | 0
2022-11-09 03:00 | 11 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 38 | 55 | 43 | 58 | 64 | 41 | 41 | 43 | 0 | 0
2022-11-09 04:00 | 11 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 38 | 51 | 43 | 56 | 64 | 40 | 40 | 43 | 0 | 0
2022-11-09 05:00 | 11 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 38 | 48 | 43 | 55 | 64 | 40 | 39 | 44 | 0 | 0
2022-11-09 06:00 | 11 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 38 | 48 | 43 | 54 | 64 | 40 | 40 | 43 | 0 | 0
2022-11-09 07:00 | 11 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 38 | 48 | 42 | 53 | 64 | 40 | 42 | 43 | 0 | 0
2022-11-09 08:00 | 11 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 38 | 47 | 43 | 52 | 64 | 42 | 48 | 44 | 0 | 0
2022-11-09 09:00 | 11 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 40 | 47 | 44 | 53 | 65 | 43 | 49 | 45 | 0 | 0
2022-11-09 10:00 | 11 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 41 | 48 | 46 | 53 | 66 | 45 | 51 | 46 | 0 | 0
2022-11-09 11:00 | 11 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 42 | 51 | 48 | 55 | 58 | 47 | 48 | 48 | 0 | 0
2022-11-09 12:00 | 11 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 43 | 52 | 50 | 56 | 59 | 49 | 44 | 48 | 0 | 0
2022-11-09 13:00 | 11 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 43 | 53 | 50 | 55 | 58 | 51 | 42 | 48 | 0 | 0
2022-11-09 14:00 | 11 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 42 | 53 | 47 | 54 | 57 | 51 | 42 | 48 | 0 | 0
2022-11-09 15:00 | 11 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 42 | 50 | 47 | 54 | 58 | 51 | 41 | 49 | 0 | 0
2022-11-09 16:00 | 11 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 41 | 48 | 45 | 54 | 53 | 49 | 40 | 44 | 0 | 0
2022-11-09 17:00 | 11 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 39 | 45 | 46 | 53 | 51 | 47 | 39 | 41 | 0 | 0
2022-11-09 18:00 | 11 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 38 | 42 | 45 | 54 | 48 | 48 | 38 | 39 | 0 | 0
2022-11-09 19:00 | 11 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 36 | 39 | 48 | 54 | 46 | 48 | 36 | 37 | 0 | 0
2022-11-09 20:00 | 11 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 37 | 39 | 49 | 54 | 45 | 47 | 35 | 35 | 0 | 0
2022-11-09 21:00 | 11 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 36 | 37 | 48 | 53 | 48 | 47 | 35 | 35 | 0 | 0
2022-11-09 22:00 | 11 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 36 | 33 | 49 | 50 | 45 | 48 | 34 | 37 | 0 | 0
2022-11-09 23:00 | 11 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 37 | 32 | 49 | 47 | 43 | 49 | 34 | 38 | 0 | 0
2022-11-10 | 11 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 37 | 32 | 50 | 45 | 42 | 49 | 33 | 43 | 0 | 0
2022-11-10 01:00 | 11 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 39 | 31 | 51 | 43 | 44 | 47 | 32 | 42 | 0 | 0
2022-11-10 02:00 | 11 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 40 | 31 | 53 | 41 | 42 | 50 | 32 | 42 | 0 | 0
2022-11-10 03:00 | 11 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 39 | 30 | 53 | 39 | 40 | 52 | 30 | 42 | 0 | 0
2022-11-10 04:00 | 11 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 40 | 29 | 55 | 39 | 44 | 54 | 30 | 44 | 0 | 0
2022-11-10 05:00 | 11 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 39 | 29 | 61 | 39 | 40 | 56 | 29 | 45 | 0 | 0
2022-11-10 06:00 | 11 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 40 | 29 | 60 | 38 | 41 | 57 | 29 | 45 | 0 | 0
2022-11-10 07:00 | 11 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 41 | 29 | 57 | 37 | 45 | 62 | 30 | 47 | 0 | 0
2022-11-10 08:00 | 11 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 45 | 28 | 58 | 37 | 50 | 62 | 32 | 47 | 0 | 0
2022-11-10 09:00 | 11 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 48 | 29 | 52 | 36 | 55 | 59 | 36 | 48 | 0 | 0
2022-11-10 10:00 | 11 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 49 | 30 | 51 | 33 | 54 | 59 | 38 | 49 | 0 | 0
2022-11-10 11:00 | 11 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 50 | 30 | 49 | 33 | 54 | 53 | 41 | 50 | 0 | 0
2022-11-10 12:00 | 11 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 50 | 33 | 49 | 32 | 50 | 55 | 42 | 51 | 0 | 0
2022-11-10 13:00 | 11 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 49 | 35 | 48 | 32 | 55 | 55 | 41 | 52 | 0 | 0
2022-11-10 14:00 | 11 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 50 | 35 | 49 | 32 | 54 | 54 | 41 | 52 | 0 | 0
2022-11-10 15:00 | 11 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 51 | 35 | 48 | 33 | 53 | 51 | 40 | 53 | 0 | 0
2022-11-10 16:00 | 11 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 51 | 33 | 47 | 32 | 49 | 50 | 40 | 55 | 0 | 0
2022-11-10 17:00 | 11 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 51 | 29 | 46 | 31 | 47 | 49 | 39 | 54 | 0 | 0
2022-11-10 18:00 | 11 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 48 | 29 | 46 | 30 | 48 | 48 | 39 | 52 | 0 | 0
2022-11-10 19:00 | 11 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 47 | 27 | 47 | 30 | 47 | 48 | 39 | 51 | 0 | 0
2022-11-10 20:00 | 11 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 46 | 26 | 47 | 28 | 45 | 48 | 39 | 51 | 0 | 0
2022-11-10 21:00 | 11 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 44 | 27 | 47 | 27 | 45 | 47 | 39 | 50 | 0 | 0
2022-11-10 22:00 | 11 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 44 | 27 | 44 | 27 | 43 | 44 | 39 | 50 | 0 | 0
2022-11-10 23:00 | 11 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 44 | 30 | 44 | 27 | 43 | 43 | 39 | 49 | 0 | 0
2022-11-11 | 11 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 43 | 29 | 43 | 27 | 40 | 41 | 39 | 48 | 0 | 0
2022-11-11 01:00 | 11 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 43 | 31 | 42 | 28 | 39 | 39 | 39 | 48 | 0 | 0
2022-11-11 02:00 | 11 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 41 | 33 | 42 | 28 | 42 | 38 | 39 | 44 | 0 | 0
2022-11-11 03:00 | 11 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 41 | 32 | 41 | 27 | 39 | 37 | 39 | 46 | 0 | 0
2022-11-11 04:00 | 11 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 40 | 30 | 41 | 27 | 39 | 36 | 39 | 43 | 0 | 0
2022-11-11 05:00 | 11 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 39 | 29 | 40 | 28 | 38 | 35 | 40 | 43 | 0 | 0
2022-11-11 06:00 | 11 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 38 | 29 | 40 | 27 | 37 | 34 | 40 | 41 | 0 | 0
2022-11-11 07:00 | 11 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 38 | 30 | 40 | 27 | 42 | 37 | 40 | 43 | 0 | 0
2022-11-11 08:00 | 11 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 38 | 31 | 40 | 28 | 46 | 37 | 41 | 46 | 0 | 0
2022-11-11 09:00 | 11 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 38 | 32 | 40 | 28 | 49 | 38 | 43 | 48 | 0 | 0
2022-11-11 10:00 | 11 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 37 | 32 | 41 | 28 | 53 | 39 | 46 | 48 | 0 | 0
2022-11-11 11:00 | 11 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 37 | 33 | 41 | 28 | 54 | 40 | 46 | 48 | 0 | 0
2022-11-11 12:00 | 11 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 37 | 33 | 42 | 28 | 55 | 42 | 47 | 49 | 0 | 0
2022-11-11 13:00 | 11 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 39 | 33 | 41 | 28 | 56 | 41 | 48 | 48 | 0 | 0
2022-11-11 14:00 | 11 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 37 | 33 | 41 | 28 | 54 | 41 | 47 | 47 | 0 | 0
2022-11-11 15:00 | 11 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 38 | 33 | 41 | 29 | 55 | 41 | 47 | 47 | 0 | 0
2022-11-11 16:00 | 11 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 36 | 33 | 40 | 28 | 55 | 40 | 46 | 45 | 0 | 0
2022-11-11 17:00 | 11 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 35 | 33 | 40 | 29 | 54 | 39 | 44 | 44 | 0 | 0
2022-11-11 18:00 | 11 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 35 | 33 | 40 | 29 | 54 | 38 | 44 | 44 | 0 | 0
2022-11-11 19:00 | 11 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 34 | 33 | 41 | 30 | 54 | 36 | 42 | 43 | 0 | 0
2022-11-11 20:00 | 11 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 32 | 32 | 40 | 31 | 55 | 37 | 42 | 42 | 0 | 0
2022-11-11 21:00 | 11 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 31 | 32 | 40 | 32 | 55 | 36 | 41 | 40 | 0 | 0
2022-11-11 22:00 | 11 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 31 | 32 | 39 | 33 | 54 | 31 | 39 | 39 | 0 | 0
2022-11-11 23:00 | 11 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 31 | 32 | 39 | 32 | 52 | 29 | 38 | 39 | 0 | 0
2022-11-12 | 11 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 32 | 32 | 38 | 31 | 53 | 29 | 38 | 39 | 0 | 0
2022-11-12 01:00 | 11 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 32 | 32 | 38 | 32 | 53 | 27 | 38 | 38 | 0 | 0
2022-11-12 02:00 | 11 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 32 | 29 | 38 | 32 | 52 | 26 | 37 | 38 | 0 | 0
2022-11-12 03:00 | 11 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 31 | 31 | 38 | 32 | 48 | 27 | 35 | 38 | 0 | 0
2022-11-12 04:00 | 11 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 31 | 31 | 37 | 33 | 47 | 26 | 35 | 36 | 0 | 0
2022-11-12 05:00 | 11 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 31 | 31 | 36 | 34 | 46 | 27 | 34 | 31 | 0 | 0
2022-11-12 06:00 | 11 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 30 | 31 | 35 | 34 | 43 | 27 | 32 | 29 | 0 | 0
2022-11-12 07:00 | 11 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 30 | 31 | 33 | 36 | 49 | 29 | 32 | 31 | 0 | 0
2022-11-12 08:00 | 11 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 31 | 32 | 37 | 37 | 54 | 33 | 33 | 36 | 0 | 0
2022-11-12 09:00 | 11 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 33 | 32 | 41 | 38 | 56 | 36 | 35 | 39 | 0 | 0
2022-11-12 10:00 | 11 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 36 | 33 | 44 | 39 | 58 | 42 | 36 | 41 | 0 | 0
2022-11-12 11:00 | 11 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 38 | 34 | 47 | 40 | 59 | 45 | 39 | 44 | 0 | 0
2022-11-12 12:00 | 11 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 40 | 35 | 49 | 41 | 58 | 48 | 40 | 44 | 0 | 0
2022-11-12 13:00 | 11 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 42 | 35 | 50 | 42 | 57 | 52 | 40 | 46 | 0 | 0
2022-11-12 14:00 | 11 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 44 | 35 | 51 | 43 | 56 | 53 | 41 | 46 | 0 | 0
2022-11-12 15:00 | 11 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 43 | 34 | 51 | 43 | 54 | 52 | 40 | 45 | 0 | 0
2022-11-12 16:00 | 11 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 39 | 33 | 50 | 42 | 53 | 50 | 38 | 44 | 0 | 0
2022-11-12 17:00 | 11 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 38 | 33 | 50 | 39 | 50 | 48 | 35 | 44 | 0 | 0
2022-11-12 18:00 | 11 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 38 | 33 | 50 | 40 | 46 | 48 | 34 | 43 | 0 | 0
2022-11-12 19:00 | 11 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 38 | 33 | 49 | 38 | 48 | 47 | 33 | 42 | 0 | 0
2022-11-12 20:00 | 11 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 37 | 32 | 47 | 38 | 48 | 47 | 32 | 41 | 0 | 0
2022-11-12 21:00 | 11 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 36 | 32 | 48 | 38 | 45 | 47 | 30 | 42 | 0 | 0
2022-11-12 22:00 | 11 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 37 | 32 | 48 | 35 | 45 | 46 | 29 | 42 | 0 | 0
2022-11-12 23:00 | 11 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 35 | 32 | 48 | 31 | 43 | 47 | 27 | 42 | 0 | 0
2022-11-13 | 11 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 36 | 30 | 48 | 31 | 42 | 47 | 26 | 42 | 0 | 0
2022-11-13 01:00 | 11 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 36 | 27 | 47 | 31 | 40 | 47 | 25 | 42 | 0 | 0
2022-11-13 02:00 | 11 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 37 | 24 | 44 | 29 | 38 | 46 | 25 | 43 | 0 | 0
2022-11-13 03:00 | 11 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 38 | 22 | 43 | 27 | 37 | 42 | 24 | 44 | 0 | 0
2022-11-13 04:00 | 11 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 39 | 21 | 42 | 29 | 36 | 42 | 23 | 45 | 0 | 0
2022-11-13 05:00 | 11 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 40 | 20 | 43 | 26 | 37 | 43 | 22 | 46 | 0 | 0
2022-11-13 06:00 | 11 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 42 | 18 | 44 | 25 | 37 | 44 | 22 | 45 | 0 | 0
2022-11-13 07:00 | 11 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 42 | 18 | 46 | 27 | 43 | 47 | 25 | 45 | 0 | 0
2022-11-13 08:00 | 11 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 44 | 18 | 47 | 33 | 48 | 49 | 28 | 46 | 0 | 0
2022-11-13 09:00 | 11 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 44 | 19 | 49 | 39 | 50 | 50 | 33 | 46 | 0 | 0
2022-11-13 10:00 | 11 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 45 | 20 | 48 | 44 | 53 | 51 | 37 | 47 | 0 | 0
2022-11-13 11:00 | 11 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 46 | 18 | 46 | 49 | 57 | 50 | 41 | 50 | 0 | 0
2022-11-13 12:00 | 11 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 47 | 19 | 46 | 51 | 60 | 47 | 45 | 48 | 0 | 0
2022-11-13 13:00 | 11 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 46 | 20 | 45 | 53 | 60 | 48 | 49 | 52 | 0 | 0
2022-11-13 14:00 | 11 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 48 | 18 | 46 | 52 | 59 | 48 | 50 | 52 | 0 | 0
2022-11-13 15:00 | 11 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 47 | 18 | 45 | 53 | 59 | 49 | 51 | 54 | 0 | 0
2022-11-13 16:00 | 11 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 46 | 18 | 45 | 47 | 56 | 48 | 47 | 52 | 0 | 0
2022-11-13 17:00 | 11 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 45 | 17 | 44 | 42 | 54 | 44 | 41 | 51 | 0 | 0
2022-11-13 18:00 | 11 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 45 | 17 | 42 | 39 | 53 | 42 | 40 | 50 | 0 | 0
2022-11-13 19:00 | 11 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 44 | 16 | 41 | 37 | 53 | 41 | 39 | 49 | 0 | 0
2022-11-13 20:00 | 11 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 43 | 15 | 42 | 38 | 50 | 41 | 37 | 47 | 0 | 0
2022-11-13 21:00 | 11 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 43 | 14 | 42 | 37 | 49 | 39 | 37 | 44 | 0 | 0
2022-11-13 22:00 | 11 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 40 | 14 | 42 | 36 | 49 | 39 | 39 | 40 | 0 | 0
2022-11-13 23:00 | 11 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 37 | 14 | 43 | 33 | 48 | 39 | 38 | 37 | 0 | 0
2022-11-14 | 11 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 37 | 13 | 44 | 33 | 50 | 39 | 38 | 35 | 0 | 0
2022-11-14 01:00 | 11 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 36 | 12 | 44 | 31 | 47 | 40 | 36 | 33 | 0 | 0
2022-11-14 02:00 | 11 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 35 | 13 | 44 | 31 | 49 | 40 | 36 | 33 | 0 | 0
2022-11-14 03:00 | 11 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 35 | 13 | 46 | 30 | 50 | 35 | 35 | 32 | 0 | 0
2022-11-14 04:00 | 11 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 35 | 12 | 46 | 30 | 47 | 36 | 34 | 31 | 0 | 0
2022-11-14 05:00 | 11 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 35 | 12 | 46 | 30 | 47 | 35 | 35 | 30 | 0 | 0
2022-11-14 06:00 | 11 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 35 | 12 | 46 | 32 | 53 | 35 | 33 | 32 | 0 | 0
2022-11-14 07:00 | 11 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 37 | 12 | 47 | 32 | 56 | 39 | 35 | 32 | 0 | 0
2022-11-14 08:00 | 11 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 42 | 13 | 49 | 39 | 59 | 45 | 38 | 32 | 0 | 0
2022-11-14 09:00 | 11 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 45 | 15 | 51 | 46 | 62 | 50 | 42 | 35 | 0 | 0
2022-11-14 10:00 | 11 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 50 | 18 | 53 | 53 | 64 | 53 | 45 | 40 | 0 | 0
2022-11-14 11:00 | 11 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 50 | 21 | 52 | 57 | 67 | 56 | 49 | 49 | 0 | 0
2022-11-14 12:00 | 11 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 54 | 23 | 52 | 59 | 69 | 59 | 50 | 53 | 0 | 0
2022-11-14 13:00 | 11 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 55 | 25 | 55 | 60 | 70 | 60 | 52 | 58 | 0 | 0
2022-11-14 14:00 | 11 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 54 | 26 | 52 | 61 | 72 | 61 | 53 | 63 | 0 | 0
2022-11-14 15:00 | 11 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 55 | 26 | 53 | 59 | 71 | 61 | 52 | 61 | 0 | 0
2022-11-14 16:00 | 11 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 54 | 23 | 50 | 57 | 66 | 57 | 49 | 56 | 0 | 0
2022-11-14 17:00 | 11 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 50 | 22 | 49 | 51 | 66 | 53 | 49 | 55 | 0 | 0
2022-11-14 18:00 | 11 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 49 | 22 | 49 | 46 | 64 | 51 | 49 | 53 | 0 | 0
2022-11-14 19:00 | 11 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 47 | 21 | 50 | 40 | 63 | 52 | 46 | 46 | 0 | 0
2022-11-14 20:00 | 11 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 46 | 21 | 50 | 40 | 61 | 52 | 45 | 43 | 0 | 0
2022-11-14 21:00 | 11 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 42 | 21 | 49 | 38 | 64 | 50 | 46 | 42 | 0 | 0
2022-11-14 22:00 | 11 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 40 | 21 | 47 | 37 | 64 | 45 | 46 | 41 | 0 | 0
2022-11-14 23:00 | 11 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 38 | 23 | 46 | 39 | 64 | 45 | 45 | 41 | 0 | 0
2022-11-15 | 11 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 37 | 23 | 43 | 36 | 65 | 45 | 45 | 39 | 0 | 0
2022-11-15 01:00 | 11 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 36 | 23 | 38 | 34 | 63 | 39 | 47 | 38 | 0 | 0
2022-11-15 02:00 | 11 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 36 | 23 | 39 | 33 | 63 | 40 | 47 | 39 | 0 | 0
2022-11-15 03:00 | 11 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 36 | 22 | 38 | 33 | 63 | 39 | 47 | 37 | 0 | 0
2022-11-15 04:00 | 11 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 35 | 23 | 38 | 32 | 62 | 36 | 47 | 35 | 0 | 0
2022-11-15 05:00 | 11 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 34 | 22 | 34 | 33 | 60 | 37 | 46 | 34 | 0 | 0
2022-11-15 06:00 | 11 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 34 | 23 | 35 | 33 | 61 | 37 | 46 | 33 | 0 | 0
2022-11-15 07:00 | 11 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 35 | 24 | 37 | 33 | 62 | 36 | 43 | 34 | 0 | 0
2022-11-15 08:00 | 11 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 38 | 27 | 46 | 39 | 64 | 44 | 42 | 38 | 0 | 0
2022-11-15 09:00 | 11 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 39 | 30 | 50 | 45 | 65 | 50 | 43 | 43 | 0 | 0
2022-11-15 10:00 | 11 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 44 | 32 | 53 | 48 | 66 | 57 | 46 | 48 | 0 | 0
2022-11-15 11:00 | 11 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 45 | 33 | 57 | 50 | 67 | 61 | 48 | 51 | 0 | 0
2022-11-15 12:00 | 11 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 46 | 34 | 61 | 52 | 69 | 64 | 48 | 53 | 0 | 0
2022-11-15 13:00 | 11 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 47 | 35 | 57 | 53 | 70 | 66 | 49 | 54 | 0 | 0
2022-11-15 14:00 | 11 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 49 | 35 | 57 | 53 | 70 | 67 | 49 | 55 | 0 | 0
2022-11-15 15:00 | 11 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 47 | 36 | 54 | 53 | 68 | 66 | 48 | 54 | 0 | 0
2022-11-15 16:00 | 11 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 43 | 35 | 50 | 51 | 67 | 60 | 47 | 50 | 0 | 0
2022-11-15 17:00 | 11 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 43 | 35 | 49 | 46 | 65 | 58 | 47 | 45 | 0 | 0
2022-11-15 18:00 | 11 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 42 | 35 | 49 | 44 | 63 | 55 | 47 | 41 | 0 | 0
2022-11-15 19:00 | 11 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 42 | 34 | 56 | 43 | 63 | 54 | 45 | 42 | 0 | 0
2022-11-15 20:00 | 11 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 42 | 34 | 57 | 40 | 63 | 54 | 45 | 42 | 0 | 0
2022-11-15 21:00 | 11 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 42 | 34 | 57 | 40 | 64 | 54 | 44 | 42 | 0 | 0
2022-11-15 22:00 | 11 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 42 | 34 | 57 | 37 | 65 | 53 | 44 | 41 | 0 | 0
2022-11-15 23:00 | 11 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 42 | 33 | 57 | 37 | 65 | 52 | 43 | 43 | 0 | 0
2022-11-16 | 11 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 42 | 33 | 56 | 36 | 64 | 54 | 43 | 42 | 0 | 0
2022-11-16 01:00 | 11 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 42 | 33 | 56 | 34 | 64 | 54 | 43 | 42 | 0 | 0
2022-11-16 02:00 | 11 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 42 | 33 | 58 | 36 | 64 | 53 | 42 | 44 | 0 | 0
2022-11-16 03:00 | 11 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 42 | 33 | 57 | 35 | 65 | 53 | 42 | 45 | 0 | 0
2022-11-16 04:00 | 11 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 43 | 34 | 57 | 35 | 66 | 53 | 42 | 46 | 0 | 0
2022-11-16 05:00 | 11 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 43 | 34 | 57 | 34 | 67 | 53 | 42 | 47 | 0 | 0
2022-11-16 06:00 | 11 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 44 | 33 | 57 | 32 | 67 | 54 | 42 | 46 | 0 | 0
2022-11-16 07:00 | 11 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 45 | 33 | 57 | 34 | 69 | 54 | 42 | 47 | 0 | 0
2022-11-16 08:00 | 11 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 46 | 33 | 59 | 40 | 67 | 58 | 42 | 49 | 0 | 0
2022-11-16 09:00 | 11 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 48 | 33 | 61 | 45 | 69 | 60 | 42 | 49 | 0 | 0
2022-11-16 10:00 | 11 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 49 | 35 | 62 | 49 | 71 | 65 | 43 | 50 | 0 | 0
2022-11-16 11:00 | 11 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 50 | 35 | 66 | 51 | 52 | 68 | 43 | 50 | 0 | 0
2022-11-16 12:00 | 11 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 53 | 35 | 62 | 52 | 52 | 68 | 44 | 53 | 0 | 0
2022-11-16 13:00 | 11 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 55 | 35 | 64 | 54 | 50 | 70 | 45 | 55 | 0 | 0
2022-11-16 14:00 | 11 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 56 | 36 | 67 | 55 | 51 | 70 | 45 | 56 | 0 | 0
2022-11-16 15:00 | 11 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 56 | 55 | 36 | 66 | 56 | 50 | 69 | 44 | 57 | 0 | 0
2022-11-16 16:00 | 11 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 54 | 36 | 50 | 52 | 48 | 69 | 44 | 57 | 0 | 0
2022-11-16 17:00 | 11 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 55 | 36 | 48 | 54 | 45 | 64 | 44 | 57 | 0 | 0
2022-11-16 18:00 | 11 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 55 | 36 | 47 | 50 | 46 | 62 | 43 | 57 | 0 | 0
2022-11-16 19:00 | 11 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 55 | 36 | 46 | 50 | 45 | 62 | 43 | 56 | 0 | 0
2022-11-16 20:00 | 11 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 56 | 36 | 45 | 50 | 43 | 53 | 43 | 58 | 0 | 0
2022-11-16 21:00 | 11 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 56 | 36 | 43 | 50 | 43 | 52 | 43 | 58 | 0 | 0
2022-11-16 22:00 | 11 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 56 | 36 | 41 | 50 | 42 | 49 | 43 | 59 | 0 | 0
2022-11-16 23:00 | 11 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 56 | 36 | 41 | 51 | 39 | 45 | 43 | 58 | 0 | 0
2022-11-17 | 11 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 56 | 36 | 40 | 50 | 39 | 42 | 43 | 58 | 0 | 0
2022-11-17 01:00 | 11 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 55 | 36 | 40 | 51 | 39 | 40 | 42 | 57 | 0 | 0
2022-11-17 02:00 | 11 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 54 | 36 | 39 | 50 | 37 | 39 | 42 | 57 | 0 | 0
2022-11-17 03:00 | 11 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 54 | 35 | 39 | 51 | 34 | 39 | 42 | 53 | 0 | 0
2022-11-17 04:00 | 11 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 48 | 35 | 38 | 51 | 34 | 39 | 42 | 51 | 0 | 0
2022-11-17 05:00 | 11 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 46 | 36 | 38 | 52 | 35 | 37 | 42 | 49 | 0 | 0
2022-11-17 06:00 | 11 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 43 | 36 | 37 | 51 | 35 | 36 | 42 | 45 | 0 | 0
2022-11-17 07:00 | 11 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 40 | 36 | 36 | 53 | 36 | 36 | 43 | 43 | 0 | 0
2022-11-17 08:00 | 11 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 39 | 37 | 37 | 52 | 37 | 36 | 44 | 45 | 0 | 0
2022-11-17 09:00 | 11 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 40 | 38 | 38 | 54 | 39 | 38 | 46 | 45 | 0 | 0
2022-11-17 10:00 | 11 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 42 | 38 | 38 | 58 | 43 | 39 | 47 | 46 | 0 | 0
2022-11-17 11:00 | 11 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 44 | 39 | 40 | 64 | 41 | 41 | 48 | 49 | 0 | 0
2022-11-17 12:00 | 11 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 66 | 44 | 41 | 41 | 65 | 43 | 42 | 48 | 50 | 0 | 0
2022-11-17 13:00 | 11 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 69 | 45 | 41 | 43 | 67 | 43 | 44 | 48 | 51 | 0 | 0
2022-11-17 14:00 | 11 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 67 | 45 | 41 | 44 | 67 | 44 | 44 | 48 | 50 | 0 | 0
2022-11-17 15:00 | 11 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 67 | 43 | 42 | 44 | 65 | 43 | 43 | 48 | 44 | 0 | 0
2022-11-17 16:00 | 11 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 65 | 41 | 40 | 42 | 65 | 45 | 42 | 47 | 43 | 0 | 0
2022-11-17 17:00 | 11 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 64 | 38 | 39 | 42 | 63 | 40 | 39 | 46 | 43 | 0 | 0
2022-11-17 18:00 | 11 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 37 | 38 | 41 | 59 | 39 | 37 | 46 | 41 | 0 | 0
2022-11-17 19:00 | 11 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 37 | 37 | 41 | 59 | 39 | 37 | 45 | 39 | 0 | 0
2022-11-17 20:00 | 11 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 34 | 37 | 41 | 60 | 36 | 37 | 45 | 38 | 0 | 0
2022-11-17 21:00 | 11 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 36 | 37 | 41 | 63 | 34 | 36 | 45 | 38 | 0 | 0
2022-11-17 22:00 | 11 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 35 | 38 | 43 | 63 | 33 | 34 | 45 | 35 | 0 | 0
2022-11-17 23:00 | 11 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 34 | 38 | 43 | 63 | 36 | 33 | 45 | 31 | 0 | 0
2022-11-18 | 11 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 33 | 38 | 43 | 63 | 36 | 32 | 44 | 29 | 0 | 0
2022-11-18 01:00 | 11 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 32 | 38 | 42 | 62 | 37 | 33 | 44 | 29 | 0 | 0
2022-11-18 02:00 | 11 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 62 | 32 | 38 | 42 | 59 | 36 | 32 | 44 | 28 | 0 | 0
2022-11-18 03:00 | 11 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 32 | 37 | 41 | 56 | 35 | 32 | 44 | 27 | 0 | 0
2022-11-18 04:00 | 11 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 33 | 37 | 41 | 52 | 34 | 31 | 44 | 30 | 0 | 0
2022-11-18 05:00 | 11 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 56 | 33 | 36 | 40 | 53 | 34 | 32 | 44 | 33 | 0 | 0
2022-11-18 06:00 | 11 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 33 | 36 | 40 | 59 | 34 | 30 | 44 | 32 | 0 | 0
2022-11-18 07:00 | 11 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 57 | 34 | 37 | 37 | 57 | 38 | 32 | 43 | 35 | 0 | 0
2022-11-18 08:00 | 11 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 35 | 36 | 40 | 59 | 40 | 34 | 43 | 39 | 0 | 0
2022-11-18 09:00 | 11 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 36 | 37 | 43 | 60 | 41 | 39 | 45 | 41 | 0 | 0
2022-11-18 10:00 | 11 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 37 | 37 | 46 | 61 | 44 | 44 | 46 | 46 | 0 | 0
2022-11-18 11:00 | 11 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 63 | 39 | 36 | 47 | 61 | 44 | 47 | 47 | 48 | 0 | 0
2022-11-18 12:00 | 11 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 62 | 40 | 34 | 46 | 61 | 47 | 49 | 48 | 46 | 0 | 0
2022-11-18 13:00 | 11 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 61 | 41 | 34 | 47 | 60 | 48 | 50 | 48 | 51 | 0 | 0
2022-11-18 14:00 | 11 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 41 | 33 | 47 | 60 | 47 | 51 | 48 | 51 | 0 | 0
2022-11-18 15:00 | 11 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 40 | 33 | 46 | 56 | 47 | 50 | 48 | 49 | 0 | 0
2022-11-18 16:00 | 11 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 36 | 33 | 42 | 53 | 41 | 47 | 47 | 45 | 0 | 0
2022-11-18 17:00 | 11 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 34 | 32 | 41 | 51 | 38 | 44 | 47 | 41 | 0 | 0
2022-11-18 18:00 | 11 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 34 | 32 | 37 | 51 | 38 | 43 | 46 | 38 | 0 | 0
2022-11-18 19:00 | 11 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 33 | 31 | 36 | 49 | 36 | 43 | 46 | 35 | 0 | 0
2022-11-18 20:00 | 11 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 30 | 30 | 35 | 48 | 35 | 43 | 46 | 33 | 0 | 0
2022-11-18 21:00 | 11 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 30 | 28 | 37 | 48 | 33 | 43 | 46 | 32 | 0 | 0
2022-11-18 22:00 | 11 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 32 | 28 | 38 | 47 | 31 | 43 | 46 | 32 | 0 | 0
2022-11-18 23:00 | 11 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 30 | 27 | 38 | 46 | 30 | 42 | 46 | 32 | 0 | 0
2022-11-19 | 11 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 31 | 27 | 39 | 45 | 30 | 42 | 45 | 31 | 0 | 0
2022-11-19 01:00 | 11 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 31 | 24 | 39 | 43 | 27 | 43 | 45 | 30 | 0 | 0
2022-11-19 02:00 | 11 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 31 | 23 | 40 | 43 | 26 | 43 | 45 | 31 | 0 | 0
2022-11-19 03:00 | 11 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 29 | 22 | 40 | 44 | 28 | 43 | 45 | 31 | 0 | 0
2022-11-19 04:00 | 11 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 29 | 22 | 40 | 41 | 28 | 44 | 44 | 32 | 0 | 0
2022-11-19 05:00 | 11 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 30 | 23 | 40 | 40 | 27 | 44 | 44 | 32 | 0 | 0
2022-11-19 06:00 | 11 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 31 | 23 | 42 | 38 | 28 | 43 | 44 | 33 | 0 | 0
2022-11-19 07:00 | 11 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 29 | 22 | 42 | 39 | 29 | 41 | 44 | 33 | 0 | 0
2022-11-19 08:00 | 11 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 29 | 23 | 44 | 43 | 31 | 42 | 45 | 35 | 0 | 0
2022-11-19 09:00 | 11 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 31 | 21 | 45 | 46 | 35 | 43 | 48 | 36 | 0 | 0
2022-11-19 10:00 | 11 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 33 | 24 | 46 | 47 | 37 | 44 | 49 | 40 | 0 | 0
2022-11-19 11:00 | 11 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 35 | 25 | 45 | 49 | 39 | 45 | 51 | 41 | 0 | 0
2022-11-19 12:00 | 11 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 36 | 25 | 45 | 51 | 40 | 45 | 52 | 41 | 0 | 0
2022-11-19 13:00 | 11 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 37 | 27 | 46 | 50 | 40 | 44 | 52 | 39 | 0 | 0
2022-11-19 14:00 | 11 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 38 | 26 | 47 | 51 | 41 | 41 | 52 | 38 | 0 | 0
2022-11-19 15:00 | 11 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 37 | 25 | 47 | 49 | 39 | 41 | 51 | 38 | 0 | 0
2022-11-19 16:00 | 11 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 37 | 21 | 46 | 48 | 37 | 41 | 50 | 38 | 0 | 0
2022-11-19 17:00 | 11 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 36 | 17 | 44 | 39 | 37 | 42 | 49 | 38 | 0 | 0
2022-11-19 18:00 | 11 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 36 | 18 | 42 | 44 | 37 | 42 | 47 | 39 | 0 | 0
2022-11-19 19:00 | 11 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 36 | 18 | 42 | 48 | 38 | 43 | 47 | 39 | 0 | 0
2022-11-19 20:00 | 11 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 36 | 16 | 43 | 48 | 39 | 44 | 46 | 39 | 0 | 0
2022-11-19 21:00 | 11 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 36 | 14 | 44 | 47 | 40 | 45 | 46 | 39 | 0 | 0
2022-11-19 22:00 | 11 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 36 | 15 | 44 | 47 | 41 | 45 | 46 | 39 | 0 | 0
2022-11-19 23:00 | 11 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 36 | 15 | 44 | 47 | 41 | 45 | 47 | 39 | 0 | 0
2022-11-20 | 11 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 36 | 16 | 44 | 45 | 42 | 45 | 47 | 39 | 0 | 0
2022-11-20 01:00 | 11 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 35 | 16 | 44 | 43 | 43 | 45 | 47 | 40 | 0 | 0
2022-11-20 02:00 | 11 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 35 | 17 | 44 | 39 | 44 | 45 | 48 | 39 | 0 | 0
2022-11-20 03:00 | 11 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 35 | 18 | 44 | 39 | 44 | 45 | 47 | 40 | 0 | 0
2022-11-20 04:00 | 11 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 35 | 19 | 44 | 40 | 43 | 45 | 47 | 40 | 0 | 0
2022-11-20 05:00 | 11 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 35 | 19 | 44 | 41 | 44 | 45 | 47 | 40 | 0 | 0
2022-11-20 06:00 | 11 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 36 | 19 | 44 | 41 | 44 | 45 | 45 | 40 | 0 | 0
2022-11-20 07:00 | 11 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 36 | 20 | 44 | 41 | 46 | 46 | 45 | 40 | 0 | 0
2022-11-20 08:00 | 11 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 37 | 20 | 45 | 43 | 48 | 46 | 47 | 40 | 0 | 0
2022-11-20 09:00 | 11 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 39 | 22 | 46 | 42 | 52 | 48 | 49 | 40 | 0 | 0
2022-11-20 10:00 | 11 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 40 | 25 | 46 | 43 | 55 | 53 | 50 | 42 | 0 | 0
2022-11-20 11:00 | 11 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 41 | 26 | 47 | 45 | 57 | 56 | 50 | 43 | 0 | 0
2022-11-20 12:00 | 11 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 43 | 27 | 47 | 44 | 61 | 64 | 51 | 43 | 0 | 0
2022-11-20 13:00 | 11 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 44 | 28 | 46 | 44 | 62 | 67 | 52 | 44 | 0 | 0
2022-11-20 14:00 | 11 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 45 | 29 | 46 | 43 | 61 | 62 | 52 | 44 | 0 | 0
2022-11-20 15:00 | 11 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 46 | 30 | 45 | 37 | 60 | 58 | 51 | 44 | 0 | 0
2022-11-20 16:00 | 11 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 47 | 31 | 44 | 38 | 59 | 58 | 50 | 45 | 0 | 0
2022-11-20 17:00 | 11 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 49 | 33 | 45 | 38 | 56 | 54 | 47 | 47 | 0 | 0
2022-11-20 18:00 | 11 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 50 | 33 | 42 | 36 | 54 | 51 | 46 | 46 | 0 | 0
2022-11-20 19:00 | 11 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 49 | 33 | 42 | 35 | 54 | 49 | 44 | 46 | 0 | 0
2022-11-20 20:00 | 11 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 49 | 33 | 43 | 34 | 56 | 46 | 43 | 46 | 0 | 0
2022-11-20 21:00 | 11 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 49 | 34 | 42 | 30 | 45 | 44 | 42 | 54 | 0 | 0
2022-11-20 22:00 | 11 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 42 | 34 | 44 | 32 | 47 | 43 | 42 | 52 | 0 | 0
2022-11-20 23:00 | 11 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 37 | 33 | 44 | 30 | 44 | 42 | 41 | 47 | 0 | 0
2022-11-21 | 11 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 35 | 33 | 44 | 26 | 42 | 41 | 40 | 47 | 0 | 0
2022-11-21 01:00 | 11 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 34 | 32 | 44 | 27 | 42 | 40 | 40 | 46 | 0 | 0
2022-11-21 02:00 | 11 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 35 | 32 | 42 | 26 | 41 | 40 | 39 | 46 | 0 | 0
2022-11-21 03:00 | 11 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 34 | 32 | 42 | 26 | 39 | 39 | 37 | 46 | 0 | 0
2022-11-21 04:00 | 11 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 34 | 31 | 42 | 26 | 37 | 40 | 34 | 45 | 0 | 0
2022-11-21 05:00 | 11 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 33 | 30 | 42 | 24 | 37 | 40 | 34 | 45 | 0 | 0
2022-11-21 06:00 | 11 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 33 | 29 | 41 | 24 | 37 | 38 | 34 | 44 | 0 | 0
2022-11-21 07:00 | 11 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 33 | 28 | 41 | 21 | 36 | 39 | 34 | 44 | 0 | 0
2022-11-21 08:00 | 11 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 18 | 32 | 28 | 42 | 21 | 36 | 39 | 35 | 45 | 0 | 0
2022-11-21 09:00 | 11 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 33 | 27 | 41 | 22 | 37 | 40 | 35 | 45 | 0 | 0
2022-11-21 10:00 | 11 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 33 | 27 | 42 | 23 | 38 | 41 | 37 | 45 | 0 | 0
2022-11-21 11:00 | 11 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 32 | 27 | 42 | 23 | 38 | 41 | 38 | 46 | 0 | 0
2022-11-21 12:00 | 11 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 32 | 27 | 42 | 25 | 37 | 40 | 39 | 46 | 0 | 0
2022-11-21 13:00 | 11 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 33 | 27 | 41 | 25 | 38 | 40 | 39 | 45 | 0 | 0
2022-11-21 14:00 | 11 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 32 | 27 | 41 | 24 | 37 | 40 | 39 | 45 | 0 | 0
2022-11-21 15:00 | 11 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 33 | 27 | 41 | 23 | 36 | 39 | 39 | 44 | 0 | 0
2022-11-21 16:00 | 11 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 18 | 32 | 27 | 41 | 23 | 34 | 39 | 38 | 43 | 0 | 0
2022-11-21 17:00 | 11 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 18 | 32 | 27 | 40 | 23 | 33 | 38 | 38 | 42 | 0 | 0
2022-11-21 18:00 | 11 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 32 | 28 | 40 | 23 | 31 | 38 | 38 | 41 | 0 | 0
2022-11-21 19:00 | 11 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 31 | 28 | 39 | 23 | 30 | 38 | 38 | 40 | 0 | 0
2022-11-21 20:00 | 11 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 31 | 28 | 39 | 23 | 29 | 38 | 37 | 39 | 0 | 0
2022-11-21 21:00 | 11 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 31 | 28 | 38 | 22 | 27 | 37 | 36 | 38 | 0 | 0
2022-11-21 22:00 | 11 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 31 | 28 | 38 | 22 | 28 | 38 | 36 | 38 | 0 | 0
2022-11-21 23:00 | 11 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 30 | 28 | 38 | 21 | 27 | 38 | 36 | 38 | 0 | 0
2022-11-22 | 11 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 30 | 27 | 38 | 21 | 26 | 37 | 35 | 37 | 0 | 0
2022-11-22 01:00 | 11 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 30 | 27 | 38 | 21 | 26 | 37 | 35 | 37 | 0 | 0
2022-11-22 02:00 | 11 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 30 | 27 | 38 | 20 | 25 | 37 | 35 | 34 | 0 | 0
2022-11-22 03:00 | 11 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 30 | 27 | 37 | 19 | 24 | 37 | 34 | 35 | 0 | 0
2022-11-22 04:00 | 11 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 30 | 27 | 37 | 20 | 25 | 36 | 34 | 34 | 0 | 0
2022-11-22 05:00 | 11 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 29 | 27 | 37 | 20 | 26 | 36 | 34 | 31 | 0 | 0
2022-11-22 06:00 | 11 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 29 | 28 | 37 | 20 | 26 | 36 | 33 | 32 | 0 | 0
2022-11-22 07:00 | 11 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 29 | 27 | 37 | 23 | 26 | 36 | 33 | 33 | 0 | 0
2022-11-22 08:00 | 11 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 30 | 29 | 38 | 26 | 29 | 36 | 33 | 35 | 0 | 0
2022-11-22 09:00 | 11 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 30 | 32 | 38 | 28 | 30 | 37 | 33 | 38 | 0 | 0
2022-11-22 10:00 | 11 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 32 | 35 | 38 | 30 | 33 | 38 | 34 | 41 | 0 | 0
2022-11-22 11:00 | 11 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 33 | 36 | 40 | 33 | 35 | 40 | 35 | 43 | 0 | 0
2022-11-22 12:00 | 11 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 35 | 38 | 39 | 34 | 34 | 44 | 35 | 44 | 0 | 0
2022-11-22 13:00 | 11 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 36 | 37 | 39 | 35 | 33 | 45 | 35 | 45 | 0 | 0
2022-11-22 14:00 | 11 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 37 | 39 | 39 | 35 | 33 | 46 | 35 | 46 | 0 | 0
2022-11-22 15:00 | 11 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 36 | 37 | 39 | 35 | 32 | 46 | 35 | 43 | 0 | 0
2022-11-22 16:00 | 11 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 33 | 34 | 39 | 32 | 33 | 44 | 34 | 41 | 0 | 0
2022-11-22 17:00 | 11 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 34 | 32 | 39 | 29 | 33 | 43 | 34 | 36 | 0 | 0
2022-11-22 18:00 | 11 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 32 | 31 | 38 | 29 | 33 | 40 | 34 | 34 | 0 | 0
2022-11-22 19:00 | 11 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 32 | 31 | 37 | 28 | 32 | 38 | 34 | 31 | 0 | 0
2022-11-22 20:00 | 11 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 30 | 30 | 36 | 26 | 30 | 37 | 34 | 30 | 0 | 0
2022-11-22 21:00 | 11 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 29 | 31 | 36 | 25 | 27 | 35 | 34 | 29 | 0 | 0
2022-11-22 22:00 | 11 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 28 | 32 | 36 | 24 | 27 | 34 | 34 | 26 | 0 | 0
2022-11-22 23:00 | 11 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 27 | 33 | 37 | 24 | 27 | 33 | 34 | 27 | 0 | 0
2022-11-23 | 11 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 28 | 32 | 37 | 23 | 26 | 32 | 34 | 26 | 0 | 0
2022-11-23 01:00 | 11 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 29 | 32 | 36 | 23 | 26 | 31 | 34 | 26 | 0 | 0
2022-11-23 02:00 | 11 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 28 | 32 | 36 | 22 | 26 | 30 | 33 | 26 | 0 | 0
2022-11-23 03:00 | 11 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 26 | 32 | 36 | 22 | 26 | 27 | 33 | 25 | 0 | 0
2022-11-23 04:00 | 11 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 26 | 32 | 36 | 21 | 26 | 27 | 33 | 24 | 0 | 0
2022-11-23 05:00 | 11 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 27 | 32 | 33 | 22 | 26 | 28 | 33 | 24 | 0 | 0
2022-11-23 06:00 | 11 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 26 | 33 | 31 | 22 | 27 | 27 | 32 | 25 | 0 | 0
2022-11-23 07:00 | 11 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 21 | 27 | 33 | 31 | 23 | 26 | 24 | 32 | 26 | 0 | 0
2022-11-23 08:00 | 11 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 30 | 35 | 36 | 29 | 26 | 31 | 32 | 26 | 0 | 0
2022-11-23 09:00 | 11 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 32 | 37 | 39 | 32 | 27 | 34 | 33 | 29 | 0 | 0
2022-11-23 10:00 | 11 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 33 | 40 | 40 | 36 | 29 | 38 | 34 | 35 | 0 | 0
2022-11-23 11:00 | 11 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 34 | 43 | 41 | 39 | 30 | 41 | 35 | 38 | 0 | 0
2022-11-23 12:00 | 11 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 36 | 44 | 41 | 43 | 30 | 43 | 35 | 42 | 0 | 0
2022-11-23 13:00 | 11 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 35 | 44 | 40 | 47 | 31 | 43 | 35 | 45 | 0 | 0
2022-11-23 14:00 | 11 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 34 | 45 | 40 | 48 | 31 | 44 | 35 | 46 | 0 | 0
2022-11-23 15:00 | 11 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 33 | 45 | 39 | 47 | 31 | 44 | 35 | 42 | 0 | 0
2022-11-23 16:00 | 11 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 32 | 43 | 37 | 47 | 31 | 42 | 35 | 38 | 0 | 0
2022-11-23 17:00 | 11 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 31 | 42 | 35 | 47 | 29 | 40 | 34 | 35 | 0 | 0
2022-11-23 18:00 | 11 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 31 | 42 | 33 | 45 | 24 | 39 | 34 | 35 | 0 | 0
2022-11-23 19:00 | 11 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 30 | 42 | 33 | 42 | 25 | 38 | 34 | 33 | 0 | 0
2022-11-23 20:00 | 11 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 30 | 41 | 33 | 41 | 24 | 36 | 33 | 32 | 0 | 0
2022-11-23 21:00 | 11 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 28 | 41 | 31 | 40 | 20 | 34 | 33 | 32 | 0 | 0
2022-11-23 22:00 | 11 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 27 | 39 | 29 | 38 | 23 | 33 | 33 | 30 | 0 | 0
2022-11-23 23:00 | 11 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 26 | 40 | 29 | 37 | 20 | 32 | 33 | 29 | 0 | 0
2022-11-24 | 11 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 26 | 41 | 28 | 34 | 20 | 32 | 33 | 29 | 0 | 0
2022-11-24 01:00 | 11 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 26 | 42 | 28 | 33 | 22 | 29 | 32 | 27 | 0 | 0
2022-11-24 02:00 | 11 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 28 | 43 | 30 | 34 | 23 | 29 | 31 | 28 | 0 | 0
2022-11-24 03:00 | 11 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 27 | 43 | 29 | 32 | 22 | 27 | 29 | 28 | 0 | 0
2022-11-24 04:00 | 11 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 27 | 43 | 31 | 31 | 22 | 27 | 28 | 28 | 0 | 0
2022-11-24 05:00 | 11 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 26 | 39 | 29 | 30 | 19 | 25 | 26 | 27 | 0 | 0
2022-11-24 06:00 | 11 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 26 | 39 | 29 | 31 | 21 | 23 | 25 | 27 | 0 | 0
2022-11-24 07:00 | 11 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 26 | 36 | 27 | 32 | 21 | 25 | 26 | 28 | 0 | 0
2022-11-24 08:00 | 11 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 28 | 36 | 32 | 36 | 25 | 28 | 29 | 30 | 0 | 0
2022-11-24 09:00 | 11 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 30 | 35 | 37 | 40 | 31 | 34 | 32 | 34 | 0 | 0
2022-11-24 10:00 | 11 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 33 | 36 | 40 | 45 | 32 | 40 | 35 | 39 | 0 | 0
2022-11-24 11:00 | 11 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 34 | 36 | 42 | 50 | 34 | 42 | 36 | 43 | 0 | 0
2022-11-24 12:00 | 11 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 35 | 36 | 44 | 55 | 35 | 45 | 37 | 44 | 0 | 0
2022-11-24 13:00 | 11 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 60 | 35 | 36 | 45 | 58 | 36 | 46 | 38 | 44 | 0 | 0
2022-11-24 14:00 | 11 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 59 | 34 | 37 | 44 | 57 | 36 | 48 | 37 | 45 | 0 | 0
2022-11-24 15:00 | 11 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 58 | 33 | 36 | 42 | 55 | 35 | 49 | 37 | 43 | 0 | 0
2022-11-24 16:00 | 11 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 55 | 30 | 34 | 40 | 51 | 31 | 46 | 35 | 40 | 0 | 0
2022-11-24 17:00 | 11 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 30 | 33 | 35 | 47 | 30 | 42 | 34 | 35 | 0 | 0
2022-11-24 18:00 | 11 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 30 | 33 | 36 | 45 | 31 | 39 | 32 | 34 | 0 | 0
2022-11-24 19:00 | 11 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 30 | 33 | 34 | 45 | 32 | 36 | 31 | 34 | 0 | 0
2022-11-24 20:00 | 11 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 31 | 33 | 32 | 45 | 31 | 36 | 30 | 31 | 0 | 0
2022-11-24 21:00 | 11 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 31 | 33 | 34 | 46 | 29 | 35 | 29 | 28 | 0 | 0
2022-11-24 22:00 | 11 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 32 | 32 | 34 | 47 | 27 | 33 | 27 | 29 | 0 | 0
2022-11-24 23:00 | 11 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 31 | 32 | 35 | 47 | 29 | 32 | 27 | 29 | 0 | 0
2022-11-25 | 11 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 31 | 31 | 33 | 47 | 29 | 31 | 28 | 27 | 0 | 0
2022-11-25 01:00 | 11 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 31 | 30 | 36 | 45 | 29 | 33 | 28 | 28 | 0 | 0
2022-11-25 02:00 | 11 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 31 | 30 | 36 | 47 | 29 | 31 | 27 | 28 | 0 | 0
2022-11-25 03:00 | 11 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 31 | 28 | 37 | 49 | 29 | 29 | 26 | 27 | 0 | 0
2022-11-25 04:00 | 11 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 31 | 26 | 37 | 48 | 29 | 30 | 25 | 26 | 0 | 0
2022-11-25 05:00 | 11 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 30 | 27 | 37 | 46 | 30 | 28 | 25 | 24 | 0 | 0
2022-11-25 06:00 | 11 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 29 | 28 | 37 | 45 | 30 | 29 | 24 | 24 | 0 | 0
2022-11-25 07:00 | 11 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 29 | 29 | 39 | 45 | 31 | 30 | 24 | 24 | 0 | 0
2022-11-25 08:00 | 11 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 33 | 31 | 43 | 47 | 36 | 32 | 26 | 29 | 0 | 0
2022-11-25 09:00 | 11 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 34 | 33 | 45 | 48 | 37 | 37 | 28 | 33 | 0 | 0
2022-11-25 10:00 | 11 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 38 | 38 | 50 | 50 | 39 | 44 | 30 | 35 | 0 | 0
2022-11-25 11:00 | 11 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 41 | 43 | 51 | 52 | 39 | 52 | 34 | 40 | 0 | 0
2022-11-25 12:00 | 11 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 42 | 46 | 55 | 54 | 42 | 55 | 35 | 42 | 0 | 0
2022-11-25 13:00 | 11 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 43 | 48 | 58 | 55 | 43 | 56 | 35 | 45 | 0 | 0
2022-11-25 14:00 | 11 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 44 | 48 | 61 | 56 | 44 | 56 | 35 | 47 | 0 | 0
2022-11-25 15:00 | 11 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 43 | 46 | 60 | 55 | 42 | 55 | 35 | 44 | 0 | 0
2022-11-25 16:00 | 11 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 41 | 41 | 56 | 53 | 41 | 52 | 33 | 37 | 0 | 0
2022-11-25 17:00 | 11 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 40 | 39 | 51 | 52 | 40 | 48 | 32 | 35 | 0 | 0
2022-11-25 18:00 | 11 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 40 | 39 | 51 | 52 | 37 | 47 | 32 | 35 | 0 | 0
2022-11-25 19:00 | 11 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 40 | 39 | 52 | 51 | 37 | 45 | 31 | 32 | 0 | 0
2022-11-25 20:00 | 11 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 39 | 39 | 53 | 49 | 39 | 47 | 30 | 30 | 0 | 0
2022-11-25 21:00 | 11 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 38 | 38 | 54 | 47 | 38 | 44 | 29 | 29 | 0 | 0
2022-11-25 22:00 | 11 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 38 | 39 | 55 | 47 | 40 | 46 | 28 | 29 | 0 | 0
2022-11-25 23:00 | 11 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 37 | 40 | 54 | 45 | 40 | 47 | 28 | 28 | 0 | 0
2022-11-26 | 11 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 37 | 38 | 55 | 46 | 41 | 47 | 28 | 28 | 0 | 0
2022-11-26 01:00 | 11 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 37 | 38 | 53 | 44 | 41 | 49 | 27 | 28 | 0 | 0
2022-11-26 02:00 | 11 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 38 | 36 | 55 | 42 | 41 | 49 | 27 | 27 | 0 | 0
2022-11-26 03:00 | 11 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 39 | 36 | 55 | 43 | 41 | 48 | 26 | 28 | 0 | 0
2022-11-26 04:00 | 11 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 41 | 36 | 55 | 42 | 41 | 47 | 25 | 27 | 0 | 0
2022-11-26 05:00 | 11 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 36 | 37 | 55 | 42 | 42 | 46 | 24 | 27 | 0 | 0
2022-11-26 06:00 | 11 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 40 | 38 | 54 | 41 | 42 | 46 | 24 | 26 | 0 | 0
2022-11-26 07:00 | 11 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 41 | 40 | 55 | 43 | 42 | 44 | 24 | 27 | 0 | 0
2022-11-26 08:00 | 11 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 42 | 42 | 55 | 47 | 43 | 48 | 27 | 31 | 0 | 0
2022-11-26 09:00 | 11 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 43 | 42 | 59 | 50 | 44 | 51 | 29 | 36 | 0 | 0
2022-11-26 10:00 | 11 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 45 | 43 | 61 | 51 | 45 | 53 | 33 | 40 | 0 | 0
2022-11-26 11:00 | 11 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 50 | 44 | 61 | 55 | 47 | 58 | 36 | 43 | 0 | 0
2022-11-26 12:00 | 11 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 54 | 45 | 63 | 55 | 51 | 62 | 36 | 48 | 0 | 0
2022-11-26 13:00 | 11 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 55 | 46 | 64 | 54 | 52 | 62 | 38 | 51 | 0 | 0
2022-11-26 14:00 | 11 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 54 | 48 | 63 | 54 | 53 | 60 | 38 | 53 | 0 | 0
2022-11-26 15:00 | 11 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 52 | 48 | 62 | 51 | 52 | 60 | 38 | 50 | 0 | 0
2022-11-26 16:00 | 11 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 49 | 47 | 61 | 49 | 49 | 57 | 38 | 48 | 0 | 0
2022-11-26 17:00 | 11 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 50 | 47 | 61 | 47 | 45 | 55 | 39 | 44 | 0 | 0
2022-11-26 18:00 | 11 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 47 | 49 | 62 | 44 | 40 | 55 | 39 | 42 | 0 | 0
2022-11-26 19:00 | 11 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 51 | 51 | 62 | 42 | 43 | 53 | 39 | 40 | 0 | 0
2022-11-26 20:00 | 11 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 49 | 43 | 62 | 40 | 40 | 53 | 39 | 42 | 0 | 0
2022-11-26 21:00 | 11 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 49 | 40 | 61 | 39 | 40 | 52 | 39 | 42 | 0 | 0
2022-11-26 22:00 | 11 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 50 | 38 | 61 | 39 | 44 | 56 | 39 | 51 | 0 | 0
2022-11-26 23:00 | 11 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 49 | 38 | 61 | 38 | 44 | 59 | 39 | 46 | 0 | 0
2022-11-27 | 11 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 49 | 37 | 60 | 38 | 45 | 59 | 40 | 47 | 0 | 0
2022-11-27 01:00 | 11 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 49 | 36 | 59 | 38 | 44 | 60 | 39 | 52 | 0 | 0
2022-11-27 02:00 | 11 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 50 | 35 | 61 | 37 | 42 | 59 | 39 | 51 | 0 | 0
2022-11-27 03:00 | 11 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 49 | 36 | 62 | 36 | 43 | 62 | 37 | 54 | 0 | 0
2022-11-27 04:00 | 11 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 50 | 35 | 61 | 36 | 41 | 62 | 37 | 55 | 0 | 0
2022-11-27 05:00 | 11 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 52 | 35 | 62 | 35 | 40 | 58 | 35 | 54 | 0 | 0
2022-11-27 06:00 | 11 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 53 | 35 | 62 | 35 | 39 | 57 | 36 | 55 | 0 | 0
2022-11-27 07:00 | 11 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 53 | 35 | 61 | 36 | 41 | 57 | 37 | 56 | 0 | 0
2022-11-27 08:00 | 11 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 54 | 36 | 56 | 36 | 45 | 56 | 39 | 56 | 0 | 0
2022-11-27 09:00 | 11 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 55 | 37 | 59 | 37 | 46 | 58 | 43 | 58 | 0 | 0
2022-11-27 10:00 | 11 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 59 | 37 | 61 | 37 | 48 | 59 | 46 | 58 | 0 | 0
2022-11-27 11:00 | 11 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 60 | 38 | 59 | 37 | 47 | 61 | 51 | 59 | 0 | 0
2022-11-27 12:00 | 11 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 59 | 41 | 57 | 38 | 49 | 63 | 52 | 59 | 0 | 0
2022-11-27 13:00 | 11 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 59 | 43 | 53 | 38 | 49 | 64 | 50 | 60 | 0 | 0
2022-11-27 14:00 | 11 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 58 | 45 | 51 | 39 | 51 | 65 | 50 | 61 | 0 | 0
2022-11-27 15:00 | 11 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 57 | 45 | 50 | 38 | 49 | 63 | 48 | 60 | 0 | 0
2022-11-27 16:00 | 11 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 56 | 39 | 50 | 38 | 47 | 58 | 45 | 60 | 0 | 0
2022-11-27 17:00 | 11 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 56 | 36 | 46 | 37 | 47 | 57 | 44 | 60 | 0 | 0
2022-11-27 18:00 | 11 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 55 | 35 | 45 | 37 | 45 | 53 | 44 | 60 | 0 | 0
2022-11-27 19:00 | 11 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 55 | 34 | 45 | 37 | 45 | 51 | 43 | 60 | 0 | 0
2022-11-27 20:00 | 11 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 55 | 34 | 44 | 37 | 43 | 50 | 42 | 60 | 0 | 0
2022-11-27 21:00 | 11 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 56 | 34 | 42 | 37 | 43 | 48 | 41 | 59 | 0 | 0
2022-11-27 22:00 | 11 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 54 | 33 | 41 | 36 | 44 | 45 | 41 | 58 | 0 | 0
2022-11-27 23:00 | 11 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 54 | 33 | 41 | 36 | 44 | 43 | 41 | 56 | 0 | 0
2022-11-28 | 11 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 53 | 33 | 40 | 36 | 44 | 41 | 41 | 54 | 0 | 0
2022-11-28 01:00 | 11 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 51 | 33 | 40 | 36 | 44 | 39 | 41 | 53 | 0 | 0
2022-11-28 02:00 | 11 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 48 | 33 | 40 | 36 | 46 | 38 | 41 | 53 | 0 | 0
2022-11-28 03:00 | 11 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 46 | 33 | 40 | 36 | 47 | 38 | 40 | 52 | 0 | 0
2022-11-28 04:00 | 11 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 43 | 33 | 39 | 36 | 50 | 36 | 39 | 52 | 0 | 0
2022-11-28 05:00 | 11 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 40 | 32 | 38 | 36 | 53 | 35 | 39 | 47 | 0 | 0
2022-11-28 06:00 | 11 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 37 | 31 | 37 | 37 | 54 | 34 | 39 | 47 | 0 | 0
2022-11-28 07:00 | 11 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 36 | 30 | 37 | 37 | 55 | 33 | 39 | 46 | 0 | 0
2022-11-28 08:00 | 11 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 35 | 31 | 37 | 37 | 56 | 35 | 38 | 44 | 0 | 0
2022-11-28 09:00 | 11 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 35 | 31 | 37 | 37 | 57 | 37 | 38 | 43 | 0 | 0
2022-11-28 10:00 | 11 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 36 | 32 | 37 | 38 | 58 | 36 | 39 | 44 | 0 | 0
2022-11-28 11:00 | 11 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 37 | 36 | 37 | 39 | 57 | 35 | 40 | 46 | 0 | 0
2022-11-28 12:00 | 11 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 37 | 41 | 36 | 39 | 58 | 33 | 39 | 44 | 0 | 0
2022-11-28 13:00 | 11 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 39 | 43 | 35 | 39 | 58 | 33 | 39 | 45 | 0 | 0
2022-11-28 14:00 | 11 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 39 | 44 | 34 | 39 | 59 | 32 | 39 | 45 | 0 | 0
2022-11-28 15:00 | 11 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 33 | 42 | 33 | 40 | 60 | 31 | 39 | 43 | 0 | 0
2022-11-28 16:00 | 11 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 33 | 39 | 32 | 40 | 57 | 31 | 39 | 34 | 0 | 0
2022-11-28 17:00 | 11 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 31 | 36 | 32 | 41 | 54 | 31 | 39 | 36 | 0 | 0
2022-11-28 18:00 | 11 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 32 | 35 | 33 | 41 | 52 | 32 | 39 | 37 | 0 | 0
2022-11-28 19:00 | 11 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 32 | 33 | 38 | 42 | 50 | 32 | 39 | 36 | 0 | 0
2022-11-28 20:00 | 11 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 32 | 33 | 39 | 41 | 48 | 32 | 39 | 36 | 0 | 0
2022-11-28 21:00 | 11 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 31 | 29 | 39 | 42 | 47 | 32 | 39 | 36 | 0 | 0
2022-11-28 22:00 | 11 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 31 | 33 | 39 | 41 | 46 | 32 | 39 | 36 | 0 | 0
2022-11-28 23:00 | 11 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 31 | 34 | 38 | 42 | 44 | 32 | 38 | 36 | 0 | 0
2022-11-29 | 11 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 31 | 35 | 37 | 41 | 43 | 32 | 38 | 37 | 0 | 0
2022-11-29 01:00 | 11 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 32 | 34 | 38 | 40 | 41 | 32 | 38 | 37 | 0 | 0
2022-11-29 02:00 | 11 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 33 | 32 | 38 | 41 | 40 | 32 | 38 | 37 | 0 | 0
2022-11-29 03:00 | 11 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 33 | 31 | 37 | 42 | 37 | 31 | 38 | 38 | 0 | 0
2022-11-29 04:00 | 11 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 34 | 32 | 37 | 42 | 39 | 31 | 38 | 37 | 0 | 0
2022-11-29 05:00 | 11 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 34 | 31 | 37 | 43 | 37 | 30 | 37 | 38 | 0 | 0
2022-11-29 06:00 | 11 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 34 | 32 | 34 | 43 | 36 | 30 | 36 | 40 | 0 | 0
2022-11-29 07:00 | 11 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 34 | 32 | 34 | 44 | 36 | 30 | 35 | 40 | 0 | 0
2022-11-29 08:00 | 11 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 33 | 32 | 33 | 44 | 36 | 29 | 35 | 39 | 0 | 0
2022-11-29 09:00 | 11 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 34 | 33 | 34 | 46 | 38 | 30 | 36 | 40 | 0 | 0
2022-11-29 10:00 | 11 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 33 | 34 | 35 | 46 | 38 | 32 | 38 | 40 | 0 | 0
2022-11-29 11:00 | 11 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 34 | 34 | 36 | 47 | 37 | 35 | 38 | 41 | 0 | 0
2022-11-29 12:00 | 11 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 34 | 35 | 38 | 46 | 38 | 38 | 38 | 42 | 0 | 0
2022-11-29 13:00 | 11 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 35 | 35 | 37 | 47 | 38 | 38 | 38 | 42 | 0 | 0
2022-11-29 14:00 | 11 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 36 | 36 | 40 | 48 | 35 | 40 | 38 | 41 | 0 | 0
2022-11-29 15:00 | 11 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 36 | 36 | 39 | 48 | 34 | 40 | 36 | 40 | 0 | 0
2022-11-29 16:00 | 11 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 34 | 36 | 37 | 51 | 32 | 38 | 34 | 39 | 0 | 0
2022-11-29 17:00 | 11 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 32 | 36 | 36 | 51 | 30 | 35 | 34 | 37 | 0 | 0
2022-11-29 18:00 | 11 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 33 | 36 | 36 | 50 | 29 | 33 | 33 | 36 | 0 | 0
2022-11-29 19:00 | 11 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 31 | 35 | 36 | 51 | 28 | 32 | 33 | 32 | 0 | 0
2022-11-29 20:00 | 11 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 30 | 34 | 37 | 48 | 28 | 33 | 33 | 30 | 0 | 0
2022-11-29 21:00 | 11 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 30 | 32 | 37 | 49 | 26 | 32 | 33 | 28 | 0 | 0
2022-11-29 22:00 | 11 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 30 | 32 | 37 | 49 | 26 | 31 | 32 | 28 | 0 | 0
2022-11-29 23:00 | 11 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 30 | 30 | 38 | 48 | 24 | 29 | 32 | 27 | 0 | 0
2022-11-30 | 11 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 60 | 30 | 31 | 39 | 48 | 24 | 32 | 32 | 27 | 0 | 0
2022-11-30 01:00 | 11 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 59 | 30 | 33 | 40 | 48 | 28 | 35 | 31 | 32 | 0 | 0
2022-11-30 02:00 | 11 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 57 | 29 | 33 | 43 | 47 | 29 | 36 | 31 | 32 | 0 | 0
2022-11-30 03:00 | 11 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 32 | 33 | 43 | 47 | 28 | 35 | 30 | 31 | 0 | 0
2022-11-30 04:00 | 11 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 32 | 32 | 42 | 46 | 28 | 36 | 29 | 34 | 0 | 0
2022-11-30 05:00 | 11 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 33 | 32 | 42 | 45 | 27 | 38 | 28 | 35 | 0 | 0
2022-11-30 06:00 | 11 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 33 | 31 | 43 | 45 | 30 | 39 | 28 | 34 | 0 | 0
2022-11-30 07:00 | 11 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 33 | 30 | 43 | 46 | 31 | 42 | 27 | 34 | 0 | 0
2022-11-30 08:00 | 11 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 36 | 30 | 43 | 45 | 33 | 43 | 28 | 37 | 0 | 0
2022-11-30 09:00 | 11 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 37 | 31 | 43 | 46 | 36 | 44 | 29 | 38 | 0 | 0
2022-11-30 10:00 | 11 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 40 | 33 | 42 | 45 | 38 | 46 | 32 | 40 | 0 | 0
2022-11-30 11:00 | 11 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 41 | 34 | 41 | 47 | 40 | 46 | 33 | 42 | 0 | 0
2022-11-30 12:00 | 11 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 42 | 36 | 38 | 46 | 41 | 47 | 34 | 42 | 0 | 0
2022-11-30 13:00 | 11 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 51 | 45 | 35 | 38 | 45 | 41 | 46 | 36 | 45 | 0 | 0
2022-11-30 14:00 | 11 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 45 | 34 | 38 | 44 | 43 | 44 | 36 | 45 | 0 | 0
2022-11-30 15:00 | 11 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 43 | 33 | 37 | 43 | 41 | 42 | 35 | 46 | 0 | 0
2022-11-30 16:00 | 11 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 42 | 28 | 36 | 42 | 39 | 40 | 33 | 42 | 0 | 0
2022-11-30 17:00 | 11 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 41 | 26 | 36 | 42 | 37 | 38 | 32 | 39 | 0 | 0
2022-11-30 18:00 | 11 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 40 | 24 | 36 | 42 | 37 | 38 | 31 | 35 | 0 | 0
2022-11-30 19:00 | 11 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 40 | 23 | 36 | 42 | 37 | 37 | 28 | 32 | 0 | 0
2022-11-30 20:00 | 11 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 39 | 21 | 36 | 41 | 35 | 38 | 28 | 32 | 0 | 0
2022-11-30 21:00 | 11 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 37 | 24 | 36 | 41 | 35 | 40 | 28 | 32 | 0 | 0
2022-11-30 22:00 | 11 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 35 | 27 | 36 | 42 | 36 | 42 | 27 | 31 | 0 | 0
2022-11-30 23:00 | 11 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 32 | 30 | 36 | 42 | 36 | 44 | 27 | 31 | 0 | 0
2022-12-01 | 12 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 30 | 33 | 36 | 42 | 36 | 46 | 26 | 30 | 0 | 0
2022-12-01 01:00 | 12 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 28 | 36 | 36 | 42 | 37 | 47 | 26 | 30 | 0 | 0
2022-12-01 02:00 | 12 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 26 | 39 | 36 | 43 | 37 | 49 | 26 | 29 | 0 | 0
2022-12-01 03:00 | 12 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 23 | 42 | 36 | 43 | 37 | 51 | 25 | 29 | 0 | 0
2022-12-01 04:00 | 12 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 22 | 42 | 35 | 43 | 36 | 51 | 25 | 27 | 0 | 0
2022-12-01 05:00 | 12 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 23 | 42 | 35 | 43 | 34 | 53 | 23 | 26 | 0 | 0
2022-12-01 06:00 | 12 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 24 | 42 | 35 | 42 | 35 | 55 | 21 | 25 | 0 | 0
2022-12-01 07:00 | 12 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 25 | 43 | 36 | 42 | 35 | 57 | 23 | 23 | 0 | 0
2022-12-01 08:00 | 12 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 27 | 45 | 37 | 42 | 38 | 59 | 26 | 26 | 0 | 0
2022-12-01 09:00 | 12 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 30 | 46 | 38 | 43 | 40 | 64 | 30 | 29 | 0 | 0
2022-12-01 10:00 | 12 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 32 | 48 | 41 | 43 | 42 | 60 | 32 | 32 | 0 | 0
2022-12-01 11:00 | 12 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 35 | 51 | 42 | 44 | 43 | 60 | 35 | 35 | 0 | 0
2022-12-01 12:00 | 12 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 37 | 53 | 42 | 45 | 44 | 58 | 37 | 40 | 0 | 0
2022-12-01 13:00 | 12 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 39 | 50 | 44 | 46 | 45 | 52 | 39 | 40 | 0 | 0
2022-12-01 14:00 | 12 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 39 | 48 | 45 | 47 | 45 | 50 | 40 | 40 | 0 | 0
2022-12-01 15:00 | 12 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 37 | 45 | 44 | 47 | 44 | 46 | 39 | 41 | 0 | 0
2022-12-01 16:00 | 12 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 36 | 42 | 44 | 46 | 41 | 43 | 36 | 40 | 0 | 0
2022-12-01 17:00 | 12 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 35 | 39 | 43 | 46 | 41 | 42 | 35 | 40 | 0 | 0
2022-12-01 18:00 | 12 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 34 | 36 | 43 | 45 | 37 | 43 | 34 | 40 | 0 | 0
2022-12-01 19:00 | 12 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 34 | 36 | 43 | 43 | 38 | 44 | 34 | 38 | 0 | 0
2022-12-01 20:00 | 12 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 34 | 35 | 43 | 43 | 37 | 42 | 34 | 37 | 0 | 0
2022-12-01 21:00 | 12 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 34 | 35 | 44 | 40 | 36 | 41 | 33 | 34 | 0 | 0
2022-12-01 22:00 | 12 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 34 | 34 | 45 | 43 | 35 | 40 | 32 | 32 | 0 | 0
2022-12-01 23:00 | 12 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 33 | 33 | 45 | 44 | 33 | 39 | 33 | 31 | 0 | 0
2022-12-02 | 12 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 34 | 32 | 43 | 40 | 34 | 40 | 33 | 31 | 0 | 0
2022-12-02 01:00 | 12 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 34 | 33 | 43 | 43 | 36 | 40 | 32 | 30 | 0 | 0
2022-12-02 02:00 | 12 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 35 | 33 | 42 | 44 | 35 | 42 | 32 | 28 | 0 | 0
2022-12-02 03:00 | 12 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 35 | 34 | 43 | 40 | 36 | 41 | 33 | 27 | 0 | 0
2022-12-02 04:00 | 12 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 36 | 34 | 42 | 43 | 38 | 40 | 30 | 27 | 0 | 0
2022-12-02 05:00 | 12 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 36 | 34 | 42 | 44 | 37 | 40 | 33 | 26 | 0 | 0
2022-12-02 06:00 | 12 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 36 | 34 | 42 | 45 | 37 | 39 | 31 | 23 | 0 | 0
2022-12-02 07:00 | 12 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 33 | 34 | 42 | 45 | 37 | 39 | 29 | 24 | 0 | 0
2022-12-02 08:00 | 12 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 33 | 34 | 42 | 44 | 40 | 39 | 33 | 28 | 0 | 0
2022-12-02 09:00 | 12 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 33 | 34 | 42 | 45 | 42 | 40 | 33 | 31 | 0 | 0
2022-12-02 10:00 | 12 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 32 | 34 | 42 | 47 | 45 | 41 | 36 | 33 | 0 | 0
2022-12-02 11:00 | 12 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 31 | 35 | 41 | 50 | 47 | 43 | 37 | 35 | 0 | 0
2022-12-02 12:00 | 12 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 30 | 35 | 41 | 51 | 50 | 45 | 39 | 36 | 0 | 0
2022-12-02 13:00 | 12 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 30 | 35 | 41 | 49 | 52 | 45 | 39 | 37 | 0 | 0
2022-12-02 14:00 | 12 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 29 | 34 | 40 | 49 | 51 | 44 | 39 | 38 | 0 | 0
2022-12-02 15:00 | 12 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 30 | 34 | 39 | 48 | 52 | 44 | 37 | 39 | 0 | 0
2022-12-02 16:00 | 12 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 27 | 32 | 39 | 47 | 47 | 42 | 34 | 37 | 0 | 0
2022-12-02 17:00 | 12 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 26 | 31 | 39 | 45 | 46 | 42 | 33 | 36 | 0 | 0
2022-12-02 18:00 | 12 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 24 | 29 | 38 | 43 | 43 | 41 | 31 | 35 | 0 | 0
2022-12-02 19:00 | 12 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 23 | 29 | 38 | 40 | 42 | 38 | 30 | 34 | 0 | 0
2022-12-02 20:00 | 12 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 23 | 30 | 38 | 39 | 45 | 36 | 29 | 33 | 0 | 0
2022-12-02 21:00 | 12 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 22 | 30 | 38 | 40 | 45 | 36 | 27 | 34 | 0 | 0
2022-12-02 22:00 | 12 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 22 | 30 | 37 | 38 | 44 | 35 | 25 | 34 | 0 | 0
2022-12-02 23:00 | 12 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 22 | 31 | 37 | 33 | 42 | 35 | 25 | 33 | 0 | 0
2022-12-03 | 12 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 22 | 31 | 37 | 35 | 40 | 35 | 25 | 32 | 0 | 0
2022-12-03 01:00 | 12 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 18 | 31 | 37 | 33 | 38 | 34 | 24 | 32 | 0 | 0
2022-12-03 02:00 | 12 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 19 | 30 | 37 | 32 | 36 | 34 | 23 | 32 | 0 | 0
2022-12-03 03:00 | 12 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 18 | 30 | 37 | 32 | 35 | 33 | 23 | 31 | 0 | 0
2022-12-03 04:00 | 12 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 19 | 30 | 37 | 31 | 35 | 34 | 23 | 32 | 0 | 0
2022-12-03 05:00 | 12 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 20 | 29 | 37 | 31 | 36 | 34 | 24 | 32 | 0 | 0
2022-12-03 06:00 | 12 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 22 | 29 | 35 | 29 | 36 | 36 | 26 | 31 | 0 | 0
2022-12-03 07:00 | 12 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 23 | 29 | 35 | 30 | 36 | 36 | 28 | 31 | 0 | 0
2022-12-03 08:00 | 12 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 23 | 29 | 36 | 33 | 37 | 34 | 27 | 32 | 0 | 0
2022-12-03 09:00 | 12 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 24 | 29 | 38 | 36 | 40 | 34 | 28 | 32 | 0 | 0
2022-12-03 10:00 | 12 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 25 | 29 | 39 | 40 | 41 | 34 | 29 | 33 | 0 | 0
2022-12-03 11:00 | 12 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 26 | 29 | 40 | 44 | 43 | 36 | 30 | 35 | 0 | 0
2022-12-03 12:00 | 12 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 26 | 29 | 43 | 43 | 47 | 37 | 31 | 35 | 0 | 0
2022-12-03 13:00 | 12 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 27 | 29 | 43 | 43 | 48 | 38 | 33 | 35 | 0 | 0
2022-12-03 14:00 | 12 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 28 | 29 | 42 | 44 | 49 | 37 | 33 | 35 | 0 | 0
2022-12-03 15:00 | 12 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 31 | 29 | 42 | 45 | 49 | 37 | 33 | 35 | 0 | 0
2022-12-03 16:00 | 12 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 34 | 28 | 34 | 43 | 48 | 36 | 37 | 34 | 0 | 0
2022-12-03 17:00 | 12 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 36 | 27 | 35 | 43 | 48 | 35 | 37 | 35 | 0 | 0
2022-12-03 18:00 | 12 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 37 | 26 | 33 | 44 | 49 | 34 | 37 | 37 | 0 | 0
2022-12-03 19:00 | 12 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 38 | 25 | 32 | 43 | 50 | 34 | 40 | 37 | 0 | 0
2022-12-03 20:00 | 12 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 38 | 24 | 32 | 40 | 51 | 33 | 41 | 40 | 0 | 0
2022-12-03 21:00 | 12 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 39 | 23 | 32 | 40 | 52 | 33 | 41 | 39 | 0 | 0
2022-12-03 22:00 | 12 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 40 | 23 | 33 | 40 | 52 | 33 | 41 | 40 | 0 | 0
2022-12-03 23:00 | 12 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 41 | 23 | 33 | 40 | 52 | 32 | 41 | 41 | 0 | 0
2022-12-04 | 12 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 41 | 23 | 33 | 39 | 52 | 31 | 41 | 41 | 0 | 0
2022-12-04 01:00 | 12 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 44 | 43 | 23 | 32 | 38 | 52 | 31 | 43 | 41 | 0 | 0
2022-12-04 02:00 | 12 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 43 | 23 | 35 | 36 | 52 | 30 | 44 | 42 | 0 | 0
2022-12-04 03:00 | 12 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 43 | 23 | 35 | 34 | 51 | 30 | 43 | 42 | 0 | 0
2022-12-04 04:00 | 12 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 44 | 23 | 36 | 33 | 52 | 30 | 44 | 43 | 0 | 0
2022-12-04 05:00 | 12 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 44 | 22 | 36 | 31 | 52 | 30 | 44 | 44 | 0 | 0
2022-12-04 06:00 | 12 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 45 | 22 | 37 | 31 | 54 | 29 | 44 | 46 | 0 | 0
2022-12-04 07:00 | 12 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 46 | 22 | 37 | 31 | 55 | 28 | 45 | 47 | 0 | 0
2022-12-04 08:00 | 12 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 47 | 21 | 37 | 32 | 55 | 30 | 48 | 48 | 0 | 0
2022-12-04 09:00 | 12 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 50 | 49 | 21 | 38 | 36 | 57 | 31 | 49 | 49 | 0 | 0
2022-12-04 10:00 | 12 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 51 | 22 | 39 | 38 | 58 | 33 | 54 | 50 | 0 | 0
2022-12-04 11:00 | 12 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 54 | 23 | 39 | 40 | 62 | 34 | 57 | 53 | 0 | 0
2022-12-04 12:00 | 12 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 63 | 55 | 24 | 38 | 43 | 66 | 36 | 60 | 51 | 0 | 0
2022-12-04 13:00 | 12 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 64 | 55 | 24 | 38 | 44 | 67 | 37 | 59 | 57 | 0 | 0
2022-12-04 14:00 | 12 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 65 | 54 | 24 | 38 | 45 | 68 | 37 | 55 | 56 | 0 | 0
2022-12-04 15:00 | 12 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 61 | 49 | 24 | 38 | 44 | 68 | 37 | 53 | 51 | 0 | 0
2022-12-04 16:00 | 12 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 58 | 43 | 23 | 37 | 40 | 66 | 35 | 50 | 47 | 0 | 0
2022-12-04 17:00 | 12 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 55 | 40 | 23 | 37 | 38 | 63 | 34 | 46 | 45 | 0 | 0
2022-12-04 18:00 | 12 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 36 | 22 | 36 | 35 | 60 | 31 | 45 | 42 | 0 | 0
2022-12-04 19:00 | 12 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 51 | 34 | 20 | 35 | 32 | 58 | 30 | 42 | 41 | 0 | 0
2022-12-04 20:00 | 12 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 35 | 17 | 36 | 32 | 55 | 30 | 40 | 41 | 0 | 0
2022-12-04 21:00 | 12 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 35 | 15 | 36 | 35 | 50 | 31 | 39 | 40 | 0 | 0
2022-12-04 22:00 | 12 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 35 | 13 | 35 | 34 | 47 | 31 | 39 | 40 | 0 | 0
2022-12-04 23:00 | 12 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 34 | 12 | 36 | 34 | 45 | 31 | 39 | 40 | 0 | 0
2022-12-05 | 12 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 34 | 10 | 36 | 35 | 44 | 31 | 38 | 40 | 0 | 0
2022-12-05 01:00 | 12 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 34 | 13 | 36 | 35 | 43 | 31 | 37 | 40 | 0 | 0
2022-12-05 02:00 | 12 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 32 | 15 | 36 | 35 | 44 | 32 | 37 | 39 | 0 | 0
2022-12-05 03:00 | 12 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 30 | 18 | 36 | 36 | 44 | 32 | 36 | 38 | 0 | 0
2022-12-05 04:00 | 12 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 32 | 19 | 36 | 34 | 45 | 33 | 34 | 37 | 0 | 0
2022-12-05 05:00 | 12 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 31 | 20 | 35 | 33 | 45 | 33 | 34 | 36 | 0 | 0
2022-12-05 06:00 | 12 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 31 | 21 | 35 | 32 | 45 | 35 | 34 | 36 | 0 | 0
2022-12-05 07:00 | 12 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 29 | 21 | 35 | 32 | 45 | 34 | 34 | 37 | 0 | 0
2022-12-05 08:00 | 12 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 32 | 20 | 34 | 32 | 46 | 34 | 35 | 37 | 0 | 0
2022-12-05 09:00 | 12 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 33 | 20 | 34 | 32 | 47 | 34 | 36 | 40 | 0 | 0
2022-12-05 10:00 | 12 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 37 | 21 | 35 | 33 | 48 | 35 | 37 | 41 | 0 | 0
2022-12-05 11:00 | 12 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 38 | 21 | 35 | 33 | 48 | 35 | 38 | 42 | 0 | 0
2022-12-05 12:00 | 12 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 39 | 22 | 35 | 34 | 48 | 35 | 40 | 45 | 0 | 0
2022-12-05 13:00 | 12 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 40 | 23 | 35 | 35 | 49 | 35 | 41 | 46 | 0 | 0
2022-12-05 14:00 | 12 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 40 | 23 | 36 | 35 | 49 | 40 | 41 | 47 | 0 | 0
2022-12-05 15:00 | 12 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 41 | 24 | 36 | 36 | 48 | 40 | 41 | 46 | 0 | 0
2022-12-05 16:00 | 12 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 39 | 25 | 35 | 36 | 45 | 40 | 39 | 39 | 0 | 0
2022-12-05 17:00 | 12 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 36 | 26 | 35 | 36 | 44 | 46 | 36 | 38 | 0 | 0
2022-12-05 18:00 | 12 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 36 | 27 | 35 | 37 | 41 | 44 | 36 | 35 | 0 | 0
2022-12-05 19:00 | 12 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 35 | 28 | 35 | 37 | 40 | 41 | 35 | 34 | 0 | 0
2022-12-05 20:00 | 12 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 36 | 29 | 35 | 38 | 38 | 38 | 32 | 33 | 0 | 0
2022-12-05 21:00 | 12 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 36 | 30 | 35 | 37 | 39 | 37 | 34 | 32 | 0 | 0
2022-12-05 22:00 | 12 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 36 | 30 | 35 | 36 | 40 | 35 | 35 | 32 | 0 | 0
2022-12-05 23:00 | 12 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 37 | 29 | 33 | 37 | 39 | 34 | 32 | 30 | 0 | 0
2022-12-06 | 12 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 37 | 29 | 35 | 37 | 36 | 33 | 29 | 29 | 0 | 0
2022-12-06 01:00 | 12 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 36 | 27 | 35 | 37 | 36 | 32 | 31 | 28 | 0 | 0
2022-12-06 02:00 | 12 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 36 | 24 | 35 | 37 | 36 | 31 | 29 | 28 | 0 | 0
2022-12-06 03:00 | 12 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 33 | 22 | 33 | 37 | 36 | 30 | 27 | 26 | 0 | 0
2022-12-06 04:00 | 12 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 35 | 22 | 32 | 37 | 36 | 29 | 28 | 28 | 0 | 0
2022-12-06 05:00 | 12 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 34 | 21 | 31 | 37 | 36 | 29 | 28 | 27 | 0 | 0
2022-12-06 06:00 | 12 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 34 | 21 | 31 | 36 | 36 | 28 | 27 | 25 | 0 | 0
2022-12-06 07:00 | 12 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 34 | 21 | 32 | 36 | 37 | 28 | 27 | 25 | 0 | 0
2022-12-06 08:00 | 12 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 38 | 21 | 32 | 36 | 42 | 28 | 32 | 28 | 0 | 0
2022-12-06 09:00 | 12 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 40 | 21 | 33 | 36 | 45 | 28 | 35 | 31 | 0 | 0
2022-12-06 10:00 | 12 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 43 | 20 | 33 | 37 | 50 | 29 | 42 | 35 | 0 | 0
2022-12-06 11:00 | 12 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 46 | 20 | 34 | 36 | 53 | 30 | 46 | 40 | 0 | 0
2022-12-06 12:00 | 12 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 40 | 19 | 35 | 35 | 56 | 30 | 48 | 45 | 0 | 0
2022-12-06 13:00 | 12 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 47 | 18 | 36 | 35 | 58 | 29 | 49 | 48 | 0 | 0
2022-12-06 14:00 | 12 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 47 | 18 | 35 | 35 | 58 | 28 | 49 | 52 | 0 | 0
2022-12-06 15:00 | 12 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 45 | 17 | 35 | 35 | 55 | 27 | 47 | 51 | 0 | 0
2022-12-06 16:00 | 12 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 41 | 17 | 32 | 34 | 49 | 26 | 45 | 47 | 0 | 0
2022-12-06 17:00 | 12 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 40 | 16 | 30 | 33 | 48 | 25 | 43 | 40 | 0 | 0
2022-12-06 18:00 | 12 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 39 | 16 | 29 | 33 | 46 | 25 | 39 | 39 | 0 | 0
2022-12-06 19:00 | 12 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 39 | 16 | 30 | 33 | 43 | 25 | 37 | 36 | 0 | 0
2022-12-06 20:00 | 12 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 37 | 17 | 32 | 30 | 40 | 24 | 35 | 33 | 0 | 0
2022-12-06 21:00 | 12 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 36 | 17 | 32 | 30 | 40 | 19 | 35 | 33 | 0 | 0
2022-12-06 22:00 | 12 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 37 | 17 | 33 | 30 | 42 | 14 | 34 | 32 | 0 | 0
2022-12-06 23:00 | 12 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 37 | 16 | 33 | 30 | 41 | 11 | 32 | 31 | 0 | 0
2022-12-07 | 12 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 51 | 16 | 34 | 30 | 36 | 10 | 31 | 31 | 0 | 0
2022-12-07 01:00 | 12 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 37 | 14 | 34 | 28 | 39 | 9 | 31 | 29 | 0 | 0
2022-12-07 02:00 | 12 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 36 | 12 | 34 | 27 | 37 | 8 | 31 | 29 | 0 | 0
2022-12-07 03:00 | 12 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 35 | 10 | 35 | 25 | 38 | 7 | 30 | 29 | 0 | 0
2022-12-07 04:00 | 12 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 34 | 9 | 35 | 24 | 36 | 7 | 28 | 27 | 0 | 0
2022-12-07 05:00 | 12 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 33 | 9 | 35 | 22 | 38 | 7 | 27 | 29 | 0 | 0
2022-12-07 06:00 | 12 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 34 | 8 | 35 | 20 | 36 | 7 | 28 | 27 | 0 | 0
2022-12-07 07:00 | 12 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 34 | 8 | 35 | 19 | 39 | 7 | 28 | 29 | 0 | 0
2022-12-07 08:00 | 12 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 36 | 9 | 36 | 19 | 44 | 7 | 31 | 31 | 0 | 0
2022-12-07 09:00 | 12 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 37 | 9 | 37 | 22 | 48 | 9 | 34 | 33 | 0 | 0
2022-12-07 10:00 | 12 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 38 | 10 | 40 | 24 | 52 | 10 | 35 | 35 | 0 | 0
2022-12-07 11:00 | 12 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 39 | 10 | 40 | 26 | 54 | 12 | 38 | 37 | 0 | 0
2022-12-07 12:00 | 12 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 40 | 11 | 41 | 29 | 56 | 14 | 40 | 39 | 0 | 0
2022-12-07 13:00 | 12 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 41 | 12 | 42 | 30 | 58 | 16 | 44 | 42 | 0 | 0
2022-12-07 14:00 | 12 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 42 | 13 | 42 | 30 | 57 | 17 | 44 | 42 | 0 | 0
2022-12-07 15:00 | 12 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 40 | 14 | 42 | 30 | 55 | 15 | 47 | 47 | 0 | 0
2022-12-07 16:00 | 12 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 39 | 14 | 42 | 27 | 54 | 15 | 47 | 47 | 0 | 0
2022-12-07 17:00 | 12 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 39 | 13 | 42 | 26 | 54 | 14 | 47 | 48 | 0 | 0
2022-12-07 18:00 | 12 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 41 | 13 | 42 | 24 | 52 | 13 | 46 | 45 | 0 | 0
2022-12-07 19:00 | 12 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 41 | 13 | 42 | 24 | 52 | 13 | 46 | 46 | 0 | 0
2022-12-07 20:00 | 12 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 43 | 13 | 42 | 22 | 51 | 14 | 46 | 48 | 0 | 0
2022-12-07 21:00 | 12 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 46 | 13 | 42 | 21 | 51 | 15 | 46 | 49 | 0 | 0
2022-12-07 22:00 | 12 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 46 | 13 | 44 | 22 | 51 | 15 | 47 | 50 | 0 | 0
2022-12-07 23:00 | 12 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 45 | 12 | 44 | 21 | 49 | 15 | 46 | 50 | 0 | 0
2022-12-08 | 12 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 46 | 12 | 44 | 19 | 49 | 15 | 44 | 50 | 0 | 0
2022-12-08 01:00 | 12 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 46 | 11 | 44 | 19 | 50 | 15 | 45 | 49 | 0 | 0
2022-12-08 02:00 | 12 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 49 | 44 | 11 | 42 | 20 | 50 | 15 | 46 | 49 | 0 | 0
2022-12-08 03:00 | 12 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 44 | 10 | 42 | 20 | 49 | 15 | 46 | 50 | 0 | 0
2022-12-08 04:00 | 12 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 45 | 9 | 41 | 20 | 49 | 14 | 46 | 49 | 0 | 0
2022-12-08 05:00 | 12 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 45 | 8 | 39 | 19 | 50 | 13 | 44 | 48 | 0 | 0
2022-12-08 06:00 | 12 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 47 | 46 | 7 | 38 | 19 | 50 | 10 | 46 | 47 | 0 | 0
2022-12-08 07:00 | 12 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 46 | 7 | 38 | 18 | 51 | 11 | 45 | 46 | 0 | 0
2022-12-08 08:00 | 12 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 46 | 8 | 38 | 19 | 52 | 14 | 46 | 46 | 0 | 0
2022-12-08 09:00 | 12 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 47 | 8 | 38 | 20 | 53 | 19 | 46 | 47 | 0 | 0
2022-12-08 10:00 | 12 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 50 | 47 | 11 | 38 | 23 | 56 | 22 | 47 | 49 | 0 | 0
2022-12-08 11:00 | 12 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 48 | 15 | 38 | 25 | 60 | 25 | 47 | 49 | 0 | 0
2022-12-08 12:00 | 12 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 48 | 18 | 37 | 29 | 63 | 26 | 48 | 48 | 0 | 0
2022-12-08 13:00 | 12 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 49 | 18 | 35 | 30 | 64 | 27 | 49 | 49 | 0 | 0
2022-12-08 14:00 | 12 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 54 | 50 | 19 | 35 | 31 | 63 | 29 | 50 | 49 | 0 | 0
2022-12-08 15:00 | 12 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 52 | 51 | 19 | 33 | 31 | 63 | 30 | 49 | 49 | 0 | 0
2022-12-08 16:00 | 12 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 48 | 19 | 31 | 30 | 61 | 31 | 50 | 48 | 0 | 0
2022-12-08 17:00 | 12 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 53 | 42 | 18 | 30 | 31 | 61 | 32 | 48 | 49 | 0 | 0
2022-12-08 18:00 | 12 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 40 | 18 | 30 | 32 | 63 | 33 | 48 | 47 | 0 | 0
2022-12-08 19:00 | 12 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 39 | 18 | 30 | 31 | 63 | 30 | 48 | 48 | 0 | 0
2022-12-08 20:00 | 12 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 52 | 39 | 18 | 29 | 31 | 65 | 30 | 47 | 49 | 0 | 0
2022-12-08 21:00 | 12 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 38 | 18 | 30 | 31 | 60 | 31 | 43 | 48 | 0 | 0
2022-12-08 22:00 | 12 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 38 | 18 | 30 | 32 | 59 | 32 | 41 | 45 | 0 | 0
2022-12-08 23:00 | 12 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 35 | 19 | 29 | 32 | 58 | 31 | 40 | 44 | 0 | 0
2022-12-09 | 12 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 54 | 34 | 19 | 28 | 32 | 60 | 32 | 40 | 43 | 0 | 0
2022-12-09 01:00 | 12 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 33 | 21 | 28 | 33 | 60 | 33 | 39 | 43 | 0 | 0
2022-12-09 02:00 | 12 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 33 | 22 | 26 | 35 | 59 | 36 | 38 | 42 | 0 | 0
2022-12-09 03:00 | 12 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 53 | 33 | 24 | 26 | 32 | 60 | 37 | 35 | 40 | 0 | 0
2022-12-09 04:00 | 12 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 48 | 32 | 26 | 24 | 32 | 60 | 37 | 35 | 39 | 0 | 0
2022-12-09 05:00 | 12 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 46 | 32 | 27 | 23 | 33 | 62 | 36 | 34 | 38 | 0 | 0
2022-12-09 06:00 | 12 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 31 | 29 | 23 | 33 | 61 | 36 | 34 | 37 | 0 | 0
2022-12-09 07:00 | 12 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 30 | 28 | 24 | 33 | 51 | 33 | 33 | 37 | 0 | 0
2022-12-09 08:00 | 12 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 43 | 28 | 26 | 24 | 34 | 50 | 27 | 33 | 37 | 0 | 0
2022-12-09 09:00 | 12 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 28 | 25 | 25 | 34 | 48 | 26 | 33 | 36 | 0 | 0
2022-12-09 10:00 | 12 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 28 | 21 | 27 | 34 | 47 | 24 | 33 | 35 | 0 | 0
2022-12-09 11:00 | 12 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 28 | 18 | 27 | 35 | 46 | 21 | 33 | 35 | 0 | 0
2022-12-09 12:00 | 12 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 27 | 14 | 28 | 41 | 45 | 21 | 32 | 35 | 0 | 0
2022-12-09 13:00 | 12 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 27 | 12 | 29 | 40 | 43 | 18 | 31 | 33 | 0 | 0
2022-12-09 14:00 | 12 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 27 | 9 | 29 | 38 | 42 | 15 | 30 | 32 | 0 | 0
2022-12-09 15:00 | 12 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 26 | 7 | 29 | 35 | 41 | 13 | 29 | 32 | 0 | 0
2022-12-09 16:00 | 12 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 26 | 5 | 28 | 29 | 40 | 11 | 27 | 31 | 0 | 0
2022-12-09 17:00 | 12 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 24 | 2 | 27 | 26 | 38 | 9 | 26 | 31 | 0 | 0
2022-12-09 18:00 | 12 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 24 | 0 | 26 | 23 | 36 | 6 | 26 | 32 | 0 | 0
2022-12-09 19:00 | 12 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 24 | -1 | 25 | 21 | 34 | 5 | 26 | 32 | 0 | 0
2022-12-09 20:00 | 12 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 24 | -2 | 25 | 19 | 34 | 4 | 26 | 30 | 0 | 0
2022-12-09 21:00 | 12 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 22 | -3 | 25 | 18 | 34 | 4 | 26 | 29 | 0 | 0
2022-12-09 22:00 | 12 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 21 | -3 | 24 | 18 | 35 | 4 | 24 | 28 | 0 | 0
2022-12-09 23:00 | 12 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 19 | -2 | 24 | 17 | 34 | 4 | 23 | 27 | 0 | 0
2022-12-10 | 12 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 17 | -2 | 23 | 15 | 32 | 4 | 22 | 25 | 0 | 0
2022-12-10 01:00 | 12 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 16 | -2 | 26 | 15 | 31 | 4 | 21 | 25 | 0 | 0
2022-12-10 02:00 | 12 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 16 | -1 | 23 | 15 | 29 | 4 | 21 | 25 | 0 | 0
2022-12-10 03:00 | 12 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 16 | -1 | 23 | 15 | 28 | 4 | 20 | 25 | 0 | 0
2022-12-10 04:00 | 12 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 16 | -1 | 23 | 16 | 29 | 4 | 19 | 24 | 0 | 0
2022-12-10 05:00 | 12 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 15 | -1 | 24 | 16 | 28 | 4 | 19 | 22 | 0 | 0
2022-12-10 06:00 | 12 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 16 | -1 | 24 | 16 | 26 | 5 | 18 | 23 | 0 | 0
2022-12-10 07:00 | 12 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 15 | 0 | 24 | 16 | 27 | 4 | 18 | 23 | 0 | 0
2022-12-10 08:00 | 12 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 16 | 0 | 25 | 17 | 29 | 5 | 19 | 23 | 0 | 0
2022-12-10 09:00 | 12 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 17 | 1 | 25 | 18 | 31 | 6 | 21 | 23 | 0 | 0
2022-12-10 10:00 | 12 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 18 | 3 | 26 | 19 | 32 | 7 | 22 | 24 | 0 | 0
2022-12-10 11:00 | 12 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 18 | 6 | 26 | 21 | 32 | 9 | 22 | 24 | 0 | 0
2022-12-10 12:00 | 12 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 19 | 8 | 26 | 24 | 31 | 11 | 22 | 25 | 0 | 0
2022-12-10 13:00 | 12 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 19 | 8 | 27 | 25 | 29 | 11 | 23 | 25 | 0 | 0
2022-12-10 14:00 | 12 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 18 | 9 | 27 | 24 | 30 | 12 | 22 | 24 | 0 | 0
2022-12-10 15:00 | 12 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 18 | 9 | 28 | 23 | 29 | 12 | 21 | 24 | 0 | 0
2022-12-10 16:00 | 12 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 16 | 7 | 28 | 22 | 28 | 12 | 19 | 23 | 0 | 0
2022-12-10 17:00 | 12 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 15 | 6 | 28 | 20 | 27 | 11 | 18 | 23 | 0 | 0
2022-12-10 18:00 | 12 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 14 | 4 | 28 | 20 | 26 | 11 | 18 | 23 | 0 | 0
2022-12-10 19:00 | 12 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 13 | 4 | 28 | 18 | 26 | 11 | 18 | 23 | 0 | 0
2022-12-10 20:00 | 12 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 14 | 3 | 28 | 18 | 25 | 11 | 16 | 22 | 0 | 0
2022-12-10 21:00 | 12 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 14 | 3 | 28 | 17 | 24 | 10 | 16 | 21 | 0 | 0
2022-12-10 22:00 | 12 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 14 | 2 | 29 | 17 | 23 | 10 | 16 | 20 | 0 | 0
2022-12-10 23:00 | 12 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 15 | 2 | 29 | 17 | 22 | 10 | 15 | 18 | 0 | 0
2022-12-11 | 12 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 15 | 1 | 29 | 17 | 23 | 10 | 15 | 18 | 0 | 0
2022-12-11 01:00 | 12 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 15 | -3 | 29 | 17 | 22 | 9 | 14 | 18 | 0 | 0
2022-12-11 02:00 | 12 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 15 | -7 | 28 | 18 | 22 | 9 | 14 | 16 | 0 | 0
2022-12-11 03:00 | 12 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 15 | -11 | 29 | 18 | 21 | 8 | 14 | 16 | 0 | 0
2022-12-11 04:00 | 12 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 15 | -10 | 29 | 17 | 20 | 7 | 13 | 15 | 0 | 0
2022-12-11 05:00 | 12 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 15 | -9 | 29 | 16 | 19 | 7 | 12 | 15 | 0 | 0
2022-12-11 06:00 | 12 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 14 | -8 | 29 | 16 | 20 | 7 | 13 | 15 | 0 | 0
2022-12-11 07:00 | 12 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 13 | -6 | 30 | 15 | 21 | 7 | 13 | 16 | 0 | 0
2022-12-11 08:00 | 12 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 14 | -3 | 30 | 15 | 25 | 8 | 14 | 17 | 0 | 0
2022-12-11 09:00 | 12 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 15 | -1 | 30 | 16 | 27 | 8 | 15 | 18 | 0 | 0
2022-12-11 10:00 | 12 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 17 | 1 | 31 | 18 | 29 | 10 | 17 | 21 | 0 | 0
2022-12-11 11:00 | 12 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 18 | 4 | 31 | 20 | 31 | 12 | 19 | 23 | 0 | 0
2022-12-11 12:00 | 12 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 21 | 6 | 31 | 23 | 33 | 14 | 21 | 25 | 0 | 0
2022-12-11 13:00 | 12 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 21 | 7 | 32 | 23 | 34 | 15 | 22 | 27 | 0 | 0
2022-12-11 14:00 | 12 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 21 | 7 | 33 | 24 | 34 | 16 | 23 | 28 | 0 | 0
2022-12-11 15:00 | 12 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 20 | 8 | 33 | 23 | 32 | 17 | 22 | 28 | 0 | 0
2022-12-11 16:00 | 12 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 20 | 5 | 33 | 21 | 30 | 16 | 20 | 27 | 0 | 0
2022-12-11 17:00 | 12 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 19 | 1 | 32 | 20 | 28 | 12 | 20 | 27 | 0 | 0
2022-12-11 18:00 | 12 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 18 | -2 | 32 | 19 | 29 | 10 | 18 | 28 | 0 | 0
2022-12-11 19:00 | 12 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 17 | -4 | 32 | 18 | 28 | 9 | 19 | 28 | 0 | 0
2022-12-11 20:00 | 12 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 17 | -6 | 32 | 18 | 29 | 8 | 21 | 27 | 0 | 0
2022-12-11 21:00 | 12 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 19 | -8 | 32 | 17 | 28 | 6 | 20 | 27 | 0 | 0
2022-12-11 22:00 | 12 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 20 | -7 | 31 | 16 | 28 | 6 | 19 | 27 | 0 | 0
2022-12-11 23:00 | 12 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 22 | -5 | 31 | 15 | 27 | 6 | 19 | 26 | 0 | 0
2022-12-12 | 12 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 21 | -4 | 30 | 14 | 27 | 6 | 19 | 26 | 0 | 0
2022-12-12 01:00 | 12 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 21 | -2 | 31 | 14 | 29 | 7 | 20 | 26 | 0 | 0
2022-12-12 02:00 | 12 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 21 | -1 | 31 | 14 | 25 | 10 | 21 | 26 | 0 | 0
2022-12-12 03:00 | 12 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 22 | 1 | 31 | 12 | 25 | 11 | 21 | 26 | 0 | 0
2022-12-12 04:00 | 12 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 22 | 3 | 31 | 14 | 27 | 12 | 21 | 27 | 0 | 0
2022-12-12 05:00 | 12 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 22 | 4 | 31 | 17 | 26 | 14 | 22 | 27 | 0 | 0
2022-12-12 06:00 | 12 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 23 | 6 | 31 | 16 | 24 | 15 | 23 | 27 | 0 | 0
2022-12-12 07:00 | 12 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 24 | 7 | 31 | 16 | 26 | 17 | 22 | 27 | 0 | 0
2022-12-12 08:00 | 12 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 25 | 9 | 30 | 16 | 30 | 19 | 24 | 27 | 0 | 0
2022-12-12 09:00 | 12 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 27 | 10 | 31 | 19 | 32 | 22 | 26 | 28 | 0 | 0
2022-12-12 10:00 | 12 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 30 | 12 | 31 | 24 | 34 | 24 | 28 | 30 | 0 | 0
2022-12-12 11:00 | 12 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 30 | 14 | 31 | 26 | 38 | 29 | 30 | 32 | 0 | 0
2022-12-12 12:00 | 12 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 31 | 16 | 31 | 29 | 40 | 31 | 32 | 33 | 0 | 0
2022-12-12 13:00 | 12 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 32 | 17 | 31 | 31 | 43 | 32 | 33 | 37 | 0 | 0
2022-12-12 14:00 | 12 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 33 | 19 | 30 | 31 | 42 | 34 | 33 | 37 | 0 | 0
2022-12-12 15:00 | 12 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 33 | 20 | 30 | 32 | 41 | 34 | 32 | 37 | 0 | 0
2022-12-12 16:00 | 12 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 32 | 21 | 30 | 32 | 38 | 34 | 32 | 36 | 0 | 0
2022-12-12 17:00 | 12 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 31 | 22 | 30 | 33 | 35 | 35 | 31 | 35 | 0 | 0
2022-12-12 18:00 | 12 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 29 | 23 | 30 | 34 | 34 | 36 | 31 | 34 | 0 | 0
2022-12-12 19:00 | 12 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 29 | 24 | 29 | 34 | 34 | 36 | 29 | 34 | 0 | 0
2022-12-12 20:00 | 12 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 29 | 24 | 29 | 34 | 35 | 36 | 29 | 33 | 0 | 0
2022-12-12 21:00 | 12 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 30 | 25 | 29 | 33 | 35 | 37 | 29 | 35 | 0 | 0
2022-12-12 22:00 | 12 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 30 | 26 | 29 | 33 | 30 | 38 | 30 | 35 | 0 | 0
2022-12-12 23:00 | 12 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 30 | 26 | 29 | 32 | 28 | 38 | 30 | 35 | 0 | 0
2022-12-13 | 12 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 28 | 27 | 29 | 33 | 29 | 38 | 30 | 35 | 0 | 0
2022-12-13 01:00 | 12 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 29 | 28 | 29 | 33 | 30 | 38 | 28 | 33 | 0 | 0
2022-12-13 02:00 | 12 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 29 | 28 | 29 | 33 | 29 | 38 | 28 | 33 | 0 | 0
2022-12-13 03:00 | 12 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 30 | 29 | 28 | 33 | 28 | 39 | 28 | 32 | 0 | 0
2022-12-13 04:00 | 12 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 30 | 30 | 28 | 33 | 27 | 38 | 29 | 31 | 0 | 0
2022-12-13 05:00 | 12 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 31 | 30 | 28 | 33 | 29 | 38 | 28 | 32 | 0 | 0
2022-12-13 06:00 | 12 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 31 | 31 | 28 | 33 | 30 | 38 | 31 | 31 | 0 | 0
2022-12-13 07:00 | 12 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 31 | 31 | 28 | 33 | 31 | 37 | 31 | 32 | 0 | 0
2022-12-13 08:00 | 12 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 32 | 32 | 28 | 34 | 37 | 38 | 33 | 34 | 0 | 0
2022-12-13 09:00 | 12 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 34 | 32 | 30 | 35 | 40 | 38 | 35 | 36 | 0 | 0
2022-12-13 10:00 | 12 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 36 | 33 | 30 | 35 | 43 | 39 | 41 | 40 | 0 | 0
2022-12-13 11:00 | 12 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 38 | 33 | 30 | 36 | 47 | 43 | 42 | 44 | 0 | 0
2022-12-13 12:00 | 12 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 38 | 34 | 32 | 38 | 49 | 47 | 41 | 48 | 0 | 0
2022-12-13 13:00 | 12 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 38 | 35 | 32 | 40 | 51 | 48 | 41 | 48 | 0 | 0
2022-12-13 14:00 | 12 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 38 | 36 | 33 | 40 | 51 | 49 | 42 | 48 | 0 | 0
2022-12-13 15:00 | 12 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 38 | 37 | 33 | 38 | 49 | 47 | 42 | 47 | 0 | 0
2022-12-13 16:00 | 12 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 37 | 38 | 32 | 36 | 46 | 46 | 41 | 44 | 0 | 0
2022-12-13 17:00 | 12 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 35 | 38 | 32 | 36 | 44 | 45 | 40 | 42 | 0 | 0
2022-12-13 18:00 | 12 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 32 | 39 | 32 | 34 | 42 | 45 | 38 | 40 | 0 | 0
2022-12-13 19:00 | 12 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 32 | 39 | 32 | 34 | 40 | 45 | 36 | 38 | 0 | 0
2022-12-13 20:00 | 12 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 31 | 39 | 32 | 33 | 44 | 46 | 34 | 37 | 0 | 0
2022-12-13 21:00 | 12 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 31 | 39 | 32 | 34 | 44 | 47 | 33 | 36 | 0 | 0
2022-12-13 22:00 | 12 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 30 | 39 | 32 | 34 | 42 | 47 | 32 | 35 | 0 | 0
2022-12-13 23:00 | 12 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 30 | 39 | 32 | 32 | 38 | 48 | 32 | 35 | 0 | 0
2022-12-14 | 12 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 29 | 39 | 31 | 32 | 38 | 49 | 31 | 34 | 0 | 0
2022-12-14 01:00 | 12 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 29 | 38 | 32 | 33 | 36 | 49 | 31 | 34 | 0 | 0
2022-12-14 02:00 | 12 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 28 | 38 | 32 | 32 | 36 | 48 | 30 | 34 | 0 | 0
2022-12-14 03:00 | 12 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 28 | 37 | 32 | 33 | 34 | 50 | 27 | 30 | 0 | 0
2022-12-14 04:00 | 12 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 27 | 37 | 32 | 33 | 34 | 51 | 27 | 30 | 0 | 0
2022-12-14 05:00 | 12 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 25 | 36 | 33 | 33 | 33 | 50 | 28 | 31 | 0 | 0
2022-12-14 06:00 | 12 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 26 | 36 | 32 | 33 | 33 | 50 | 28 | 30 | 0 | 0
2022-12-14 07:00 | 12 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 25 | 37 | 32 | 33 | 33 | 50 | 28 | 31 | 0 | 0
2022-12-14 08:00 | 12 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 25 | 37 | 34 | 34 | 35 | 51 | 28 | 30 | 0 | 0
2022-12-14 09:00 | 12 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 24 | 38 | 34 | 36 | 35 | 52 | 28 | 31 | 0 | 0
2022-12-14 10:00 | 12 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 26 | 39 | 34 | 37 | 36 | 51 | 28 | 33 | 0 | 0
2022-12-14 11:00 | 12 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 26 | 40 | 35 | 38 | 37 | 52 | 29 | 35 | 0 | 0
2022-12-14 12:00 | 12 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 27 | 41 | 35 | 38 | 39 | 54 | 31 | 34 | 0 | 0
2022-12-14 13:00 | 12 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 26 | 42 | 36 | 39 | 39 | 55 | 29 | 33 | 0 | 0
2022-12-14 14:00 | 12 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 27 | 44 | 36 | 39 | 37 | 56 | 30 | 35 | 0 | 0
2022-12-14 15:00 | 12 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 28 | 45 | 36 | 40 | 36 | 56 | 29 | 34 | 0 | 0
2022-12-14 16:00 | 12 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 26 | 44 | 35 | 39 | 34 | 56 | 27 | 31 | 0 | 0
2022-12-14 17:00 | 12 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 25 | 44 | 35 | 40 | 32 | 55 | 27 | 30 | 0 | 0
2022-12-14 18:00 | 12 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 25 | 43 | 34 | 41 | 31 | 56 | 26 | 28 | 0 | 0
2022-12-14 19:00 | 12 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 25 | 42 | 31 | 40 | 31 | 54 | 26 | 28 | 0 | 0
2022-12-14 20:00 | 12 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 25 | 42 | 29 | 41 | 31 | 48 | 25 | 27 | 0 | 0
2022-12-14 21:00 | 12 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 24 | 41 | 28 | 40 | 30 | 45 | 25 | 28 | 0 | 0
2022-12-14 22:00 | 12 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 24 | 39 | 30 | 40 | 30 | 41 | 25 | 24 | 0 | 0
2022-12-14 23:00 | 12 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 24 | 37 | 31 | 40 | 30 | 41 | 25 | 22 | 0 | 0
2022-12-15 | 12 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 23 | 35 | 31 | 40 | 30 | 39 | 25 | 22 | 0 | 0
2022-12-15 01:00 | 12 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 24 | 34 | 32 | 40 | 30 | 39 | 23 | 22 | 0 | 0
2022-12-15 02:00 | 12 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 23 | 33 | 32 | 41 | 30 | 39 | 22 | 23 | 0 | 0
2022-12-15 03:00 | 12 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 24 | 32 | 32 | 41 | 31 | 39 | 23 | 23 | 0 | 0
2022-12-15 04:00 | 12 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 24 | 32 | 32 | 41 | 31 | 39 | 24 | 24 | 0 | 0
2022-12-15 05:00 | 12 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 25 | 32 | 32 | 41 | 32 | 39 | 24 | 23 | 0 | 0
2022-12-15 06:00 | 12 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 25 | 32 | 32 | 45 | 32 | 38 | 25 | 23 | 0 | 0
2022-12-15 07:00 | 12 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 26 | 32 | 32 | 41 | 34 | 38 | 26 | 25 | 0 | 0
2022-12-15 08:00 | 12 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 28 | 32 | 32 | 44 | 35 | 37 | 28 | 27 | 0 | 0
2022-12-15 09:00 | 12 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 29 | 32 | 32 | 44 | 37 | 37 | 30 | 29 | 0 | 0
2022-12-15 10:00 | 12 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 30 | 32 | 33 | 44 | 40 | 37 | 33 | 35 | 0 | 0
2022-12-15 11:00 | 12 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 33 | 32 | 33 | 44 | 43 | 37 | 39 | 37 | 0 | 0
2022-12-15 12:00 | 12 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 45 | 35 | 32 | 34 | 44 | 47 | 37 | 42 | 41 | 0 | 0
2022-12-15 13:00 | 12 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 37 | 32 | 35 | 44 | 50 | 36 | 43 | 46 | 0 | 0
2022-12-15 14:00 | 12 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 40 | 31 | 36 | 44 | 51 | 37 | 43 | 49 | 0 | 0
2022-12-15 15:00 | 12 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 46 | 40 | 31 | 36 | 43 | 49 | 37 | 43 | 47 | 0 | 0
2022-12-15 16:00 | 12 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 37 | 31 | 36 | 42 | 44 | 37 | 41 | 43 | 0 | 0
2022-12-15 17:00 | 12 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 36 | 31 | 36 | 40 | 43 | 37 | 40 | 42 | 0 | 0
2022-12-15 18:00 | 12 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 37 | 31 | 35 | 39 | 41 | 36 | 40 | 38 | 0 | 0
2022-12-15 19:00 | 12 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 36 | 31 | 35 | 38 | 39 | 37 | 40 | 33 | 0 | 0
2022-12-15 20:00 | 12 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 36 | 30 | 35 | 37 | 40 | 36 | 38 | 29 | 0 | 0
2022-12-15 21:00 | 12 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 36 | 30 | 34 | 37 | 38 | 36 | 36 | 31 | 0 | 0
2022-12-15 22:00 | 12 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 36 | 29 | 34 | 36 | 36 | 35 | 37 | 28 | 0 | 0
2022-12-15 23:00 | 12 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 35 | 29 | 34 | 35 | 34 | 34 | 37 | 29 | 0 | 0
2022-12-16 | 12 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 34 | 28 | 34 | 34 | 34 | 33 | 36 | 31 | 0 | 0
2022-12-16 01:00 | 12 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 33 | 28 | 34 | 34 | 34 | 33 | 34 | 37 | 0 | 0
2022-12-16 02:00 | 12 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 34 | 27 | 34 | 33 | 31 | 33 | 36 | 37 | 0 | 0
2022-12-16 03:00 | 12 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 34 | 27 | 33 | 31 | 33 | 33 | 35 | 37 | 0 | 0
2022-12-16 04:00 | 12 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 32 | 27 | 33 | 30 | 31 | 33 | 34 | 36 | 0 | 0
2022-12-16 05:00 | 12 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 30 | 27 | 33 | 29 | 33 | 32 | 31 | 29 | 0 | 0
2022-12-16 06:00 | 12 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 31 | 27 | 33 | 30 | 34 | 33 | 32 | 28 | 0 | 0
2022-12-16 07:00 | 12 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 29 | 28 | 32 | 29 | 36 | 34 | 33 | 27 | 0 | 0
2022-12-16 08:00 | 12 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 32 | 30 | 31 | 30 | 37 | 34 | 35 | 27 | 0 | 0
2022-12-16 09:00 | 12 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 34 | 31 | 32 | 34 | 42 | 40 | 37 | 31 | 0 | 0
2022-12-16 10:00 | 12 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 36 | 35 | 33 | 39 | 47 | 44 | 39 | 36 | 0 | 0
2022-12-16 11:00 | 12 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 38 | 40 | 32 | 43 | 51 | 49 | 42 | 41 | 0 | 0
2022-12-16 12:00 | 12 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 48 | 40 | 44 | 32 | 47 | 54 | 54 | 43 | 43 | 0 | 0
2022-12-16 13:00 | 12 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 41 | 45 | 32 | 48 | 55 | 57 | 45 | 46 | 0 | 0
2022-12-16 14:00 | 12 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 49 | 42 | 45 | 32 | 48 | 54 | 57 | 44 | 48 | 0 | 0
2022-12-16 15:00 | 12 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 47 | 40 | 46 | 32 | 47 | 51 | 58 | 44 | 48 | 0 | 0
2022-12-16 16:00 | 12 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 44 | 39 | 43 | 31 | 39 | 48 | 55 | 40 | 47 | 0 | 0
2022-12-16 17:00 | 12 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 38 | 41 | 29 | 38 | 45 | 50 | 40 | 48 | 0 | 0
2022-12-16 18:00 | 12 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 39 | 38 | 26 | 36 | 44 | 49 | 39 | 47 | 0 | 0
2022-12-16 19:00 | 12 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 39 | 35 | 27 | 35 | 44 | 48 | 38 | 46 | 0 | 0
2022-12-16 20:00 | 12 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 39 | 32 | 27 | 34 | 45 | 46 | 39 | 46 | 0 | 0
2022-12-16 21:00 | 12 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 39 | 29 | 27 | 33 | 45 | 45 | 42 | 46 | 0 | 0
2022-12-16 22:00 | 12 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 40 | 29 | 27 | 31 | 42 | 43 | 41 | 43 | 0 | 0
2022-12-16 23:00 | 12 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 38 | 28 | 28 | 33 | 42 | 42 | 37 | 40 | 0 | 0
2022-12-17 | 12 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 34 | 28 | 27 | 32 | 43 | 41 | 35 | 40 | 0 | 0
2022-12-17 01:00 | 12 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 35 | 28 | 25 | 32 | 43 | 40 | 35 | 39 | 0 | 0
2022-12-17 02:00 | 12 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 35 | 28 | 25 | 32 | 43 | 38 | 35 | 41 | 0 | 0
2022-12-17 03:00 | 12 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 35 | 28 | 23 | 29 | 45 | 36 | 36 | 40 | 0 | 0
2022-12-17 04:00 | 12 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 34 | 28 | 23 | 32 | 43 | 36 | 35 | 39 | 0 | 0
2022-12-17 05:00 | 12 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 34 | 28 | 23 | 33 | 41 | 35 | 35 | 39 | 0 | 0
2022-12-17 06:00 | 12 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 33 | 28 | 23 | 34 | 40 | 34 | 35 | 38 | 0 | 0
2022-12-17 07:00 | 12 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 33 | 29 | 23 | 34 | 40 | 34 | 36 | 37 | 0 | 0
2022-12-17 08:00 | 12 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 33 | 30 | 23 | 34 | 42 | 35 | 36 | 38 | 0 | 0
2022-12-17 09:00 | 12 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 32 | 31 | 25 | 35 | 44 | 41 | 35 | 39 | 0 | 0
2022-12-17 10:00 | 12 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 32 | 32 | 27 | 36 | 43 | 47 | 35 | 39 | 0 | 0
2022-12-17 11:00 | 12 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 42 | 31 | 32 | 26 | 38 | 44 | 52 | 35 | 39 | 0 | 0
2022-12-17 12:00 | 12 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 32 | 33 | 26 | 40 | 43 | 56 | 34 | 35 | 0 | 0
2022-12-17 13:00 | 12 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 31 | 33 | 27 | 40 | 43 | 57 | 33 | 38 | 0 | 0
2022-12-17 14:00 | 12 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 29 | 33 | 28 | 41 | 43 | 57 | 29 | 38 | 0 | 0
2022-12-17 15:00 | 12 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 28 | 33 | 28 | 41 | 42 | 57 | 29 | 37 | 0 | 0
2022-12-17 16:00 | 12 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 27 | 33 | 28 | 39 | 40 | 54 | 30 | 35 | 0 | 0
2022-12-17 17:00 | 12 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 27 | 32 | 28 | 39 | 39 | 52 | 28 | 35 | 0 | 0
2022-12-17 18:00 | 12 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 26 | 32 | 27 | 39 | 38 | 50 | 28 | 34 | 0 | 0
2022-12-17 19:00 | 12 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 27 | 32 | 27 | 39 | 37 | 49 | 27 | 34 | 0 | 0
2022-12-17 20:00 | 12 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 25 | 32 | 26 | 39 | 37 | 48 | 27 | 34 | 0 | 0
2022-12-17 21:00 | 12 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 25 | 32 | 25 | 39 | 37 | 48 | 26 | 35 | 0 | 0
2022-12-17 22:00 | 12 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 25 | 33 | 24 | 39 | 38 | 48 | 26 | 35 | 0 | 0
2022-12-17 23:00 | 12 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 24 | 33 | 23 | 39 | 37 | 48 | 26 | 35 | 0 | 0
2022-12-18 | 12 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 23 | 34 | 23 | 38 | 37 | 47 | 27 | 35 | 0 | 0
2022-12-18 01:00 | 12 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 21 | 34 | 23 | 38 | 37 | 48 | 26 | 34 | 0 | 0
2022-12-18 02:00 | 12 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 20 | 34 | 21 | 37 | 37 | 50 | 26 | 33 | 0 | 0
2022-12-18 03:00 | 12 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 19 | 34 | 20 | 37 | 37 | 50 | 24 | 32 | 0 | 0
2022-12-18 04:00 | 12 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 19 | 34 | 20 | 37 | 37 | 49 | 22 | 32 | 0 | 0
2022-12-18 05:00 | 12 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 18 | 34 | 16 | 36 | 36 | 49 | 21 | 33 | 0 | 0
2022-12-18 06:00 | 12 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 18 | 34 | 18 | 35 | 35 | 49 | 21 | 33 | 0 | 0
2022-12-18 07:00 | 12 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 18 | 34 | 15 | 35 | 35 | 50 | 23 | 34 | 0 | 0
2022-12-18 08:00 | 12 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 20 | 35 | 16 | 35 | 38 | 49 | 24 | 36 | 0 | 0
2022-12-18 09:00 | 12 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 21 | 35 | 22 | 34 | 41 | 48 | 25 | 36 | 0 | 0
2022-12-18 10:00 | 12 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 22 | 35 | 25 | 34 | 41 | 49 | 25 | 37 | 0 | 0
2022-12-18 11:00 | 12 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 23 | 35 | 25 | 34 | 42 | 50 | 25 | 38 | 0 | 0
2022-12-18 12:00 | 12 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 24 | 35 | 27 | 36 | 44 | 49 | 25 | 38 | 0 | 0
2022-12-18 13:00 | 12 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 25 | 34 | 24 | 36 | 45 | 47 | 26 | 40 | 0 | 0
2022-12-18 14:00 | 12 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 25 | 33 | 21 | 36 | 43 | 47 | 27 | 40 | 0 | 0
2022-12-18 15:00 | 12 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 26 | 32 | 20 | 37 | 43 | 46 | 32 | 39 | 0 | 0
2022-12-18 16:00 | 12 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 23 | 31 | 22 | 37 | 42 | 45 | 29 | 37 | 0 | 0
2022-12-18 17:00 | 12 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 21 | 31 | 21 | 37 | 39 | 44 | 29 | 38 | 0 | 0
2022-12-18 18:00 | 12 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 20 | 30 | 22 | 36 | 37 | 49 | 29 | 38 | 0 | 0
2022-12-18 19:00 | 12 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 15 | 30 | 21 | 36 | 39 | 44 | 25 | 38 | 0 | 0
2022-12-18 20:00 | 12 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 14 | 29 | 21 | 36 | 40 | 44 | 23 | 36 | 0 | 0
2022-12-18 21:00 | 12 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 13 | 29 | 21 | 36 | 40 | 43 | 21 | 31 | 0 | 0
2022-12-18 22:00 | 12 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 12 | 29 | 21 | 36 | 38 | 42 | 18 | 29 | 0 | 0
2022-12-18 23:00 | 12 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 12 | 30 | 22 | 36 | 39 | 41 | 14 | 28 | 0 | 0
2022-12-19 | 12 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 12 | 30 | 22 | 36 | 37 | 41 | 13 | 26 | 0 | 0
2022-12-19 01:00 | 12 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 11 | 30 | 21 | 36 | 32 | 41 | 12 | 23 | 0 | 0
2022-12-19 02:00 | 12 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 10 | 29 | 21 | 36 | 30 | 40 | 11 | 23 | 0 | 0
2022-12-19 03:00 | 12 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 9 | 29 | 20 | 35 | 29 | 40 | 10 | 20 | 0 | 0
2022-12-19 04:00 | 12 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 8 | 29 | 19 | 35 | 27 | 40 | 9 | 18 | 0 | 0
2022-12-19 05:00 | 12 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 9 | 29 | 20 | 35 | 24 | 40 | 8 | 17 | 0 | 0
2022-12-19 06:00 | 12 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 9 | 29 | 23 | 36 | 24 | 40 | 7 | 17 | 0 | 0
2022-12-19 07:00 | 12 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 10 | 29 | 22 | 36 | 26 | 39 | 10 | 17 | 0 | 0
2022-12-19 08:00 | 12 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 11 | 30 | 22 | 37 | 28 | 40 | 10 | 18 | 0 | 0
2022-12-19 09:00 | 12 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 14 | 30 | 23 | 37 | 29 | 40 | 12 | 22 | 0 | 0
2022-12-19 10:00 | 12 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 16 | 30 | 24 | 38 | 31 | 41 | 14 | 26 | 0 | 0
2022-12-19 11:00 | 12 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 18 | 31 | 25 | 38 | 32 | 41 | 15 | 28 | 0 | 0
2022-12-19 12:00 | 12 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 18 | 31 | 27 | 38 | 32 | 42 | 16 | 31 | 0 | 0
2022-12-19 13:00 | 12 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 18 | 31 | 25 | 38 | 33 | 46 | 18 | 31 | 0 | 0
2022-12-19 14:00 | 12 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 18 | 31 | 23 | 38 | 34 | 45 | 19 | 31 | 0 | 0
2022-12-19 15:00 | 12 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 18 | 31 | 22 | 38 | 32 | 44 | 19 | 30 | 0 | 0
2022-12-19 16:00 | 12 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 17 | 31 | 20 | 38 | 31 | 42 | 18 | 27 | 0 | 0
2022-12-19 17:00 | 12 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 15 | 30 | 23 | 38 | 30 | 42 | 18 | 26 | 0 | 0
2022-12-19 18:00 | 12 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 16 | 30 | 23 | 37 | 28 | 42 | 16 | 25 | 0 | 0
2022-12-19 19:00 | 12 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 15 | 30 | 23 | 37 | 29 | 41 | 18 | 24 | 0 | 0
2022-12-19 20:00 | 12 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 14 | 30 | 23 | 37 | 28 | 39 | 17 | 24 | 0 | 0
2022-12-19 21:00 | 12 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 14 | 30 | 22 | 37 | 27 | 37 | 17 | 25 | 0 | 0
2022-12-19 22:00 | 12 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 13 | 30 | 22 | 36 | 29 | 35 | 17 | 24 | 0 | 0
2022-12-19 23:00 | 12 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 14 | 30 | 22 | 36 | 30 | 36 | 16 | 25 | 0 | 0
2022-12-20 | 12 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 15 | 30 | 22 | 36 | 31 | 36 | 16 | 25 | 0 | 0
2022-12-20 01:00 | 12 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 15 | 29 | 22 | 35 | 31 | 37 | 16 | 26 | 0 | 0
2022-12-20 02:00 | 12 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 16 | 29 | 22 | 35 | 31 | 37 | 17 | 26 | 0 | 0
2022-12-20 03:00 | 12 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 16 | 28 | 22 | 35 | 31 | 37 | 17 | 26 | 0 | 0
2022-12-20 04:00 | 12 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 17 | 28 | 23 | 35 | 31 | 38 | 17 | 26 | 0 | 0
2022-12-20 05:00 | 12 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 17 | 27 | 23 | 35 | 31 | 38 | 18 | 27 | 0 | 0
2022-12-20 06:00 | 12 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 17 | 27 | 23 | 35 | 31 | 38 | 18 | 27 | 0 | 0
2022-12-20 07:00 | 12 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 18 | 28 | 24 | 35 | 31 | 37 | 19 | 27 | 0 | 0
2022-12-20 08:00 | 12 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 18 | 28 | 25 | 36 | 31 | 38 | 19 | 27 | 0 | 0
2022-12-20 09:00 | 12 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 20 | 29 | 24 | 36 | 32 | 39 | 21 | 27 | 0 | 0
2022-12-20 10:00 | 12 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 22 | 29 | 24 | 36 | 32 | 40 | 21 | 27 | 0 | 0
2022-12-20 11:00 | 12 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 22 | 29 | 24 | 37 | 33 | 42 | 22 | 26 | 0 | 0
2022-12-20 12:00 | 12 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 23 | 29 | 24 | 36 | 33 | 43 | 23 | 27 | 0 | 0
2022-12-20 13:00 | 12 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 23 | 30 | 25 | 33 | 32 | 45 | 25 | 28 | 0 | 0
2022-12-20 14:00 | 12 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 24 | 30 | 23 | 34 | 32 | 45 | 25 | 28 | 0 | 0
2022-12-20 15:00 | 12 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 25 | 31 | 23 | 35 | 32 | 44 | 25 | 29 | 0 | 0
2022-12-20 16:00 | 12 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 26 | 31 | 22 | 35 | 32 | 43 | 25 | 29 | 0 | 0
2022-12-20 17:00 | 12 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 27 | 30 | 22 | 35 | 33 | 42 | 27 | 30 | 0 | 0
2022-12-20 18:00 | 12 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 28 | 30 | 22 | 36 | 34 | 40 | 29 | 30 | 0 | 0
2022-12-20 19:00 | 12 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 30 | 30 | 21 | 36 | 36 | 39 | 28 | 31 | 0 | 0
2022-12-20 20:00 | 12 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 30 | 30 | 18 | 36 | 37 | 40 | 29 | 32 | 0 | 0
2022-12-20 21:00 | 12 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 31 | 30 | 17 | 36 | 39 | 39 | 30 | 33 | 0 | 0
2022-12-20 22:00 | 12 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 32 | 30 | 16 | 37 | 40 | 38 | 30 | 34 | 0 | 0
2022-12-20 23:00 | 12 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 34 | 31 | 14 | 37 | 43 | 36 | 32 | 35 | 0 | 0
2022-12-21 | 12 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 34 | 31 | 13 | 36 | 44 | 35 | 32 | 35 | 0 | 0
2022-12-21 01:00 | 12 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 34 | 31 | 14 | 37 | 44 | 35 | 32 | 36 | 0 | 0
2022-12-21 02:00 | 12 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 35 | 31 | 14 | 37 | 44 | 34 | 32 | 35 | 0 | 0
2022-12-21 03:00 | 12 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 36 | 31 | 14 | 37 | 45 | 34 | 32 | 35 | 0 | 0
2022-12-21 04:00 | 12 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 35 | 30 | 14 | 37 | 45 | 34 | 33 | 35 | 0 | 0
2022-12-21 05:00 | 12 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 36 | 29 | 14 | 38 | 46 | 34 | 33 | 35 | 0 | 0
2022-12-21 06:00 | 12 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 36 | 28 | 14 | 39 | 47 | 33 | 33 | 35 | 0 | 0
2022-12-21 07:00 | 12 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 36 | 27 | 16 | 40 | 48 | 33 | 34 | 39 | 0 | 0
2022-12-21 08:00 | 12 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 35 | 27 | 19 | 39 | 48 | 33 | 35 | 38 | 0 | 0
2022-12-21 09:00 | 12 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 35 | 26 | 20 | 39 | 46 | 32 | 34 | 38 | 0 | 0
2022-12-21 10:00 | 12 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 33 | 26 | 24 | 39 | 48 | 32 | 33 | 37 | 0 | 0
2022-12-21 11:00 | 12 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 32 | 27 | 26 | 39 | 45 | 32 | 32 | 37 | 0 | 0
2022-12-21 12:00 | 12 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 32 | 27 | 29 | 40 | 45 | 33 | 33 | 37 | 0 | 0
2022-12-21 13:00 | 12 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 30 | 26 | 29 | 40 | 44 | 32 | 32 | 37 | 0 | 0
2022-12-21 14:00 | 12 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 39 | 29 | 24 | 30 | 39 | 42 | 32 | 31 | 37 | 0 | 0
2022-12-21 15:00 | 12 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 29 | 23 | 32 | 39 | 41 | 32 | 31 | 37 | 0 | 0
2022-12-21 16:00 | 12 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 29 | 23 | 31 | 38 | 40 | 32 | 31 | 36 | 0 | 0
2022-12-21 17:00 | 12 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 29 | 22 | 31 | 38 | 39 | 31 | 31 | 36 | 0 | 0
2022-12-21 18:00 | 12 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 28 | 22 | 31 | 37 | 38 | 31 | 31 | 35 | 0 | 0
2022-12-21 19:00 | 12 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 27 | 21 | 32 | 35 | 37 | 31 | 31 | 36 | 0 | 0
2022-12-21 20:00 | 12 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 26 | 21 | 33 | 34 | 35 | 31 | 31 | 36 | 0 | 0
2022-12-21 21:00 | 12 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 27 | 20 | 31 | 33 | 37 | 31 | 31 | 36 | 0 | 0
2022-12-21 22:00 | 12 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 26 | 20 | 31 | 30 | 38 | 27 | 31 | 35 | 0 | 0
2022-12-21 23:00 | 12 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 26 | 19 | 32 | 29 | 38 | 27 | 30 | 35 | 0 | 0
2022-12-22 | 12 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 25 | 19 | 32 | 28 | 37 | 27 | 30 | 35 | 0 | 0
2022-12-22 01:00 | 12 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 25 | 18 | 34 | 26 | 35 | 26 | 29 | 35 | 0 | 0
2022-12-22 02:00 | 12 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 25 | 18 | 33 | 27 | 36 | 26 | 29 | 34 | 0 | 0
2022-12-22 03:00 | 12 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 25 | 17 | 34 | 29 | 35 | 26 | 29 | 33 | 0 | 0
2022-12-22 04:00 | 12 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 26 | 17 | 34 | 30 | 32 | 26 | 29 | 33 | 0 | 0
2022-12-22 05:00 | 12 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 26 | 17 | 34 | 30 | 30 | 26 | 28 | 33 | 0 | 0
2022-12-22 06:00 | 12 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 26 | 17 | 34 | 30 | 29 | 25 | 28 | 32 | 0 | 0
2022-12-22 07:00 | 12 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 26 | 18 | 36 | 31 | 31 | 25 | 26 | 31 | 0 | 0
2022-12-22 08:00 | 12 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 27 | 18 | 36 | 31 | 35 | 25 | 26 | 32 | 0 | 0
2022-12-22 09:00 | 12 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 27 | 19 | 37 | 32 | 38 | 26 | 28 | 34 | 0 | 0
2022-12-22 10:00 | 12 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 28 | 20 | 37 | 33 | 40 | 27 | 29 | 34 | 0 | 0
2022-12-22 11:00 | 12 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 28 | 20 | 37 | 34 | 41 | 27 | 30 | 36 | 0 | 0
2022-12-22 12:00 | 12 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 29 | 21 | 38 | 34 | 41 | 28 | 30 | 37 | 0 | 0
2022-12-22 13:00 | 12 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 29 | 21 | 38 | 35 | 42 | 29 | 31 | 38 | 0 | 0
2022-12-22 14:00 | 12 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 38 | 29 | 21 | 38 | 36 | 42 | 29 | 32 | 39 | 0 | 0
2022-12-22 15:00 | 12 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 30 | 21 | 38 | 36 | 40 | 28 | 33 | 38 | 0 | 0
2022-12-22 16:00 | 12 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 29 | 21 | 37 | 35 | 38 | 28 | 30 | 35 | 0 | 0
2022-12-22 17:00 | 12 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 29 | 21 | 37 | 33 | 36 | 28 | 30 | 35 | 0 | 0
2022-12-22 18:00 | 12 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 29 | 21 | 37 | 31 | 36 | 29 | 30 | 35 | 0 | 0
2022-12-22 19:00 | 12 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 29 | 21 | 36 | 30 | 35 | 29 | 31 | 33 | 0 | 0
2022-12-22 20:00 | 12 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 30 | 21 | 38 | 29 | 32 | 29 | 31 | 30 | 0 | 0
2022-12-22 21:00 | 12 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 30 | 21 | 38 | 29 | 32 | 29 | 28 | 29 | 0 | 0
2022-12-22 22:00 | 12 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 29 | 21 | 38 | 28 | 32 | 29 | 28 | 27 | 0 | 0
2022-12-22 23:00 | 12 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 30 | 20 | 40 | 28 | 33 | 28 | 27 | 27 | 0 | 0
2022-12-23 | 12 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 30 | 20 | 38 | 29 | 31 | 28 | 26 | 25 | 0 | 0
2022-12-23 01:00 | 12 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 30 | 20 | 38 | 29 | 31 | 28 | 27 | 24 | 0 | 0
2022-12-23 02:00 | 12 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 31 | 20 | 38 | 28 | 30 | 29 | 23 | 22 | 0 | 0
2022-12-23 03:00 | 12 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 31 | 20 | 42 | 24 | 29 | 30 | 22 | 22 | 0 | 0
2022-12-23 04:00 | 12 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 32 | 21 | 50 | 24 | 28 | 31 | 21 | 22 | 0 | 0
2022-12-23 05:00 | 12 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 30 | 21 | 44 | 25 | 27 | 32 | 21 | 20 | 0 | 0
2022-12-23 06:00 | 12 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 29 | 22 | 36 | 24 | 28 | 33 | 19 | 20 | 0 | 0
2022-12-23 07:00 | 12 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 28 | 23 | 36 | 27 | 28 | 34 | 23 | 20 | 0 | 0
2022-12-23 08:00 | 12 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 29 | 25 | 36 | 29 | 33 | 36 | 25 | 23 | 0 | 0
2022-12-23 09:00 | 12 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 30 | 26 | 36 | 30 | 38 | 39 | 29 | 25 | 0 | 0
2022-12-23 10:00 | 12 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 32 | 28 | 36 | 32 | 41 | 41 | 32 | 28 | 0 | 0
2022-12-23 11:00 | 12 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 41 | 32 | 31 | 37 | 34 | 46 | 44 | 34 | 31 | 0 | 0
2022-12-23 12:00 | 12 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 33 | 33 | 36 | 36 | 47 | 45 | 34 | 34 | 0 | 0
2022-12-23 13:00 | 12 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 42 | 33 | 33 | 36 | 38 | 47 | 47 | 35 | 38 | 0 | 0
2022-12-23 14:00 | 12 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 33 | 34 | 36 | 39 | 45 | 46 | 34 | 40 | 0 | 0
2022-12-23 15:00 | 12 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 40 | 33 | 34 | 36 | 40 | 44 | 44 | 33 | 37 | 0 | 0
2022-12-23 16:00 | 12 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 31 | 33 | 36 | 39 | 40 | 44 | 31 | 32 | 0 | 0
2022-12-23 17:00 | 12 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 29 | 31 | 35 | 36 | 37 | 41 | 28 | 30 | 0 | 0
2022-12-23 18:00 | 12 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 29 | 30 | 35 | 35 | 38 | 40 | 28 | 28 | 0 | 0
2022-12-23 19:00 | 12 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 29 | 29 | 35 | 33 | 36 | 39 | 26 | 27 | 0 | 0
2022-12-23 20:00 | 12 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 29 | 29 | 35 | 34 | 36 | 38 | 24 | 25 | 0 | 0
2022-12-23 21:00 | 12 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 28 | 28 | 35 | 33 | 33 | 38 | 25 | 25 | 0 | 0
2022-12-23 22:00 | 12 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 29 | 27 | 35 | 31 | 34 | 37 | 24 | 24 | 0 | 0
2022-12-23 23:00 | 12 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 25 | 26 | 34 | 30 | 33 | 37 | 23 | 23 | 0 | 0
2022-12-24 | 12 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 24 | 25 | 33 | 29 | 32 | 37 | 22 | 23 | 0 | 0
2022-12-24 01:00 | 12 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 23 | 26 | 32 | 28 | 31 | 36 | 22 | 24 | 0 | 0
2022-12-24 02:00 | 12 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 22 | 27 | 30 | 27 | 31 | 36 | 21 | 23 | 0 | 0
2022-12-24 03:00 | 12 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 20 | 28 | 30 | 26 | 28 | 34 | 21 | 23 | 0 | 0
2022-12-24 04:00 | 12 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 20 | 27 | 27 | 26 | 26 | 35 | 19 | 21 | 0 | 0
2022-12-24 05:00 | 12 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 20 | 26 | 27 | 26 | 27 | 34 | 20 | 21 | 0 | 0
2022-12-24 06:00 | 12 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 19 | 25 | 26 | 25 | 26 | 35 | 19 | 21 | 0 | 0
2022-12-24 07:00 | 12 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 19 | 26 | 26 | 24 | 28 | 34 | 22 | 20 | 0 | 0
2022-12-24 08:00 | 12 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 23 | 28 | 29 | 27 | 32 | 38 | 27 | 22 | 0 | 0
2022-12-24 09:00 | 12 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 26 | 29 | 31 | 31 | 34 | 42 | 29 | 26 | 0 | 0
2022-12-24 10:00 | 12 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 29 | 31 | 33 | 35 | 37 | 45 | 31 | 28 | 0 | 0
2022-12-24 11:00 | 12 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 30 | 34 | 36 | 37 | 39 | 47 | 32 | 32 | 0 | 0
2022-12-24 12:00 | 12 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 31 | 36 | 37 | 41 | 40 | 49 | 33 | 35 | 0 | 0
2022-12-24 13:00 | 12 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 31 | 37 | 37 | 44 | 41 | 51 | 33 | 38 | 0 | 0
2022-12-24 14:00 | 12 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 31 | 38 | 37 | 45 | 40 | 51 | 33 | 38 | 0 | 0
2022-12-24 15:00 | 12 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 31 | 39 | 35 | 45 | 40 | 51 | 33 | 38 | 0 | 0
2022-12-24 16:00 | 12 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 31 | 38 | 34 | 40 | 41 | 51 | 32 | 34 | 0 | 0
2022-12-24 17:00 | 12 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 31 | 38 | 33 | 45 | 41 | 51 | 31 | 34 | 0 | 0
2022-12-24 18:00 | 12 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 30 | 37 | 32 | 44 | 42 | 52 | 30 | 34 | 0 | 0
2022-12-24 19:00 | 12 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 31 | 37 | 32 | 46 | 43 | 51 | 31 | 35 | 0 | 0
2022-12-24 20:00 | 12 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 31 | 36 | 32 | 46 | 44 | 50 | 31 | 36 | 0 | 0
2022-12-24 21:00 | 12 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 31 | 36 | 31 | 45 | 45 | 51 | 31 | 37 | 0 | 0
2022-12-24 22:00 | 12 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 32 | 37 | 31 | 45 | 45 | 51 | 30 | 36 | 0 | 0
2022-12-24 23:00 | 12 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 31 | 37 | 30 | 45 | 45 | 51 | 31 | 35 | 0 | 0
2022-12-25 | 12 | 7 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 30 | 38 | 29 | 45 | 45 | 51 | 31 | 34 | 0 | 0
2022-12-25 01:00 | 12 | 7 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 28 | 39 | 27 | 46 | 45 | 50 | 31 | 34 | 0 | 0
2022-12-25 02:00 | 12 | 7 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 28 | 39 | 26 | 49 | 43 | 45 | 30 | 34 | 0 | 0
2022-12-25 03:00 | 12 | 7 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 28 | 40 | 25 | 51 | 40 | 42 | 29 | 34 | 0 | 0
2022-12-25 04:00 | 12 | 7 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 27 | 35 | 24 | 51 | 38 | 37 | 29 | 35 | 0 | 0
2022-12-25 05:00 | 12 | 7 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 27 | 31 | 22 | 51 | 39 | 35 | 29 | 35 | 0 | 0
2022-12-25 06:00 | 12 | 7 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 27 | 26 | 23 | 51 | 40 | 34 | 29 | 35 | 0 | 0
2022-12-25 07:00 | 12 | 7 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 27 | 25 | 23 | 50 | 40 | 33 | 29 | 36 | 0 | 0
2022-12-25 08:00 | 12 | 7 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 28 | 25 | 27 | 48 | 42 | 33 | 30 | 36 | 0 | 0
2022-12-25 09:00 | 12 | 7 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 29 | 24 | 30 | 41 | 43 | 33 | 31 | 36 | 0 | 0
2022-12-25 10:00 | 12 | 7 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 29 | 23 | 34 | 46 | 44 | 29 | 32 | 38 | 0 | 0
2022-12-25 11:00 | 12 | 7 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 30 | 22 | 35 | 44 | 45 | 29 | 33 | 38 | 0 | 0
2022-12-25 12:00 | 12 | 7 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 41 | 30 | 21 | 37 | 44 | 44 | 29 | 33 | 37 | 0 | 0
2022-12-25 13:00 | 12 | 7 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 30 | 20 | 38 | 43 | 42 | 25 | 32 | 36 | 0 | 0
2022-12-25 14:00 | 12 | 7 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 31 | 19 | 38 | 40 | 42 | 23 | 32 | 37 | 0 | 0
2022-12-25 15:00 | 12 | 7 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 38 | 30 | 18 | 38 | 38 | 40 | 21 | 32 | 36 | 0 | 0
2022-12-25 16:00 | 12 | 7 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 30 | 15 | 33 | 36 | 38 | 21 | 32 | 33 | 0 | 0
2022-12-25 17:00 | 12 | 7 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 28 | 13 | 29 | 35 | 36 | 21 | 31 | 33 | 0 | 0
2022-12-25 18:00 | 12 | 7 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 28 | 10 | 28 | 33 | 35 | 19 | 30 | 32 | 0 | 0
2022-12-25 19:00 | 12 | 7 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 25 | 9 | 29 | 33 | 34 | 16 | 28 | 31 | 0 | 0
2022-12-25 20:00 | 12 | 7 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 25 | 9 | 29 | 31 | 33 | 15 | 26 | 30 | 0 | 0
2022-12-25 21:00 | 12 | 7 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 25 | 8 | 30 | 27 | 32 | 15 | 25 | 30 | 0 | 0
2022-12-25 22:00 | 12 | 7 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 30 | 25 | 6 | 30 | 25 | 32 | 14 | 25 | 29 | 0 | 0
2022-12-25 23:00 | 12 | 7 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 25 | 4 | 29 | 24 | 29 | 13 | 24 | 29 | 0 | 0
2022-12-26 | 12 | 1 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 25 | 2 | 30 | 21 | 31 | 13 | 23 | 28 | 0 | 0
2022-12-26 01:00 | 12 | 1 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 25 | 1 | 30 | 20 | 30 | 12 | 23 | 28 | 0 | 0
2022-12-26 02:00 | 12 | 1 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 25 | 1 | 30 | 18 | 30 | 11 | 22 | 27 | 0 | 0
2022-12-26 03:00 | 12 | 1 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 25 | 0 | 30 | 19 | 28 | 10 | 22 | 26 | 0 | 0
2022-12-26 04:00 | 12 | 1 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 25 | 0 | 29 | 18 | 30 | 9 | 21 | 25 | 0 | 0
2022-12-26 05:00 | 12 | 1 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 25 | 0 | 30 | 17 | 28 | 9 | 20 | 23 | 0 | 0
2022-12-26 06:00 | 12 | 1 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 25 | 0 | 28 | 17 | 27 | 8 | 20 | 20 | 0 | 0
2022-12-26 07:00 | 12 | 1 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 25 | 1 | 30 | 16 | 28 | 6 | 19 | 19 | 0 | 0
2022-12-26 08:00 | 12 | 1 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 24 | 1 | 30 | 16 | 32 | 7 | 21 | 18 | 0 | 0
2022-12-26 09:00 | 12 | 1 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 23 | 2 | 31 | 17 | 35 | 7 | 22 | 21 | 0 | 0
2022-12-26 10:00 | 12 | 1 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 23 | 3 | 33 | 18 | 35 | 10 | 23 | 23 | 0 | 0
2022-12-26 11:00 | 12 | 1 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 23 | 5 | 35 | 20 | 36 | 12 | 24 | 25 | 0 | 0
2022-12-26 12:00 | 12 | 1 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 35 | 24 | 6 | 36 | 21 | 39 | 12 | 25 | 25 | 0 | 0
2022-12-26 13:00 | 12 | 1 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 36 | 24 | 6 | 38 | 21 | 41 | 11 | 26 | 28 | 0 | 0
2022-12-26 14:00 | 12 | 1 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 37 | 24 | 5 | 36 | 20 | 41 | 12 | 26 | 29 | 0 | 0
2022-12-26 15:00 | 12 | 1 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 34 | 24 | 5 | 36 | 19 | 40 | 12 | 26 | 29 | 0 | 0
2022-12-26 16:00 | 12 | 1 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 23 | 4 | 34 | 18 | 38 | 12 | 26 | 30 | 0 | 0
2022-12-26 17:00 | 12 | 1 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 23 | 3 | 32 | 18 | 38 | 11 | 26 | 30 | 0 | 0
2022-12-26 18:00 | 12 | 1 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 23 | 2 | 30 | 17 | 38 | 11 | 25 | 29 | 0 | 0
2022-12-26 19:00 | 12 | 1 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 23 | 2 | 31 | 17 | 37 | 12 | 25 | 29 | 0 | 0
2022-12-26 20:00 | 12 | 1 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 23 | 2 | 33 | 16 | 38 | 12 | 25 | 29 | 0 | 0
2022-12-26 21:00 | 12 | 1 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 23 | 2 | 33 | 15 | 38 | 13 | 25 | 27 | 0 | 0
2022-12-26 22:00 | 12 | 1 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 23 | 2 | 32 | 14 | 38 | 14 | 25 | 27 | 0 | 0
2022-12-26 23:00 | 12 | 1 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 23 | 2 | 32 | 14 | 38 | 14 | 25 | 29 | 0 | 0
2022-12-27 | 12 | 2 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 23 | 2 | 32 | 14 | 36 | 14 | 25 | 29 | 0 | 0
2022-12-27 01:00 | 12 | 2 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 31 | 22 | 2 | 32 | 13 | 36 | 15 | 25 | 28 | 0 | 0
2022-12-27 02:00 | 12 | 2 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 29 | 21 | 3 | 32 | 14 | 33 | 15 | 24 | 27 | 0 | 0
2022-12-27 03:00 | 12 | 2 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 28 | 21 | 3 | 33 | 14 | 31 | 16 | 24 | 26 | 0 | 0
2022-12-27 04:00 | 12 | 2 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 21 | 4 | 33 | 16 | 30 | 16 | 23 | 25 | 0 | 0
2022-12-27 05:00 | 12 | 2 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 22 | 4 | 34 | 16 | 30 | 16 | 21 | 26 | 0 | 0
2022-12-27 06:00 | 12 | 2 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 26 | 22 | 5 | 34 | 15 | 29 | 16 | 21 | 26 | 0 | 0
2022-12-27 07:00 | 12 | 2 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 22 | 6 | 34 | 15 | 29 | 16 | 21 | 25 | 0 | 0
2022-12-27 08:00 | 12 | 2 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 22 | 8 | 33 | 14 | 30 | 17 | 21 | 25 | 0 | 0
2022-12-27 09:00 | 12 | 2 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 23 | 9 | 32 | 17 | 32 | 21 | 23 | 24 | 0 | 0
2022-12-27 10:00 | 12 | 2 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 24 | 10 | 34 | 19 | 32 | 18 | 24 | 25 | 0 | 0
2022-12-27 11:00 | 12 | 2 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 24 | 12 | 35 | 23 | 34 | 20 | 25 | 26 | 0 | 0
2022-12-27 12:00 | 12 | 2 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 25 | 13 | 36 | 27 | 33 | 20 | 25 | 27 | 0 | 0
2022-12-27 13:00 | 12 | 2 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 24 | 12 | 36 | 26 | 34 | 19 | 25 | 28 | 0 | 0
2022-12-27 14:00 | 12 | 2 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 23 | 12 | 37 | 26 | 33 | 19 | 24 | 28 | 0 | 0
2022-12-27 15:00 | 12 | 2 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 23 | 11 | 37 | 27 | 32 | 17 | 24 | 28 | 0 | 0
2022-12-27 16:00 | 12 | 2 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 22 | 8 | 37 | 26 | 30 | 16 | 23 | 28 | 0 | 0
2022-12-27 17:00 | 12 | 2 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 20 | 6 | 36 | 23 | 28 | 14 | 22 | 26 | 0 | 0
2022-12-27 18:00 | 12 | 2 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 20 | 3 | 36 | 22 | 28 | 14 | 22 | 25 | 0 | 0
2022-12-27 19:00 | 12 | 2 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 19 | 3 | 35 | 19 | 27 | 13 | 20 | 25 | 0 | 0
2022-12-27 20:00 | 12 | 2 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 18 | 2 | 35 | 18 | 26 | 11 | 20 | 26 | 0 | 0
2022-12-27 21:00 | 12 | 2 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 18 | 2 | 34 | 18 | 26 | 10 | 19 | 24 | 0 | 0
2022-12-27 22:00 | 12 | 2 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 18 | 2 | 32 | 19 | 26 | 8 | 18 | 24 | 0 | 0
2022-12-27 23:00 | 12 | 2 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 18 | 1 | 31 | 20 | 26 | 8 | 17 | 23 | 0 | 0
2022-12-28 | 12 | 3 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 23 | 17 | 1 | 31 | 20 | 25 | 8 | 16 | 23 | 0 | 0
2022-12-28 01:00 | 12 | 3 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 17 | 1 | 31 | 19 | 25 | 7 | 15 | 23 | 0 | 0
2022-12-28 02:00 | 12 | 3 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 17 | 0 | 31 | 18 | 24 | 8 | 16 | 22 | 0 | 0
2022-12-28 03:00 | 12 | 3 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 21 | 18 | 0 | 31 | 16 | 25 | 7 | 17 | 21 | 0 | 0
2022-12-28 04:00 | 12 | 3 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 18 | 1 | 30 | 16 | 24 | 6 | 17 | 20 | 0 | 0
2022-12-28 05:00 | 12 | 3 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 18 | 1 | 30 | 15 | 24 | 6 | 17 | 21 | 0 | 0
2022-12-28 06:00 | 12 | 3 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 17 | 2 | 29 | 14 | 24 | 4 | 17 | 20 | 0 | 0
2022-12-28 07:00 | 12 | 3 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 17 | 2 | 27 | 14 | 24 | 6 | 18 | 19 | 0 | 0
2022-12-28 08:00 | 12 | 3 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 17 | 3 | 27 | 15 | 27 | 8 | 18 | 21 | 0 | 0
2022-12-28 09:00 | 12 | 3 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 17 | 3 | 29 | 17 | 29 | 11 | 20 | 22 | 0 | 0
2022-12-28 10:00 | 12 | 3 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 18 | 4 | 33 | 19 | 31 | 14 | 20 | 26 | 0 | 0
2022-12-28 11:00 | 12 | 3 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 18 | 6 | 35 | 20 | 32 | 15 | 22 | 28 | 0 | 0
2022-12-28 12:00 | 12 | 3 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 20 | 7 | 35 | 22 | 33 | 16 | 21 | 28 | 0 | 0
2022-12-28 13:00 | 12 | 3 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 19 | 8 | 37 | 22 | 33 | 18 | 21 | 28 | 0 | 0
2022-12-28 14:00 | 12 | 3 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 19 | 8 | 34 | 22 | 33 | 20 | 21 | 28 | 0 | 0
2022-12-28 15:00 | 12 | 3 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 28 | 18 | 9 | 34 | 23 | 32 | 20 | 20 | 28 | 0 | 0
2022-12-28 16:00 | 12 | 3 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 25 | 16 | 8 | 32 | 21 | 30 | 20 | 19 | 26 | 0 | 0
2022-12-28 17:00 | 12 | 3 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 22 | 16 | 8 | 33 | 21 | 29 | 17 | 17 | 23 | 0 | 0
2022-12-28 18:00 | 12 | 3 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 15 | 7 | 33 | 20 | 28 | 18 | 16 | 23 | 0 | 0
2022-12-28 19:00 | 12 | 3 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 14 | 7 | 33 | 19 | 26 | 19 | 15 | 21 | 0 | 0
2022-12-28 20:00 | 12 | 3 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 15 | 6 | 33 | 18 | 26 | 19 | 15 | 18 | 0 | 0
2022-12-28 21:00 | 12 | 3 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 15 | 6 | 33 | 17 | 25 | 19 | 15 | 18 | 0 | 0
2022-12-28 22:00 | 12 | 3 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 15 | 6 | 32 | 18 | 24 | 19 | 15 | 18 | 0 | 0
2022-12-28 23:00 | 12 | 3 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 15 | 7 | 31 | 17 | 23 | 20 | 15 | 17 | 0 | 0
2022-12-29 | 12 | 4 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 12 | 7 | 32 | 17 | 21 | 19 | 15 | 15 | 0 | 0
2022-12-29 01:00 | 12 | 4 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 16 | 10 | 8 | 31 | 17 | 21 | 20 | 14 | 14 | 0 | 0
2022-12-29 02:00 | 12 | 4 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 10 | 8 | 32 | 16 | 21 | 21 | 13 | 13 | 0 | 0
2022-12-29 03:00 | 12 | 4 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 11 | 9 | 32 | 17 | 20 | 21 | 12 | 12 | 0 | 0
2022-12-29 04:00 | 12 | 4 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 13 | 10 | 10 | 31 | 15 | 20 | 22 | 9 | 12 | 0 | 0
2022-12-29 05:00 | 12 | 4 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 15 | 7 | 11 | 31 | 14 | 18 | 23 | 7 | 11 | 0 | 0
2022-12-29 06:00 | 12 | 4 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 14 | 7 | 12 | 31 | 16 | 18 | 23 | 8 | 11 | 0 | 0
2022-12-29 07:00 | 12 | 4 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 14 | 7 | 13 | 30 | 13 | 19 | 23 | 8 | 11 | 0 | 0
2022-12-29 08:00 | 12 | 4 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 9 | 13 | 30 | 18 | 23 | 23 | 10 | 11 | 0 | 0
2022-12-29 09:00 | 12 | 4 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 24 | 10 | 14 | 31 | 20 | 25 | 25 | 13 | 12 | 0 | 0
2022-12-29 10:00 | 12 | 4 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 11 | 16 | 31 | 27 | 28 | 26 | 15 | 16 | 0 | 0
2022-12-29 11:00 | 12 | 4 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 29 | 13 | 17 | 31 | 31 | 30 | 29 | 18 | 19 | 0 | 0
2022-12-29 12:00 | 12 | 4 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 15 | 19 | 30 | 32 | 33 | 30 | 20 | 23 | 0 | 0
2022-12-29 13:00 | 12 | 4 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 17 | 19 | 30 | 33 | 34 | 30 | 21 | 25 | 0 | 0
2022-12-29 14:00 | 12 | 4 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 20 | 20 | 29 | 34 | 34 | 31 | 22 | 26 | 0 | 0
2022-12-29 15:00 | 12 | 4 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 19 | 20 | 29 | 34 | 34 | 31 | 21 | 28 | 0 | 0
2022-12-29 16:00 | 12 | 4 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 19 | 20 | 29 | 33 | 32 | 31 | 19 | 28 | 0 | 0
2022-12-29 17:00 | 12 | 4 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 27 | 18 | 19 | 29 | 33 | 31 | 30 | 18 | 25 | 0 | 0
2022-12-29 18:00 | 12 | 4 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 27 | 17 | 19 | 29 | 33 | 31 | 30 | 17 | 23 | 0 | 0
2022-12-29 19:00 | 12 | 4 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 25 | 17 | 19 | 29 | 33 | 30 | 30 | 16 | 22 | 0 | 0
2022-12-29 20:00 | 12 | 4 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 24 | 16 | 19 | 29 | 31 | 25 | 28 | 14 | 20 | 0 | 0
2022-12-29 21:00 | 12 | 4 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 22 | 17 | 19 | 29 | 31 | 25 | 27 | 14 | 20 | 0 | 0
2022-12-29 22:00 | 12 | 4 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 18 | 19 | 29 | 28 | 26 | 27 | 14 | 17 | 0 | 0
2022-12-29 23:00 | 12 | 4 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 18 | 19 | 28 | 28 | 26 | 26 | 14 | 19 | 0 | 0
2022-12-30 | 12 | 5 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 20 | 17 | 19 | 28 | 24 | 24 | 29 | 14 | 18 | 0 | 0
2022-12-30 01:00 | 12 | 5 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 19 | 17 | 20 | 27 | 22 | 25 | 31 | 13 | 18 | 0 | 0
2022-12-30 02:00 | 12 | 5 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 18 | 15 | 21 | 24 | 21 | 24 | 32 | 13 | 16 | 0 | 0
2022-12-30 03:00 | 12 | 5 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 15 | 22 | 21 | 22 | 24 | 34 | 12 | 17 | 0 | 0
2022-12-30 04:00 | 12 | 5 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 17 | 22 | 17 | 22 | 22 | 34 | 12 | 17 | 0 | 0
2022-12-30 05:00 | 12 | 5 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 17 | 23 | 19 | 23 | 25 | 33 | 13 | 17 | 0 | 0
2022-12-30 06:00 | 12 | 5 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 17 | 17 | 23 | 19 | 23 | 25 | 30 | 13 | 17 | 0 | 0
2022-12-30 07:00 | 12 | 5 | 8 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 19 | 19 | 24 | 19 | 23 | 25 | 31 | 14 | 17 | 0 | 0
2022-12-30 08:00 | 12 | 5 | 9 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 20 | 20 | 25 | 19 | 25 | 27 | 33 | 17 | 17 | 0 | 0
2022-12-30 09:00 | 12 | 5 | 10 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 23 | 23 | 26 | 23 | 28 | 30 | 37 | 19 | 19 | 0 | 0
2022-12-30 10:00 | 12 | 5 | 11 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 26 | 25 | 27 | 23 | 31 | 34 | 39 | 23 | 23 | 0 | 0
2022-12-30 11:00 | 12 | 5 | 12 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 30 | 27 | 29 | 24 | 36 | 35 | 41 | 25 | 28 | 0 | 0
2022-12-30 12:00 | 12 | 5 | 13 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 31 | 29 | 30 | 26 | 38 | 37 | 41 | 27 | 29 | 0 | 0
2022-12-30 13:00 | 12 | 5 | 14 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 31 | 31 | 28 | 40 | 38 | 42 | 29 | 30 | 0 | 0
2022-12-30 14:00 | 12 | 5 | 15 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 31 | 31 | 28 | 42 | 40 | 42 | 30 | 31 | 0 | 0
2022-12-30 15:00 | 12 | 5 | 16 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 31 | 32 | 28 | 42 | 37 | 41 | 30 | 32 | 0 | 0
2022-12-30 16:00 | 12 | 5 | 17 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 32 | 30 | 31 | 26 | 40 | 35 | 40 | 30 | 32 | 0 | 0
2022-12-30 17:00 | 12 | 5 | 18 | 0 | #N/A | Heating | 70 | 70 | 0 | 0 | #N/A | #N/A | 33 | 30 | 31 | 24 | 37 | 35 | 39 | 31 | 32 | 0 | 0
2022-12-30 18:00 | 12 | 5 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 30 | 30 | 22 | 35 | 35 | 39 | 30 | 33 | 0 | 0
2022-12-30 19:00 | 12 | 5 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 30 | 29 | 25 | 34 | 36 | 39 | 30 | 33 | 0 | 0
2022-12-30 20:00 | 12 | 5 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 30 | 28 | 27 | 35 | 36 | 39 | 30 | 34 | 0 | 0
2022-12-30 21:00 | 12 | 5 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 30 | 27 | 28 | 35 | 36 | 38 | 30 | 34 | 0 | 0
2022-12-30 22:00 | 12 | 5 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 30 | 27 | 30 | 35 | 36 | 38 | 30 | 34 | 0 | 0
2022-12-30 23:00 | 12 | 5 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 30 | 28 | 31 | 35 | 36 | 38 | 30 | 35 | 0 | 0
2022-12-31 | 12 | 6 | 1 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 32 | 29 | 28 | 31 | 35 | 36 | 37 | 30 | 34 | 0 | 0
2022-12-31 01:00 | 12 | 6 | 2 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 29 | 28 | 31 | 34 | 37 | 36 | 31 | 34 | 0 | 0
2022-12-31 02:00 | 12 | 6 | 3 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 29 | 28 | 32 | 34 | 37 | 34 | 31 | 34 | 0 | 0
2022-12-31 03:00 | 12 | 6 | 4 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 30 | 28 | 33 | 35 | 37 | 33 | 31 | 34 | 0 | 0
2022-12-31 04:00 | 12 | 6 | 5 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 30 | 28 | 33 | 34 | 36 | 31 | 31 | 35 | 0 | 0
2022-12-31 05:00 | 12 | 6 | 6 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 31 | 27 | 32 | 33 | 37 | 31 | 30 | 35 | 0 | 0
2022-12-31 06:00 | 12 | 6 | 7 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 30 | 27 | 32 | 32 | 36 | 30 | 31 | 35 | 0 | 0
2022-12-31 07:00 | 12 | 6 | 8 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 30 | 27 | 31 | 29 | 36 | 29 | 31 | 35 | 0 | 0
2022-12-31 08:00 | 12 | 6 | 9 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 31 | 26 | 32 | 32 | 36 | 31 | 31 | 35 | 0 | 0
2022-12-31 09:00 | 12 | 6 | 10 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 33 | 32 | 26 | 33 | 37 | 37 | 35 | 31 | 34 | 0 | 0
2022-12-31 10:00 | 12 | 6 | 11 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 32 | 26 | 34 | 40 | 38 | 37 | 31 | 35 | 0 | 0
2022-12-31 11:00 | 12 | 6 | 12 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 34 | 32 | 27 | 35 | 42 | 41 | 40 | 31 | 35 | 0 | 0
2022-12-31 12:00 | 12 | 6 | 13 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 35 | 33 | 27 | 37 | 46 | 43 | 41 | 32 | 35 | 0 | 0
2022-12-31 13:00 | 12 | 6 | 14 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 36 | 34 | 27 | 38 | 47 | 43 | 43 | 33 | 36 | 0 | 0
2022-12-31 14:00 | 12 | 6 | 15 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 34 | 27 | 39 | 46 | 43 | 43 | 33 | 36 | 0 | 0
2022-12-31 15:00 | 12 | 6 | 16 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 35 | 27 | 39 | 44 | 44 | 42 | 33 | 37 | 0 | 0
2022-12-31 16:00 | 12 | 6 | 17 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 36 | 27 | 39 | 41 | 44 | 40 | 36 | 37 | 0 | 0
2022-12-31 17:00 | 12 | 6 | 18 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 37 | 36 | 26 | 38 | 38 | 44 | 38 | 37 | 38 | 0 | 0
2022-12-31 18:00 | 12 | 6 | 19 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 39 | 37 | 26 | 36 | 36 | 44 | 36 | 37 | 38 | 0 | 0
2022-12-31 19:00 | 12 | 6 | 20 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 37 | 25 | 37 | 34 | 44 | 34 | 37 | 39 | 0 | 0
2022-12-31 20:00 | 12 | 6 | 21 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 38 | 24 | 37 | 32 | 46 | 33 | 38 | 38 | 0 | 0
2022-12-31 21:00 | 12 | 6 | 22 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 40 | 39 | 23 | 37 | 31 | 47 | 33 | 42 | 39 | 0 | 0
2022-12-31 22:00 | 12 | 6 | 23 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 43 | 40 | 21 | 37 | 27 | 48 | 32 | 42 | 41 | 0 | 0
2022-12-31 23:00 | 12 | 6 | 24 | 0 | #N/A | Heating | 66 | 64 | 0 | 0 | #N/A | #N/A | 45 | 41 | 20 | 38 | 28 | 48 | 32 | 42 | 42 | 0 | 0
Formulas:
Date = [Date, row above]+1/24
Note on W11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Wilkes-Barre_Scranton