## Zip Code Lookup Table (hidden)
ZCTA/ZIP | Climat Region (CR) | Reference City
15001 | H | Pittsburgh
15003 | H | Pittsburgh
15004 | H | Pittsburgh
15005 | H | Pittsburgh
15006 | H | Pittsburgh
15007 | H | Pittsburgh
15009 | H | Pittsburgh
15010 | H | Pittsburgh
15012 | H | Pittsburgh
15014 | H | Pittsburgh
15015 | H | Pittsburgh
15017 | H | Pittsburgh
15018 | H | Pittsburgh
15019 | H | Pittsburgh
15020 | H | Pittsburgh
15021 | H | Pittsburgh
15022 | H | Pittsburgh
15024 | H | Pittsburgh
15025 | H | Pittsburgh
15026 | H | Pittsburgh
15027 | H | Pittsburgh
15028 | H | Pittsburgh
15030 | H | Pittsburgh
15031 | H | Pittsburgh
15032 | H | Pittsburgh
15033 | H | Pittsburgh
15034 | H | Pittsburgh
15035 | H | Pittsburgh
15036 | H | Pittsburgh
15037 | H | Pittsburgh
15038 | H | Pittsburgh
15042 | H | Pittsburgh
15043 | H | Pittsburgh
15044 | H | Pittsburgh
15045 | H | Pittsburgh
15046 | H | Pittsburgh
15047 | H | Pittsburgh
15049 | H | Pittsburgh
15050 | H | Pittsburgh
15051 | H | Pittsburgh
15052 | H | Pittsburgh
15053 | H | Pittsburgh
15054 | H | Pittsburgh
15055 | H | Pittsburgh
15056 | H | Pittsburgh
15057 | H | Pittsburgh
15059 | H | Pittsburgh
15060 | H | Pittsburgh
15061 | H | Pittsburgh
15062 | H | Pittsburgh
15063 | H | Pittsburgh
15064 | H | Pittsburgh
15065 | H | Pittsburgh
15066 | H | Pittsburgh
15067 | H | Pittsburgh
15068 | H | Pittsburgh
15069 | H | Pittsburgh
15071 | H | Pittsburgh
15072 | H | Pittsburgh
15074 | H | Pittsburgh
15075 | H | Pittsburgh
15076 | H | Pittsburgh
15077 | H | Pittsburgh
15078 | H | Pittsburgh
15081 | H | Pittsburgh
15082 | H | Pittsburgh
15083 | H | Pittsburgh
15084 | H | Pittsburgh
15085 | H | Pittsburgh
15086 | H | Pittsburgh
15087 | H | Pittsburgh
15088 | H | Pittsburgh
15089 | H | Pittsburgh
15090 | H | Pittsburgh
15091 | H | Pittsburgh
15095 | H | Pittsburgh
15096 | H | Pittsburgh
15101 | H | Pittsburgh
15102 | H | Pittsburgh
15104 | H | Pittsburgh
15106 | H | Pittsburgh
15108 | H | Pittsburgh
15110 | H | Pittsburgh
15112 | H | Pittsburgh
15116 | H | Pittsburgh
15120 | H | Pittsburgh
15122 | H | Pittsburgh
15123 | H | Pittsburgh
15126 | H | Pittsburgh
15127 | H | Pittsburgh
15129 | H | Pittsburgh
15130 | H | Pittsburgh
15131 | H | Pittsburgh
15132 | H | Pittsburgh
15133 | H | Pittsburgh
15134 | H | Pittsburgh
15135 | H | Pittsburgh
15136 | H | Pittsburgh
15137 | H | Pittsburgh
15139 | H | Pittsburgh
15140 | H | Pittsburgh
15142 | H | Pittsburgh
15143 | H | Pittsburgh
15144 | H | Pittsburgh
15145 | H | Pittsburgh
15146 | H | Pittsburgh
15147 | H | Pittsburgh
15148 | H | Pittsburgh
15189 | H | Pittsburgh
15201 | H | Pittsburgh
15202 | H | Pittsburgh
15203 | H | Pittsburgh
15204 | H | Pittsburgh
15205 | H | Pittsburgh
15206 | H | Pittsburgh
15207 | H | Pittsburgh
15208 | H | Pittsburgh
15209 | H | Pittsburgh
15210 | H | Pittsburgh
15211 | H | Pittsburgh
15212 | H | Pittsburgh
15213 | H | Pittsburgh
15214 | H | Pittsburgh
15215 | H | Pittsburgh
15216 | H | Pittsburgh
15217 | H | Pittsburgh
15218 | H | Pittsburgh
15219 | H | Pittsburgh
15220 | H | Pittsburgh
15221 | H | Pittsburgh
15222 | H | Pittsburgh
15223 | H | Pittsburgh
15224 | H | Pittsburgh
15225 | H | Pittsburgh
15226 | H | Pittsburgh
15227 | H | Pittsburgh
15228 | H | Pittsburgh
15229 | H | Pittsburgh
15230 | H | Pittsburgh
15231 | H | Pittsburgh
15232 | H | Pittsburgh
15233 | H | Pittsburgh
15234 | H | Pittsburgh
15235 | H | Pittsburgh
15236 | H | Pittsburgh
15237 | H | Pittsburgh
15238 | H | Pittsburgh
15239 | H | Pittsburgh
15240 | H | Pittsburgh
15241 | H | Pittsburgh
15242 | H | Pittsburgh
15243 | H | Pittsburgh
15244 | H | Pittsburgh
15250 | H | Pittsburgh
15251 | H | Pittsburgh
15252 | H | Pittsburgh
15253 | H | Pittsburgh
15254 | H | Pittsburgh
15255 | H | Pittsburgh
15257 | H | Pittsburgh
15258 | H | Pittsburgh
15259 | H | Pittsburgh
15260 | H | Pittsburgh
15261 | H | Pittsburgh
15262 | H | Pittsburgh
15263 | H | Pittsburgh
15264 | H | Pittsburgh
15265 | H | Pittsburgh
15266 | H | Pittsburgh
15267 | H | Pittsburgh
15268 | H | Pittsburgh
15270 | H | Pittsburgh
15272 | H | Pittsburgh
15274 | H | Pittsburgh
15275 | H | Pittsburgh
15276 | H | Pittsburgh
15277 | H | Pittsburgh
15278 | H | Pittsburgh
15279 | H | Pittsburgh
15281 | H | Pittsburgh
15282 | H | Pittsburgh
15283 | H | Pittsburgh
15285 | H | Pittsburgh
15286 | H | Pittsburgh
15290 | H | Pittsburgh
15295 | H | Pittsburgh
15301 | H | Pittsburgh
15310 | H | Pittsburgh
15311 | H | Pittsburgh
15312 | H | Pittsburgh
15313 | H | Pittsburgh
15314 | H | Pittsburgh
15315 | H | Pittsburgh
15316 | H | Pittsburgh
15317 | H | Pittsburgh
15320 | H | Pittsburgh
15321 | H | Pittsburgh
15322 | H | Pittsburgh
15323 | H | Pittsburgh
15324 | H | Pittsburgh
15325 | H | Pittsburgh
15327 | H | Pittsburgh
15329 | H | Pittsburgh
15330 | H | Pittsburgh
15331 | H | Pittsburgh
15332 | H | Pittsburgh
15333 | H | Pittsburgh
15334 | H | Pittsburgh
15336 | H | Pittsburgh
15337 | H | Pittsburgh
15338 | H | Pittsburgh
15339 | H | Pittsburgh
15340 | H | Pittsburgh
15341 | H | Pittsburgh
15342 | H | Pittsburgh
15344 | H | Pittsburgh
15345 | H | Pittsburgh
15346 | H | Pittsburgh
15347 | H | Pittsburgh
15348 | H | Pittsburgh
15349 | H | Pittsburgh
15350 | H | Pittsburgh
15351 | H | Pittsburgh
15352 | H | Pittsburgh
15353 | H | Pittsburgh
15354 | H | Pittsburgh
15357 | H | Pittsburgh
15358 | H | Pittsburgh
15359 | H | Pittsburgh
15360 | H | Pittsburgh
15361 | H | Pittsburgh
15362 | H | Pittsburgh
15363 | H | Pittsburgh
15364 | H | Pittsburgh
15365 | H | Pittsburgh
15366 | H | Pittsburgh
15367 | H | Pittsburgh
15368 | H | Pittsburgh
15370 | H | Pittsburgh
15376 | H | Pittsburgh
15377 | H | Pittsburgh
15378 | H | Pittsburgh
15379 | H | Pittsburgh
15380 | H | Pittsburgh
15401 | H | Pittsburgh
15410 | H | Pittsburgh
15411 | H | Pittsburgh
15412 | H | Pittsburgh
15413 | H | Pittsburgh
15415 | H | Pittsburgh
15416 | H | Pittsburgh
15417 | H | Pittsburgh
15419 | H | Pittsburgh
15420 | H | Pittsburgh
15421 | H | Pittsburgh
15422 | H | Pittsburgh
15423 | H | Pittsburgh
15424 | H | Pittsburgh
15425 | H | Pittsburgh
15427 | H | Pittsburgh
15428 | H | Pittsburgh
15429 | H | Pittsburgh
15430 | H | Pittsburgh
15431 | H | Pittsburgh
15432 | H | Pittsburgh
15433 | H | Pittsburgh
15434 | H | Pittsburgh
15435 | H | Pittsburgh
15436 | H | Pittsburgh
15437 | H | Pittsburgh
15438 | H | Pittsburgh
15439 | H | Pittsburgh
15440 | H | Pittsburgh
15442 | H | Pittsburgh
15443 | H | Pittsburgh
15444 | H | Pittsburgh
15445 | H | Pittsburgh
15446 | H | Pittsburgh
15447 | H | Pittsburgh
15448 | H | Pittsburgh
15449 | H | Pittsburgh
15450 | H | Pittsburgh
15451 | H | Pittsburgh
15454 | H | Pittsburgh
15455 | H | Pittsburgh
15456 | H | Pittsburgh
15458 | H | Pittsburgh
15459 | H | Pittsburgh
15460 | H | Pittsburgh
15461 | H | Pittsburgh
15462 | H | Pittsburgh
15463 | H | Pittsburgh
15464 | H | Pittsburgh
15465 | H | Pittsburgh
15466 | H | Pittsburgh
15467 | H | Pittsburgh
15468 | H | Pittsburgh
15469 | H | Pittsburgh
15470 | H | Pittsburgh
15472 | H | Pittsburgh
15473 | H | Pittsburgh
15474 | H | Pittsburgh
15475 | H | Pittsburgh
15476 | H | Pittsburgh
15477 | H | Pittsburgh
15478 | H | Pittsburgh
15479 | H | Pittsburgh
15480 | H | Pittsburgh
15482 | H | Pittsburgh
15483 | H | Pittsburgh
15484 | H | Pittsburgh
15485 | H | Pittsburgh
15486 | H | Pittsburgh
15488 | H | Pittsburgh
15489 | H | Pittsburgh
15490 | H | Pittsburgh
15492 | H | Pittsburgh
15501 | H | Pittsburgh
15502 | H | Pittsburgh
15510 | H | Pittsburgh
15520 | H | Pittsburgh
15521 | H | Pittsburgh
15522 | H | Pittsburgh
15530 | H | Pittsburgh
15531 | H | Pittsburgh
15532 | H | Pittsburgh
15533 | H | Pittsburgh
15534 | H | Pittsburgh
15535 | H | Pittsburgh
15536 | E | Harrisburg
15537 | H | Pittsburgh
15538 | H | Pittsburgh
15539 | H | Pittsburgh
15540 | H | Pittsburgh
15541 | H | Pittsburgh
15542 | H | Pittsburgh
15544 | H | Pittsburgh
15545 | H | Pittsburgh
15546 | H | Pittsburgh
15547 | H | Pittsburgh
15548 | H | Pittsburgh
15549 | H | Pittsburgh
15550 | H | Pittsburgh
15551 | H | Pittsburgh
15552 | H | Pittsburgh
15553 | H | Pittsburgh
15554 | H | Pittsburgh
15555 | H | Pittsburgh
15557 | H | Pittsburgh
15558 | H | Pittsburgh
15559 | H | Pittsburgh
15560 | H | Pittsburgh
15561 | H | Pittsburgh
15562 | H | Pittsburgh
15563 | H | Pittsburgh
15564 | H | Pittsburgh
15565 | H | Pittsburgh
15601 | H | Pittsburgh
15605 | H | Pittsburgh
15606 | H | Pittsburgh
15610 | H | Pittsburgh
15611 | H | Pittsburgh
15612 | H | Pittsburgh
15613 | H | Pittsburgh
15615 | H | Pittsburgh
15616 | H | Pittsburgh
15617 | H | Pittsburgh
15618 | H | Pittsburgh
15619 | H | Pittsburgh
15620 | H | Pittsburgh
15621 | H | Pittsburgh
15622 | H | Pittsburgh
15623 | H | Pittsburgh
15624 | H | Pittsburgh
15625 | H | Pittsburgh
15626 | H | Pittsburgh
15627 | H | Pittsburgh
15628 | H | Pittsburgh
15629 | H | Pittsburgh
15630 | H | Pittsburgh
15631 | H | Pittsburgh
15632 | H | Pittsburgh
15633 | H | Pittsburgh
15634 | H | Pittsburgh
15635 | H | Pittsburgh
15636 | H | Pittsburgh
15637 | H | Pittsburgh
15638 | H | Pittsburgh
15639 | H | Pittsburgh
15640 | H | Pittsburgh
15641 | H | Pittsburgh
15642 | H | Pittsburgh
15644 | H | Pittsburgh
15646 | H | Pittsburgh
15647 | H | Pittsburgh
15650 | H | Pittsburgh
15655 | H | Pittsburgh
15656 | H | Pittsburgh
15658 | H | Pittsburgh
15660 | H | Pittsburgh
15661 | H | Pittsburgh
15662 | H | Pittsburgh
15663 | H | Pittsburgh
15664 | H | Pittsburgh
15665 | H | Pittsburgh
15666 | H | Pittsburgh
15668 | H | Pittsburgh
15670 | H | Pittsburgh
15671 | H | Pittsburgh
15672 | H | Pittsburgh
15673 | H | Pittsburgh
15674 | H | Pittsburgh
15675 | H | Pittsburgh
15676 | H | Pittsburgh
15677 | H | Pittsburgh
15678 | H | Pittsburgh
15679 | H | Pittsburgh
15680 | H | Pittsburgh
15681 | H | Pittsburgh
15682 | H | Pittsburgh
15683 | H | Pittsburgh
15684 | H | Pittsburgh
15685 | H | Pittsburgh
15686 | H | Pittsburgh
15687 | H | Pittsburgh
15688 | H | Pittsburgh
15689 | H | Pittsburgh
15690 | H | Pittsburgh
15691 | H | Pittsburgh
15692 | H | Pittsburgh
15693 | H | Pittsburgh
15695 | H | Pittsburgh
15696 | H | Pittsburgh
15697 | H | Pittsburgh
15698 | H | Pittsburgh
15701 | H | Pittsburgh
15705 | H | Pittsburgh
15710 | H | Pittsburgh
15711 | I | Erie
15712 | H | Pittsburgh
15713 | H | Pittsburgh
15714 | H | Pittsburgh
15715 | I | Erie
15716 | H | Pittsburgh
15717 | H | Pittsburgh
15720 | H | Pittsburgh
15721 | G | Bradford
15722 | H | Pittsburgh
15723 | H | Pittsburgh
15724 | H | Pittsburgh
15725 | H | Pittsburgh
15727 | H | Pittsburgh
15728 | H | Pittsburgh
15729 | H | Pittsburgh
15730 | I | Erie
15731 | H | Pittsburgh
15732 | H | Pittsburgh
15733 | I | Erie
15734 | H | Pittsburgh
15736 | H | Pittsburgh
15737 | H | Pittsburgh
15738 | H | Pittsburgh
15739 | H | Pittsburgh
15740 | I | Erie
15741 | H | Pittsburgh
15742 | H | Pittsburgh
15744 | I | Erie
15745 | H | Pittsburgh
15746 | H | Pittsburgh
15747 | H | Pittsburgh
15748 | H | Pittsburgh
15750 | H | Pittsburgh
15751 | H | Pittsburgh
15752 | H | Pittsburgh
15753 | G | Bradford
15754 | H | Pittsburgh
15756 | H | Pittsburgh
15757 | G | Bradford
15758 | H | Pittsburgh
15759 | H | Pittsburgh
15760 | H | Pittsburgh
15761 | H | Pittsburgh
15762 | H | Pittsburgh
15763 | H | Pittsburgh
15764 | I | Erie
15765 | H | Pittsburgh
15767 | I | Erie
15770 | I | Erie
15771 | H | Pittsburgh
15772 | H | Pittsburgh
15773 | H | Pittsburgh
15774 | H | Pittsburgh
15775 | H | Pittsburgh
15776 | I | Erie
15777 | H | Pittsburgh
15778 | I | Erie
15779 | H | Pittsburgh
15780 | I | Erie
15781 | I | Erie
15783 | H | Pittsburgh
15784 | I | Erie
15801 | G | Bradford
15821 | G | Bradford
15822 | G | Bradford
15823 | G | Bradford
15824 | I | Erie
15825 | I | Erie
15827 | G | Bradford
15828 | I | Erie
15829 | I | Erie
15831 | G | Bradford
15832 | G | Bradford
15834 | G | Bradford
15840 | I | Erie
15841 | G | Bradford
15845 | G | Bradford
15846 | G | Bradford
15847 | I | Erie
15848 | G | Bradford
15849 | G | Bradford
15851 | I | Erie
15853 | G | Bradford
15856 | G | Bradford
15857 | G | Bradford
15860 | I | Erie
15861 | G | Bradford
15863 | I | Erie
15864 | I | Erie
15865 | I | Erie
15866 | G | Bradford
15868 | G | Bradford
15870 | G | Bradford
15901 | H | Pittsburgh
15902 | H | Pittsburgh
15904 | H | Pittsburgh
15905 | H | Pittsburgh
15906 | H | Pittsburgh
15907 | H | Pittsburgh
15909 | H | Pittsburgh
15915 | H | Pittsburgh
15920 | H | Pittsburgh
15921 | H | Pittsburgh
15922 | H | Pittsburgh
15923 | H | Pittsburgh
15924 | H | Pittsburgh
15925 | H | Pittsburgh
15926 | H | Pittsburgh
15927 | H | Pittsburgh
15928 | H | Pittsburgh
15929 | H | Pittsburgh
15930 | H | Pittsburgh
15931 | H | Pittsburgh
15934 | H | Pittsburgh
15935 | H | Pittsburgh
15936 | H | Pittsburgh
15937 | H | Pittsburgh
15938 | H | Pittsburgh
15940 | H | Pittsburgh
15942 | H | Pittsburgh
15943 | H | Pittsburgh
15944 | H | Pittsburgh
15945 | H | Pittsburgh
15946 | H | Pittsburgh
15948 | H | Pittsburgh
15949 | H | Pittsburgh
15951 | H | Pittsburgh
15952 | H | Pittsburgh
15953 | H | Pittsburgh
15954 | H | Pittsburgh
15955 | H | Pittsburgh
15956 | H | Pittsburgh
15957 | H | Pittsburgh
15958 | H | Pittsburgh
15959 | H | Pittsburgh
15960 | H | Pittsburgh
15961 | H | Pittsburgh
15962 | H | Pittsburgh
15963 | H | Pittsburgh
16001 | H | Pittsburgh
16002 | H | Pittsburgh
16003 | H | Pittsburgh
16016 | H | Pittsburgh
16017 | H | Pittsburgh
16018 | H | Pittsburgh
16020 | H | Pittsburgh
16021 | H | Pittsburgh
16022 | H | Pittsburgh
16023 | H | Pittsburgh
16024 | H | Pittsburgh
16025 | H | Pittsburgh
16027 | H | Pittsburgh
16028 | H | Pittsburgh
16029 | H | Pittsburgh
16030 | H | Pittsburgh
16033 | H | Pittsburgh
16034 | H | Pittsburgh
16035 | H | Pittsburgh
16036 | I | Erie
16037 | H | Pittsburgh
16038 | H | Pittsburgh
16039 | H | Pittsburgh
16040 | H | Pittsburgh
16041 | H | Pittsburgh
16045 | H | Pittsburgh
16046 | H | Pittsburgh
16048 | H | Pittsburgh
16049 | H | Pittsburgh
16050 | H | Pittsburgh
16051 | H | Pittsburgh
16052 | H | Pittsburgh
16053 | H | Pittsburgh
16054 | I | Erie
16055 | H | Pittsburgh
16056 | H | Pittsburgh
16057 | H | Pittsburgh
16058 | H | Pittsburgh
16059 | H | Pittsburgh
16061 | H | Pittsburgh
16063 | H | Pittsburgh
16066 | H | Pittsburgh
16101 | H | Pittsburgh
16102 | H | Pittsburgh
16103 | H | Pittsburgh
16105 | H | Pittsburgh
16107 | H | Pittsburgh
16108 | H | Pittsburgh
16110 | I | Erie
16111 | I | Erie
16112 | H | Pittsburgh
16113 | I | Erie
16114 | I | Erie
16115 | H | Pittsburgh
16116 | H | Pittsburgh
16117 | H | Pittsburgh
16120 | H | Pittsburgh
16121 | I | Erie
16123 | H | Pittsburgh
16124 | I | Erie
16125 | I | Erie
16127 | I | Erie
16130 | I | Erie
16131 | I | Erie
16132 | H | Pittsburgh
16133 | I | Erie
16134 | I | Erie
16136 | H | Pittsburgh
16137 | I | Erie
16140 | H | Pittsburgh
16141 | H | Pittsburgh
16142 | H | Pittsburgh
16143 | H | Pittsburgh
16145 | I | Erie
16146 | I | Erie
16148 | I | Erie
16150 | I | Erie
16151 | I | Erie
16153 | I | Erie
16154 | I | Erie
16155 | H | Pittsburgh
16156 | H | Pittsburgh
16157 | H | Pittsburgh
16159 | I | Erie
16160 | H | Pittsburgh
16161 | I | Erie
16172 | H | Pittsburgh
16201 | H | Pittsburgh
16210 | H | Pittsburgh
16211 | H | Pittsburgh
16212 | H | Pittsburgh
16213 | I | Erie
16214 | I | Erie
16215 | H | Pittsburgh
16216 | H | Pittsburgh
16217 | I | Erie
16218 | H | Pittsburgh
16220 | I | Erie
16221 | I | Erie
16222 | H | Pittsburgh
16223 | H | Pittsburgh
16224 | I | Erie
16225 | I | Erie
16226 | H | Pittsburgh
16228 | H | Pittsburgh
16229 | H | Pittsburgh
16230 | I | Erie
16232 | I | Erie
16233 | I | Erie
16234 | I | Erie
16235 | I | Erie
16236 | H | Pittsburgh
16238 | H | Pittsburgh
16239 | I | Erie
16240 | I | Erie
16242 | I | Erie
16244 | H | Pittsburgh
16245 | H | Pittsburgh
16246 | H | Pittsburgh
16248 | I | Erie
16249 | H | Pittsburgh
16250 | H | Pittsburgh
16253 | H | Pittsburgh
16254 | I | Erie
16255 | I | Erie
16256 | H | Pittsburgh
16257 | I | Erie
16258 | I | Erie
16259 | H | Pittsburgh
16260 | I | Erie
16261 | H | Pittsburgh
16262 | H | Pittsburgh
16263 | H | Pittsburgh
16301 | I | Erie
16311 | I | Erie
16312 | I | Erie
16313 | I | Erie
16314 | I | Erie
16316 | I | Erie
16317 | I | Erie
16319 | I | Erie
16321 | I | Erie
16322 | I | Erie
16323 | I | Erie
16326 | I | Erie
16327 | I | Erie
16328 | I | Erie
16329 | I | Erie
16331 | I | Erie
16332 | I | Erie
16333 | G | Bradford
16334 | I | Erie
16335 | I | Erie
16340 | I | Erie
16341 | I | Erie
16342 | I | Erie
16343 | I | Erie
16344 | I | Erie
16345 | I | Erie
16346 | I | Erie
16347 | I | Erie
16350 | I | Erie
16351 | I | Erie
16352 | I | Erie
16353 | I | Erie
16354 | I | Erie
16360 | I | Erie
16361 | I | Erie
16362 | I | Erie
16364 | I | Erie
16365 | I | Erie
16366 | I | Erie
16367 | I | Erie
16368 | I | Erie
16369 | I | Erie
16370 | I | Erie
16371 | I | Erie
16372 | I | Erie
16373 | I | Erie
16374 | I | Erie
16375 | I | Erie
16388 | I | Erie
16401 | I | Erie
16402 | I | Erie
16403 | I | Erie
16404 | I | Erie
16405 | I | Erie
16406 | I | Erie
16407 | I | Erie
16410 | I | Erie
16411 | I | Erie
16412 | I | Erie
16413 | I | Erie
16415 | I | Erie
16416 | I | Erie
16417 | I | Erie
16420 | I | Erie
16421 | I | Erie
16422 | I | Erie
16423 | I | Erie
16424 | I | Erie
16426 | I | Erie
16427 | I | Erie
16428 | I | Erie
16430 | I | Erie
16432 | I | Erie
16433 | I | Erie
16434 | I | Erie
16435 | I | Erie
16436 | I | Erie
16438 | I | Erie
16440 | I | Erie
16441 | I | Erie
16442 | I | Erie
16443 | I | Erie
16444 | I | Erie
16475 | I | Erie
16501 | I | Erie
16502 | I | Erie
16503 | I | Erie
16504 | I | Erie
16505 | I | Erie
16506 | I | Erie
16507 | I | Erie
16508 | I | Erie
16509 | I | Erie
16510 | I | Erie
16511 | I | Erie
16512 | I | Erie
16514 | I | Erie
16515 | I | Erie
16522 | I | Erie
16530 | I | Erie
16531 | I | Erie
16532 | I | Erie
16533 | I | Erie
16534 | I | Erie
16538 | I | Erie
16541 | I | Erie
16544 | I | Erie
16546 | I | Erie
16550 | I | Erie
16553 | I | Erie
16554 | I | Erie
16558 | I | Erie
16563 | I | Erie
16565 | I | Erie
16601 | H | Pittsburgh
16602 | H | Pittsburgh
16603 | H | Pittsburgh
16611 | F | Williamsport
16613 | H | Pittsburgh
16614 | H | Pittsburgh
16616 | G | Bradford
16617 | H | Pittsburgh
16619 | H | Pittsburgh
16620 | G | Bradford
16621 | F | Williamsport
16622 | F | Williamsport
16623 | F | Williamsport
16624 | H | Pittsburgh
16625 | H | Pittsburgh
16627 | G | Bradford
16629 | H | Pittsburgh
16630 | H | Pittsburgh
16631 | H | Pittsburgh
16633 | H | Pittsburgh
16634 | F | Williamsport
16635 | H | Pittsburgh
16636 | H | Pittsburgh
16637 | H | Pittsburgh
16638 | F | Williamsport
16639 | H | Pittsburgh
16640 | H | Pittsburgh
16641 | H | Pittsburgh
16644 | H | Pittsburgh
16645 | G | Bradford
16646 | H | Pittsburgh
16647 | F | Williamsport
16648 | H | Pittsburgh
16650 | H | Pittsburgh
16651 | G | Bradford
16652 | F | Williamsport
16654 | F | Williamsport
16655 | H | Pittsburgh
16656 | G | Bradford
16657 | F | Williamsport
16659 | H | Pittsburgh
16660 | H | Pittsburgh
16661 | G | Bradford
16662 | H | Pittsburgh
16663 | G | Bradford
16664 | H | Pittsburgh
16665 | H | Pittsburgh
16666 | G | Bradford
16667 | H | Pittsburgh
16668 | H | Pittsburgh
16669 | F | Williamsport
16670 | H | Pittsburgh
16671 | G | Bradford
16672 | H | Pittsburgh
16673 | H | Pittsburgh
16674 | F | Williamsport
16675 | H | Pittsburgh
16677 | F | Williamsport
16678 | H | Pittsburgh
16679 | H | Pittsburgh
16680 | G | Bradford
16681 | G | Bradford
16682 | H | Pittsburgh
16683 | F | Williamsport
16684 | H | Pittsburgh
16685 | F | Williamsport
16686 | H | Pittsburgh
16689 | E | Harrisburg
16691 | E | Harrisburg
16692 | G | Bradford
16693 | H | Pittsburgh
16694 | F | Williamsport
16695 | H | Pittsburgh
16698 | G | Bradford
16699 | H | Pittsburgh
16701 | G | Bradford
16720 | G | Bradford
16724 | G | Bradford
16725 | G | Bradford
16726 | G | Bradford
16727 | G | Bradford
16728 | G | Bradford
16729 | G | Bradford
16730 | G | Bradford
16731 | G | Bradford
16732 | G | Bradford
16733 | G | Bradford
16734 | G | Bradford
16735 | G | Bradford
16738 | G | Bradford
16740 | G | Bradford
16743 | G | Bradford
16744 | G | Bradford
16745 | G | Bradford
16746 | G | Bradford
16748 | G | Bradford
16749 | G | Bradford
16750 | G | Bradford
16751 | G | Bradford
16801 | F | Williamsport
16802 | F | Williamsport
16803 | F | Williamsport
16804 | F | Williamsport
16805 | F | Williamsport
16820 | F | Williamsport
16821 | G | Bradford
16822 | F | Williamsport
16823 | F | Williamsport
16825 | G | Bradford
16826 | F | Williamsport
16827 | F | Williamsport
16828 | F | Williamsport
16829 | F | Williamsport
16830 | G | Bradford
16832 | F | Williamsport
16833 | G | Bradford
16834 | G | Bradford
16835 | F | Williamsport
16836 | G | Bradford
16837 | G | Bradford
16838 | G | Bradford
16839 | G | Bradford
16840 | G | Bradford
16841 | F | Williamsport
16843 | G | Bradford
16844 | F | Williamsport
16845 | G | Bradford
16847 | G | Bradford
16848 | F | Williamsport
16849 | G | Bradford
16850 | G | Bradford
16851 | F | Williamsport
16852 | F | Williamsport
16853 | F | Williamsport
16854 | F | Williamsport
16855 | G | Bradford
16856 | F | Williamsport
16858 | G | Bradford
16859 | F | Williamsport
16860 | F | Williamsport
16861 | G | Bradford
16863 | G | Bradford
16864 | F | Williamsport
16865 | F | Williamsport
16866 | F | Williamsport
16868 | F | Williamsport
16870 | F | Williamsport
16871 | F | Williamsport
16872 | F | Williamsport
16873 | G | Bradford
16874 | F | Williamsport
16875 | F | Williamsport
16876 | G | Bradford
16877 | F | Williamsport
16878 | G | Bradford
16879 | G | Bradford
16881 | G | Bradford
16882 | F | Williamsport
16901 | G | Bradford
16910 | B | Scranton
16911 | G | Bradford
16912 | G | Bradford
16914 | B | Scranton
16915 | G | Bradford
16917 | G | Bradford
16918 | G | Bradford
16920 | G | Bradford
16921 | G | Bradford
16922 | G | Bradford
16923 | G | Bradford
16925 | B | Scranton
16926 | B | Scranton
16927 | G | Bradford
16928 | G | Bradford
16929 | G | Bradford
16930 | G | Bradford
16932 | G | Bradford
16933 | G | Bradford
16935 | G | Bradford
16936 | G | Bradford
16937 | G | Bradford
16938 | G | Bradford
16939 | G | Bradford
16940 | G | Bradford
16941 | G | Bradford
16942 | G | Bradford
16943 | G | Bradford
16945 | B | Scranton
16946 | G | Bradford
16947 | B | Scranton
16948 | G | Bradford
16950 | G | Bradford
17001 | E | Harrisburg
17002 | F | Williamsport
17003 | D | Philadelphia
17004 | F | Williamsport
17005 | E | Harrisburg
17006 | E | Harrisburg
17007 | E | Harrisburg
17008 | E | Harrisburg
17009 | F | Williamsport
17010 | D | Philadelphia
17011 | E | Harrisburg
17012 | E | Harrisburg
17013 | E | Harrisburg
17014 | F | Williamsport
17015 | E | Harrisburg
17016 | D | Philadelphia
17017 | F | Williamsport
17018 | E | Harrisburg
17019 | E | Harrisburg
17020 | E | Harrisburg
17021 | F | Williamsport
17022 | D | Philadelphia
17023 | E | Harrisburg
17024 | E | Harrisburg
17025 | E | Harrisburg
17026 | D | Philadelphia
17027 | E | Harrisburg
17028 | E | Harrisburg
17029 | F | Williamsport
17030 | E | Harrisburg
17031 | F | Williamsport
17032 | E | Harrisburg
17033 | E | Harrisburg
17034 | E | Harrisburg
17035 | F | Williamsport
17036 | E | Harrisburg
17037 | E | Harrisburg
17038 | D | Philadelphia
17039 | D | Philadelphia
17040 | E | Harrisburg
17041 | D | Philadelphia
17042 | D | Philadelphia
17043 | E | Harrisburg
17044 | F | Williamsport
17045 | E | Harrisburg
17046 | D | Philadelphia
17047 | E | Harrisburg
17048 | E | Harrisburg
17049 | F | Williamsport
17050 | E | Harrisburg
17051 | F | Williamsport
17052 | F | Williamsport
17053 | E | Harrisburg
17054 | F | Williamsport
17055 | E | Harrisburg
17056 | F | Williamsport
17057 | E | Harrisburg
17058 | F | Williamsport
17059 | F | Williamsport
17060 | F | Williamsport
17061 | E | Harrisburg
17062 | E | Harrisburg
17063 | F | Williamsport
17064 | D | Philadelphia
17065 | E | Harrisburg
17066 | F | Williamsport
17067 | D | Philadelphia
17068 | E | Harrisburg
17069 | E | Harrisburg
17070 | E | Harrisburg
17071 | E | Harrisburg
17072 | E | Harrisburg
17073 | D | Philadelphia
17074 | E | Harrisburg
17075 | F | Williamsport
17076 | F | Williamsport
17077 | D | Philadelphia
17078 | D | Philadelphia
17080 | E | Harrisburg
17081 | E | Harrisburg
17082 | F | Williamsport
17083 | D | Philadelphia
17084 | F | Williamsport
17085 | D | Philadelphia
17086 | F | Williamsport
17087 | D | Philadelphia
17088 | D | Philadelphia
17089 | E | Harrisburg
17090 | E | Harrisburg
17091 | D | Philadelphia
17093 | E | Harrisburg
17094 | F | Williamsport
17097 | E | Harrisburg
17098 | E | Harrisburg
17099 | F | Williamsport
17101 | E | Harrisburg
17102 | E | Harrisburg
17103 | E | Harrisburg
17104 | E | Harrisburg
17105 | E | Harrisburg
17106 | E | Harrisburg
17107 | E | Harrisburg
17108 | E | Harrisburg
17109 | E | Harrisburg
17110 | E | Harrisburg
17111 | E | Harrisburg
17112 | E | Harrisburg
17113 | E | Harrisburg
17120 | E | Harrisburg
17121 | E | Harrisburg
17122 | E | Harrisburg
17123 | E | Harrisburg
17124 | E | Harrisburg
17125 | E | Harrisburg
17126 | E | Harrisburg
17127 | E | Harrisburg
17128 | E | Harrisburg
17129 | E | Harrisburg
17130 | E | Harrisburg
17140 | E | Harrisburg
17177 | E | Harrisburg
17201 | E | Harrisburg
17202 | E | Harrisburg
17210 | E | Harrisburg
17211 | H | Pittsburgh
17212 | E | Harrisburg
17213 | F | Williamsport
17214 | E | Harrisburg
17215 | E | Harrisburg
17217 | E | Harrisburg
17219 | E | Harrisburg
17220 | E | Harrisburg
17221 | E | Harrisburg
17222 | E | Harrisburg
17223 | E | Harrisburg
17224 | E | Harrisburg
17225 | E | Harrisburg
17228 | E | Harrisburg
17229 | E | Harrisburg
17231 | E | Harrisburg
17232 | E | Harrisburg
17233 | E | Harrisburg
17235 | E | Harrisburg
17236 | E | Harrisburg
17237 | E | Harrisburg
17238 | E | Harrisburg
17239 | F | Williamsport
17240 | E | Harrisburg
17241 | E | Harrisburg
17243 | F | Williamsport
17244 | E | Harrisburg
17246 | E | Harrisburg
17247 | E | Harrisburg
17249 | F | Williamsport
17250 | E | Harrisburg
17251 | E | Harrisburg
17252 | E | Harrisburg
17253 | F | Williamsport
17254 | E | Harrisburg
17255 | F | Williamsport
17256 | E | Harrisburg
17257 | E | Harrisburg
17260 | F | Williamsport
17261 | E | Harrisburg
17262 | E | Harrisburg
17263 | E | Harrisburg
17264 | F | Williamsport
17265 | E | Harrisburg
17266 | E | Harrisburg
17267 | E | Harrisburg
17268 | E | Harrisburg
17270 | E | Harrisburg
17271 | E | Harrisburg
17272 | E | Harrisburg
17301 | E | Harrisburg
17302 | E | Harrisburg
17303 | E | Harrisburg
17304 | E | Harrisburg
17306 | E | Harrisburg
17307 | E | Harrisburg
17309 | E | Harrisburg
17310 | E | Harrisburg
17311 | E | Harrisburg
17312 | E | Harrisburg
17313 | E | Harrisburg
17314 | E | Harrisburg
17315 | E | Harrisburg
17316 | E | Harrisburg
17317 | E | Harrisburg
17318 | E | Harrisburg
17319 | E | Harrisburg
17320 | E | Harrisburg
17321 | E | Harrisburg
17322 | E | Harrisburg
17323 | E | Harrisburg
17324 | E | Harrisburg
17325 | E | Harrisburg
17326 | E | Harrisburg
17327 | E | Harrisburg
17329 | E | Harrisburg
17331 | E | Harrisburg
17332 | E | Harrisburg
17333 | E | Harrisburg
17334 | E | Harrisburg
17337 | E | Harrisburg
17339 | E | Harrisburg
17340 | E | Harrisburg
17342 | E | Harrisburg
17343 | E | Harrisburg
17344 | E | Harrisburg
17345 | E | Harrisburg
17347 | E | Harrisburg
17349 | E | Harrisburg
17350 | E | Harrisburg
17352 | E | Harrisburg
17353 | E | Harrisburg
17354 | E | Harrisburg
17355 | E | Harrisburg
17356 | E | Harrisburg
17358 | E | Harrisburg
17360 | E | Harrisburg
17361 | E | Harrisburg
17362 | E | Harrisburg
17363 | E | Harrisburg
17364 | E | Harrisburg
17365 | E | Harrisburg
17366 | E | Harrisburg
17368 | E | Harrisburg
17370 | E | Harrisburg
17371 | E | Harrisburg
17372 | E | Harrisburg
17375 | E | Harrisburg
17401 | E | Harrisburg
17402 | E | Harrisburg
17403 | E | Harrisburg
17404 | E | Harrisburg
17405 | E | Harrisburg
17406 | E | Harrisburg
17407 | E | Harrisburg
17408 | E | Harrisburg
17415 | E | Harrisburg
17501 | D | Philadelphia
17502 | D | Philadelphia
17503 | D | Philadelphia
17504 | D | Philadelphia
17505 | D | Philadelphia
17506 | D | Philadelphia
17507 | D | Philadelphia
17508 | D | Philadelphia
17509 | D | Philadelphia
17512 | D | Philadelphia
17516 | D | Philadelphia
17517 | D | Philadelphia
17518 | D | Philadelphia
17519 | D | Philadelphia
17520 | D | Philadelphia
17521 | D | Philadelphia
17522 | D | Philadelphia
17527 | D | Philadelphia
17528 | D | Philadelphia
17529 | D | Philadelphia
17532 | D | Philadelphia
17533 | D | Philadelphia
17534 | D | Philadelphia
17535 | D | Philadelphia
17536 | D | Philadelphia
17537 | D | Philadelphia
17538 | D | Philadelphia
17540 | D | Philadelphia
17543 | D | Philadelphia
17545 | D | Philadelphia
17547 | D | Philadelphia
17549 | D | Philadelphia
17550 | D | Philadelphia
17551 | D | Philadelphia
17552 | D | Philadelphia
17554 | D | Philadelphia
17555 | D | Philadelphia
17557 | D | Philadelphia
17560 | D | Philadelphia
17562 | D | Philadelphia
17563 | D | Philadelphia
17564 | D | Philadelphia
17565 | D | Philadelphia
17566 | D | Philadelphia
17567 | D | Philadelphia
17568 | D | Philadelphia
17569 | D | Philadelphia
17570 | D | Philadelphia
17572 | D | Philadelphia
17573 | D | Philadelphia
17575 | D | Philadelphia
17576 | D | Philadelphia
17577 | D | Philadelphia
17578 | D | Philadelphia
17579 | D | Philadelphia
17580 | D | Philadelphia
17581 | D | Philadelphia
17582 | D | Philadelphia
17583 | D | Philadelphia
17584 | D | Philadelphia
17585 | D | Philadelphia
17601 | D | Philadelphia
17602 | D | Philadelphia
17603 | D | Philadelphia
17604 | D | Philadelphia
17605 | D | Philadelphia
17606 | D | Philadelphia
17607 | D | Philadelphia
17608 | D | Philadelphia
17611 | D | Philadelphia
17622 | D | Philadelphia
17699 | D | Philadelphia
17701 | F | Williamsport
17702 | F | Williamsport
17703 | F | Williamsport
17705 | F | Williamsport
17720 | F | Williamsport
17721 | F | Williamsport
17722 | F | Williamsport
17723 | F | Williamsport
17724 | B | Scranton
17726 | F | Williamsport
17727 | F | Williamsport
17728 | F | Williamsport
17729 | F | Williamsport
17730 | F | Williamsport
17731 | B | Scranton
17735 | B | Scranton
17737 | F | Williamsport
17738 | F | Williamsport
17739 | F | Williamsport
17740 | F | Williamsport
17742 | F | Williamsport
17743 | B | Scranton
17744 | F | Williamsport
17745 | F | Williamsport
17747 | F | Williamsport
17748 | F | Williamsport
17749 | F | Williamsport
17750 | F | Williamsport
17751 | F | Williamsport
17752 | F | Williamsport
17754 | F | Williamsport
17756 | F | Williamsport
17758 | B | Scranton
17759 | F | Williamsport
17760 | F | Williamsport
17762 | F | Williamsport
17763 | F | Williamsport
17764 | F | Williamsport
17765 | G | Bradford
17767 | F | Williamsport
17768 | B | Scranton
17769 | F | Williamsport
17771 | F | Williamsport
17772 | F | Williamsport
17773 | F | Williamsport
17774 | F | Williamsport
17776 | F | Williamsport
17777 | F | Williamsport
17778 | F | Williamsport
17779 | F | Williamsport
17801 | F | Williamsport
17810 | F | Williamsport
17812 | F | Williamsport
17813 | F | Williamsport
17814 | F | Williamsport
17815 | F | Williamsport
17820 | F | Williamsport
17821 | F | Williamsport
17822 | F | Williamsport
17823 | F | Williamsport
17824 | F | Williamsport
17825 | F | Williamsport
17827 | F | Williamsport
17828 | F | Williamsport
17829 | F | Williamsport
17830 | F | Williamsport
17831 | F | Williamsport
17832 | F | Williamsport
17833 | F | Williamsport
17834 | F | Williamsport
17835 | F | Williamsport
17836 | F | Williamsport
17837 | F | Williamsport
17839 | F | Williamsport
17840 | F | Williamsport
17841 | F | Williamsport
17842 | F | Williamsport
17843 | F | Williamsport
17844 | F | Williamsport
17845 | F | Williamsport
17846 | F | Williamsport
17847 | F | Williamsport
17850 | F | Williamsport
17851 | F | Williamsport
17853 | F | Williamsport
17855 | F | Williamsport
17856 | F | Williamsport
17857 | F | Williamsport
17858 | F | Williamsport
17859 | F | Williamsport
17860 | F | Williamsport
17861 | F | Williamsport
17862 | F | Williamsport
17864 | F | Williamsport
17865 | F | Williamsport
17866 | F | Williamsport
17867 | F | Williamsport
17868 | F | Williamsport
17870 | F | Williamsport
17872 | F | Williamsport
17876 | F | Williamsport
17877 | F | Williamsport
17878 | F | Williamsport
17880 | F | Williamsport
17881 | F | Williamsport
17882 | F | Williamsport
17883 | F | Williamsport
17884 | F | Williamsport
17885 | F | Williamsport
17886 | F | Williamsport
17887 | F | Williamsport
17888 | F | Williamsport
17889 | F | Williamsport
17901 | C | Allentown
17920 | F | Williamsport
17921 | C | Allentown
17922 | C | Allentown
17923 | C | Allentown
17925 | C | Allentown
17927 | F | Williamsport
17929 | C | Allentown
17930 | C | Allentown
17931 | C | Allentown
17932 | C | Allentown
17933 | C | Allentown
17934 | C | Allentown
17935 | C | Allentown
17936 | C | Allentown
17938 | C | Allentown
17941 | C | Allentown
17942 | C | Allentown
17943 | C | Allentown
17944 | C | Allentown
17945 | F | Williamsport
17946 | C | Allentown
17948 | C | Allentown
17949 | C | Allentown
17951 | C | Allentown
17952 | C | Allentown
17953 | C | Allentown
17954 | C | Allentown
17957 | C | Allentown
17959 | C | Allentown
17960 | C | Allentown
17961 | C | Allentown
17963 | C | Allentown
17964 | C | Allentown
17965 | C | Allentown
17966 | C | Allentown
17967 | C | Allentown
17968 | C | Allentown
17970 | C | Allentown
17972 | C | Allentown
17974 | C | Allentown
17976 | C | Allentown
17978 | E | Harrisburg
17979 | C | Allentown
17980 | C | Allentown
17981 | C | Allentown
17982 | C | Allentown
17983 | C | Allentown
17985 | C | Allentown
18001 | C | Allentown
18002 | C | Allentown
18003 | C | Allentown
18010 | C | Allentown
18011 | C | Allentown
18012 | C | Allentown
18013 | C | Allentown
18014 | C | Allentown
18015 | C | Allentown
18016 | C | Allentown
18017 | C | Allentown
18018 | C | Allentown
18020 | C | Allentown
18025 | C | Allentown
18030 | C | Allentown
18031 | C | Allentown
18032 | C | Allentown
18034 | C | Allentown
18035 | C | Allentown
18036 | C | Allentown
18037 | C | Allentown
18038 | C | Allentown
18039 | D | Philadelphia
18040 | C | Allentown
18041 | D | Philadelphia
18042 | C | Allentown
18043 | C | Allentown
18044 | C | Allentown
18045 | C | Allentown
18046 | C | Allentown
18049 | C | Allentown
18050 | C | Allentown
18051 | C | Allentown
18052 | C | Allentown
18053 | C | Allentown
18054 | D | Philadelphia
18055 | C | Allentown
18056 | D | Philadelphia
18058 | B | Scranton
18059 | C | Allentown
18060 | C | Allentown
18062 | C | Allentown
18063 | C | Allentown
18064 | C | Allentown
18065 | C | Allentown
18066 | C | Allentown
18067 | C | Allentown
18068 | C | Allentown
18069 | C | Allentown
18070 | D | Philadelphia
18071 | C | Allentown
18072 | C | Allentown
18073 | D | Philadelphia
18074 | D | Philadelphia
18076 | D | Philadelphia
18077 | D | Philadelphia
18078 | C | Allentown
18079 | C | Allentown
18080 | C | Allentown
18081 | D | Philadelphia
18083 | C | Allentown
18084 | D | Philadelphia
18085 | C | Allentown
18086 | C | Allentown
18087 | C | Allentown
18088 | C | Allentown
18091 | C | Allentown
18092 | C | Allentown
18098 | C | Allentown
18099 | C | Allentown
18101 | C | Allentown
18102 | C | Allentown
18103 | C | Allentown
18104 | C | Allentown
18105 | C | Allentown
18106 | C | Allentown
18109 | C | Allentown
18175 | C | Allentown
18195 | C | Allentown
18201 | B | Scranton
18202 | B | Scranton
18210 | C | Allentown
18211 | C | Allentown
18212 | C | Allentown
18214 | C | Allentown
18216 | C | Allentown
18218 | C | Allentown
18219 | B | Scranton
18220 | C | Allentown
18221 | B | Scranton
18222 | B | Scranton
18223 | B | Scranton
18224 | B | Scranton
18225 | B | Scranton
18229 | C | Allentown
18230 | C | Allentown
18231 | C | Allentown
18232 | C | Allentown
18234 | B | Scranton
18235 | C | Allentown
18237 | C | Allentown
18239 | B | Scranton
18240 | C | Allentown
18241 | C | Allentown
18242 | C | Allentown
18243 | B | Scranton
18244 | C | Allentown
18245 | C | Allentown
18246 | B | Scranton
18247 | B | Scranton
18248 | C | Allentown
18249 | B | Scranton
18250 | C | Allentown
18251 | B | Scranton
18252 | C | Allentown
18254 | C | Allentown
18255 | C | Allentown
18256 | B | Scranton
18301 | B | Scranton
18302 | B | Scranton
18320 | B | Scranton
18321 | B | Scranton
18322 | B | Scranton
18323 | B | Scranton
18324 | B | Scranton
18325 | B | Scranton
18326 | B | Scranton
18327 | B | Scranton
18328 | B | Scranton
18330 | B | Scranton
18331 | B | Scranton
18332 | B | Scranton
18333 | B | Scranton
18334 | B | Scranton
18335 | B | Scranton
18336 | B | Scranton
18337 | B | Scranton
18340 | B | Scranton
18341 | B | Scranton
18342 | B | Scranton
18343 | C | Allentown
18344 | B | Scranton
18346 | B | Scranton
18347 | B | Scranton
18348 | B | Scranton
18349 | B | Scranton
18350 | B | Scranton
18351 | C | Allentown
18352 | B | Scranton
18353 | B | Scranton
18354 | B | Scranton
18355 | B | Scranton
18356 | B | Scranton
18357 | B | Scranton
18360 | B | Scranton
18370 | B | Scranton
18371 | B | Scranton
18372 | B | Scranton
18373 | B | Scranton
18401 | A | Binghamton, NY
18403 | B | Scranton
18405 | A | Binghamton, NY
18407 | B | Scranton
18410 | B | Scranton
18411 | B | Scranton
18413 | A | Binghamton, NY
18414 | B | Scranton
18415 | A | Binghamton, NY
18416 | B | Scranton
18417 | A | Binghamton, NY
18419 | B | Scranton
18420 | B | Scranton
18421 | A | Binghamton, NY
18424 | B | Scranton
18425 | B | Scranton
18426 | B | Scranton
18427 | A | Binghamton, NY
18428 | B | Scranton
18430 | A | Binghamton, NY
18431 | A | Binghamton, NY
18433 | B | Scranton
18434 | B | Scranton
18435 | B | Scranton
18436 | A | Binghamton, NY
18437 | A | Binghamton, NY
18438 | A | Binghamton, NY
18439 | A | Binghamton, NY
18440 | B | Scranton
18441 | A | Binghamton, NY
18443 | A | Binghamton, NY
18444 | B | Scranton
18445 | A | Binghamton, NY
18446 | B | Scranton
18447 | B | Scranton
18448 | B | Scranton
18449 | A | Binghamton, NY
18451 | B | Scranton
18452 | B | Scranton
18453 | A | Binghamton, NY
18454 | A | Binghamton, NY
18455 | A | Binghamton, NY
18456 | A | Binghamton, NY
18457 | B | Scranton
18458 | B | Scranton
18459 | A | Binghamton, NY
18460 | A | Binghamton, NY
18461 | A | Binghamton, NY
18462 | A | Binghamton, NY
18463 | A | Binghamton, NY
18464 | B | Scranton
18465 | A | Binghamton, NY
18466 | B | Scranton
18469 | A | Binghamton, NY
18470 | A | Binghamton, NY
18471 | B | Scranton
18472 | A | Binghamton, NY
18473 | A | Binghamton, NY
18501 | B | Scranton
18502 | B | Scranton
18503 | B | Scranton
18504 | B | Scranton
18505 | B | Scranton
18507 | B | Scranton
18508 | B | Scranton
18509 | B | Scranton
18510 | B | Scranton
18512 | B | Scranton
18514 | B | Scranton
18515 | B | Scranton
18517 | B | Scranton
18518 | B | Scranton
18519 | B | Scranton
18522 | B | Scranton
18540 | B | Scranton
18577 | B | Scranton
18601 | B | Scranton
18602 | B | Scranton
18603 | F | Williamsport
18610 | B | Scranton
18611 | B | Scranton
18612 | B | Scranton
18614 | B | Scranton
18615 | B | Scranton
18616 | B | Scranton
18617 | B | Scranton
18618 | B | Scranton
18619 | B | Scranton
18621 | B | Scranton
18622 | B | Scranton
18623 | B | Scranton
18624 | C | Allentown
18625 | B | Scranton
18626 | B | Scranton
18627 | B | Scranton
18628 | B | Scranton
18629 | B | Scranton
18630 | B | Scranton
18631 | F | Williamsport
18632 | B | Scranton
18634 | B | Scranton
18635 | B | Scranton
18636 | B | Scranton
18640 | B | Scranton
18641 | B | Scranton
18642 | B | Scranton
18643 | B | Scranton
18644 | B | Scranton
18651 | B | Scranton
18653 | B | Scranton
18654 | B | Scranton
18655 | B | Scranton
18656 | B | Scranton
18657 | B | Scranton
18660 | B | Scranton
18661 | B | Scranton
18690 | B | Scranton
18701 | B | Scranton
18702 | B | Scranton
18703 | B | Scranton
18704 | B | Scranton
18705 | B | Scranton
18706 | B | Scranton
18707 | B | Scranton
18708 | B | Scranton
18709 | B | Scranton
18710 | B | Scranton
18711 | B | Scranton
18761 | B | Scranton
18762 | B | Scranton
18763 | B | Scranton
18764 | B | Scranton
18765 | B | Scranton
18766 | B | Scranton
18767 | B | Scranton
18768 | B | Scranton
18769 | B | Scranton
18773 | B | Scranton
18774 | B | Scranton
18801 | A | Binghamton, NY
18810 | B | Scranton
18812 | A | Binghamton, NY
18813 | A | Binghamton, NY
18814 | B | Scranton
18815 | B | Scranton
18816 | A | Binghamton, NY
18817 | B | Scranton
18818 | A | Binghamton, NY
18820 | A | Binghamton, NY
18821 | A | Binghamton, NY
18822 | A | Binghamton, NY
18823 | A | Binghamton, NY
18824 | A | Binghamton, NY
18825 | A | Binghamton, NY
18826 | A | Binghamton, NY
18827 | A | Binghamton, NY
18828 | A | Binghamton, NY
18829 | B | Scranton
18830 | A | Binghamton, NY
18831 | B | Scranton
18832 | B | Scranton
18833 | B | Scranton
18834 | A | Binghamton, NY
18837 | B | Scranton
18839 | A | Binghamton, NY
18840 | B | Scranton
18842 | A | Binghamton, NY
18843 | A | Binghamton, NY
18844 | A | Binghamton, NY
18845 | B | Scranton
18846 | B | Scranton
18847 | A | Binghamton, NY
18848 | B | Scranton
18850 | B | Scranton
18851 | B | Scranton
18853 | B | Scranton
18854 | B | Scranton
18901 | D | Philadelphia
18902 | D | Philadelphia
18910 | D | Philadelphia
18911 | D | Philadelphia
18912 | D | Philadelphia
18913 | D | Philadelphia
18914 | D | Philadelphia
18915 | D | Philadelphia
18916 | D | Philadelphia
18917 | D | Philadelphia
18918 | D | Philadelphia
18920 | D | Philadelphia
18921 | D | Philadelphia
18922 | D | Philadelphia
18923 | D | Philadelphia
18924 | D | Philadelphia
18925 | D | Philadelphia
18926 | D | Philadelphia
18927 | D | Philadelphia
18928 | D | Philadelphia
18929 | D | Philadelphia
18930 | D | Philadelphia
18931 | D | Philadelphia
18932 | D | Philadelphia
18933 | D | Philadelphia
18934 | D | Philadelphia
18935 | D | Philadelphia
18936 | D | Philadelphia
18938 | D | Philadelphia
18940 | D | Philadelphia
18942 | D | Philadelphia
18943 | D | Philadelphia
18944 | D | Philadelphia
18946 | D | Philadelphia
18947 | D | Philadelphia
18949 | D | Philadelphia
18950 | D | Philadelphia
18951 | D | Philadelphia
18953 | D | Philadelphia
18954 | D | Philadelphia
18955 | D | Philadelphia
18956 | D | Philadelphia
18957 | D | Philadelphia
18958 | D | Philadelphia
18960 | D | Philadelphia
18962 | D | Philadelphia
18963 | D | Philadelphia
18964 | D | Philadelphia
18966 | D | Philadelphia
18968 | D | Philadelphia
18969 | D | Philadelphia
18970 | D | Philadelphia
18971 | D | Philadelphia
18972 | D | Philadelphia
18974 | D | Philadelphia
18976 | D | Philadelphia
18977 | D | Philadelphia
18979 | D | Philadelphia
18980 | D | Philadelphia
18981 | D | Philadelphia
18991 | D | Philadelphia
19001 | D | Philadelphia
19002 | D | Philadelphia
19003 | D | Philadelphia
19004 | D | Philadelphia
19006 | D | Philadelphia
19007 | D | Philadelphia
19008 | D | Philadelphia
19009 | D | Philadelphia
19010 | D | Philadelphia
19012 | D | Philadelphia
19013 | D | Philadelphia
19014 | D | Philadelphia
19015 | D | Philadelphia
19016 | D | Philadelphia
19017 | D | Philadelphia
19018 | D | Philadelphia
19019 | D | Philadelphia
19020 | D | Philadelphia
19021 | D | Philadelphia
19022 | D | Philadelphia
19023 | D | Philadelphia
19025 | D | Philadelphia
19026 | D | Philadelphia
19027 | D | Philadelphia
19028 | D | Philadelphia
19029 | D | Philadelphia
19030 | D | Philadelphia
19031 | D | Philadelphia
19032 | D | Philadelphia
19033 | D | Philadelphia
19034 | D | Philadelphia
19035 | D | Philadelphia
19036 | D | Philadelphia
19037 | D | Philadelphia
19038 | D | Philadelphia
19039 | D | Philadelphia
19040 | D | Philadelphia
19041 | D | Philadelphia
19043 | D | Philadelphia
19044 | D | Philadelphia
19046 | D | Philadelphia
19047 | D | Philadelphia
19048 | D | Philadelphia
19049 | D | Philadelphia
19050 | D | Philadelphia
19052 | D | Philadelphia
19053 | D | Philadelphia
19054 | D | Philadelphia
19055 | D | Philadelphia
19056 | D | Philadelphia
19057 | D | Philadelphia
19058 | D | Philadelphia
19059 | D | Philadelphia
19060 | D | Philadelphia
19061 | D | Philadelphia
19063 | D | Philadelphia
19064 | D | Philadelphia
19065 | D | Philadelphia
19066 | D | Philadelphia
19067 | D | Philadelphia
19070 | D | Philadelphia
19072 | D | Philadelphia
19073 | D | Philadelphia
19074 | D | Philadelphia
19075 | D | Philadelphia
19076 | D | Philadelphia
19078 | D | Philadelphia
19079 | D | Philadelphia
19080 | D | Philadelphia
19081 | D | Philadelphia
19082 | D | Philadelphia
19083 | D | Philadelphia
19085 | D | Philadelphia
19086 | D | Philadelphia
19087 | D | Philadelphia
19088 | D | Philadelphia
19089 | D | Philadelphia
19090 | D | Philadelphia
19091 | D | Philadelphia
19092 | D | Philadelphia
19093 | D | Philadelphia
19094 | D | Philadelphia
19095 | D | Philadelphia
19096 | D | Philadelphia
19098 | D | Philadelphia
19099 | D | Philadelphia
19101 | D | Philadelphia
19102 | D | Philadelphia
19103 | D | Philadelphia
19104 | D | Philadelphia
19105 | D | Philadelphia
19106 | D | Philadelphia
19107 | D | Philadelphia
19108 | D | Philadelphia
19109 | D | Philadelphia
19110 | D | Philadelphia
19111 | D | Philadelphia
19112 | D | Philadelphia
19113 | D | Philadelphia
19114 | D | Philadelphia
19115 | D | Philadelphia
19116 | D | Philadelphia
19118 | D | Philadelphia
19119 | D | Philadelphia
19120 | D | Philadelphia
19121 | D | Philadelphia
19122 | D | Philadelphia
19123 | D | Philadelphia
19124 | D | Philadelphia
19125 | D | Philadelphia
19126 | D | Philadelphia
19127 | D | Philadelphia
19128 | D | Philadelphia
19129 | D | Philadelphia
19130 | D | Philadelphia
19131 | D | Philadelphia
19132 | D | Philadelphia
19133 | D | Philadelphia
19134 | D | Philadelphia
19135 | D | Philadelphia
19136 | D | Philadelphia
19137 | D | Philadelphia
19138 | D | Philadelphia
19139 | D | Philadelphia
19140 | D | Philadelphia
19141 | D | Philadelphia
19142 | D | Philadelphia
19143 | D | Philadelphia
19144 | D | Philadelphia
19145 | D | Philadelphia
19146 | D | Philadelphia
19147 | D | Philadelphia
19148 | D | Philadelphia
19149 | D | Philadelphia
19150 | D | Philadelphia
19151 | D | Philadelphia
19152 | D | Philadelphia
19153 | D | Philadelphia
19154 | D | Philadelphia
19155 | D | Philadelphia
19160 | D | Philadelphia
19161 | D | Philadelphia
19162 | D | Philadelphia
19170 | D | Philadelphia
19171 | D | Philadelphia
19172 | D | Philadelphia
19173 | D | Philadelphia
19175 | D | Philadelphia
19176 | D | Philadelphia
19177 | D | Philadelphia
19178 | D | Philadelphia
19179 | D | Philadelphia
19181 | D | Philadelphia
19182 | D | Philadelphia
19183 | D | Philadelphia
19184 | D | Philadelphia
19185 | D | Philadelphia
19187 | D | Philadelphia
19188 | D | Philadelphia
19190 | D | Philadelphia
19191 | D | Philadelphia
19192 | D | Philadelphia
19193 | D | Philadelphia
19194 | D | Philadelphia
19195 | D | Philadelphia
19196 | D | Philadelphia
19197 | D | Philadelphia
19244 | D | Philadelphia
19255 | D | Philadelphia
19301 | D | Philadelphia
19310 | D | Philadelphia
19311 | D | Philadelphia
19312 | D | Philadelphia
19316 | D | Philadelphia
19317 | D | Philadelphia
19318 | D | Philadelphia
19319 | D | Philadelphia
19320 | D | Philadelphia
19330 | D | Philadelphia
19331 | D | Philadelphia
19333 | D | Philadelphia
19335 | D | Philadelphia
19339 | D | Philadelphia
19340 | D | Philadelphia
19341 | D | Philadelphia
19342 | D | Philadelphia
19343 | D | Philadelphia
19344 | D | Philadelphia
19345 | D | Philadelphia
19346 | D | Philadelphia
19347 | D | Philadelphia
19348 | D | Philadelphia
19350 | D | Philadelphia
19351 | D | Philadelphia
19352 | D | Philadelphia
19353 | D | Philadelphia
19354 | D | Philadelphia
19355 | D | Philadelphia
19357 | D | Philadelphia
19358 | D | Philadelphia
19360 | D | Philadelphia
19362 | D | Philadelphia
19363 | D | Philadelphia
19365 | D | Philadelphia
19366 | D | Philadelphia
19367 | D | Philadelphia
19369 | D | Philadelphia
19370 | D | Philadelphia
19371 | D | Philadelphia
19372 | D | Philadelphia
19373 | D | Philadelphia
19374 | D | Philadelphia
19375 | D | Philadelphia
19376 | D | Philadelphia
19380 | D | Philadelphia
19381 | D | Philadelphia
19382 | D | Philadelphia
19383 | D | Philadelphia
19388 | D | Philadelphia
19390 | D | Philadelphia
19395 | D | Philadelphia
19397 | D | Philadelphia
19398 | D | Philadelphia
19399 | D | Philadelphia
19401 | D | Philadelphia
19403 | D | Philadelphia
19404 | D | Philadelphia
19405 | D | Philadelphia
19406 | D | Philadelphia
19407 | D | Philadelphia
19408 | D | Philadelphia
19409 | D | Philadelphia
19415 | D | Philadelphia
19420 | D | Philadelphia
19421 | D | Philadelphia
19422 | D | Philadelphia
19423 | D | Philadelphia
19424 | D | Philadelphia
19425 | D | Philadelphia
19426 | D | Philadelphia
19428 | D | Philadelphia
19429 | D | Philadelphia
19430 | D | Philadelphia
19432 | D | Philadelphia
19435 | D | Philadelphia
19436 | D | Philadelphia
19437 | D | Philadelphia
19438 | D | Philadelphia
19440 | D | Philadelphia
19441 | D | Philadelphia
19442 | D | Philadelphia
19443 | D | Philadelphia
19444 | D | Philadelphia
19446 | D | Philadelphia
19450 | D | Philadelphia
19451 | D | Philadelphia
19452 | D | Philadelphia
19453 | D | Philadelphia
19454 | D | Philadelphia
19455 | D | Philadelphia
19456 | D | Philadelphia
19457 | D | Philadelphia
19460 | D | Philadelphia
19462 | D | Philadelphia
19464 | D | Philadelphia
19465 | D | Philadelphia
19468 | D | Philadelphia
19470 | D | Philadelphia
19472 | D | Philadelphia
19473 | D | Philadelphia
19474 | D | Philadelphia
19475 | D | Philadelphia
19477 | D | Philadelphia
19478 | D | Philadelphia
19480 | D | Philadelphia
19481 | D | Philadelphia
19482 | D | Philadelphia
19483 | D | Philadelphia
19484 | D | Philadelphia
19485 | D | Philadelphia
19486 | D | Philadelphia
19487 | D | Philadelphia
19488 | D | Philadelphia
19489 | D | Philadelphia
19490 | D | Philadelphia
19492 | D | Philadelphia
19493 | D | Philadelphia
19494 | D | Philadelphia
19495 | D | Philadelphia
19496 | D | Philadelphia
19501 | D | Philadelphia
19503 | D | Philadelphia
19504 | D | Philadelphia
19505 | D | Philadelphia
19506 | D | Philadelphia
19507 | D | Philadelphia
19508 | D | Philadelphia
19510 | D | Philadelphia
19511 | D | Philadelphia
19512 | D | Philadelphia
19516 | D | Philadelphia
19518 | D | Philadelphia
19519 | D | Philadelphia
19520 | D | Philadelphia
19522 | D | Philadelphia
19523 | D | Philadelphia
19525 | D | Philadelphia
19526 | D | Philadelphia
19529 | D | Philadelphia
19530 | D | Philadelphia
19533 | D | Philadelphia
19534 | D | Philadelphia
19535 | D | Philadelphia
19536 | D | Philadelphia
19538 | D | Philadelphia
19539 | D | Philadelphia
19540 | D | Philadelphia
19541 | D | Philadelphia
19542 | D | Philadelphia
19543 | D | Philadelphia
19544 | D | Philadelphia
19545 | D | Philadelphia
19547 | D | Philadelphia
19548 | D | Philadelphia
19549 | C | Allentown
19550 | D | Philadelphia
19551 | D | Philadelphia
19554 | D | Philadelphia
19555 | D | Philadelphia
19557 | D | Philadelphia
19559 | D | Philadelphia
19560 | D | Philadelphia
19562 | D | Philadelphia
19564 | D | Philadelphia
19565 | D | Philadelphia
19567 | D | Philadelphia
19601 | D | Philadelphia
19602 | D | Philadelphia
19603 | D | Philadelphia
19604 | D | Philadelphia
19605 | D | Philadelphia
19606 | D | Philadelphia
19607 | D | Philadelphia
19608 | D | Philadelphia
19609 | D | Philadelphia
19610 | D | Philadelphia
19611 | D | Philadelphia
19612 | D | Philadelphia
19640 | D | Philadelphia

## Instructions
PPL Electric Motors and Drives Estimator
This estimator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this estimator is deemed acceptable for the PPL Electric Business Energy Efficiency Program. However, the assumptions used by the applicant to esimate the annual savings will be reviewed by the Program Team, which is solely responsible for the final determination of the annual energy savings to be used in estimating the incentive amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities. For any questions, or assistance using this estimator, please call 899-432-5501 or email us at pplbusiness@clearesult.com.
Input Instructions
Yellow cells indicate that user input is required. Cells with a * are required.
Grey cells are calculated values.
Worksheet Summary
Methodology
Provides methodology for savings estimations
Project Summary
This provides summary of estimated savings along with some required inputs
Premium Efficiency Motors
This measure applies to the installation of premium‑efficiency, constant‑speed motors in new construction or replace‑on‑burnout applications. Motors must be uniformly loaded and single‑speed. Variable‑speed motors, motors with horsepower changes, or multi‑motor configurations are treated as custom measures.
VFD Improvements
This measure applies to the installation of variable frequency drives (VFDs) on existing constant‑speed motors in standard commercial applications. The baseline condition assumes operation without variable speed control.
ECM Fans
This measure is for the retrofit of existing shaded-pole (SP) or permanent-split capacitor (PSC) evaporator fan motors in an air handling unit to a electronically commutated motor (ECM). This measure only applies to motors of one horsepower or less. Anything greater than 1 HP are governed by NEMA standard. The targeted fan can be for cooling, heating, or both.
VSD Kitchen Fans
This measure is for the installation of variable speed drives (VSD) on commercial kitchen exhaust fans. The VSD must vary the exhaust rate of kitchen ventilation based on the energy and effluent output from the cooking appliances. This involves installing a temperature sensor in the hood exhaust collar and/or an optic sensor on the end of the hood that can sense cooking conditions.
ECM Circulator Pump
This measure applies to replacing existing single‑speed circulator pumps used for space heating, cooling, or domestic hot water with high‑efficiency electronically commutated motor (ECM) circulator pumps. The measure is applicable to commercial and industrial retrofit or replace‑on‑burnout installations.
High Efficiency Pumps
This measure applies to the installation of high‑efficiency clean water pumps in commercial, industrial, or agricultural applications. Eligible pumps include end‑suction, in‑line, split‑case, multistage, and submersible turbine pumps and may be installed as part of retrofit, replace‑on‑burnout, or new construction projects.
Version Log
The Version Log Worksheet tracks updates and changes made to the workbook.
Glossary of Inputs
Date | Date the estimator is completed.
Project Name | Name of project for reference.
Address | Physical location of project.
Installation Date | Date the project is completed.
Project Cost* | The cost associated with the project. Required for incentive calculation.
Location* | The nearest city to the project location.
Building Type* | The building type for the project. If your building type is not listed, please contact the Program.
Motor ID | The ID of the motor for reference.
Motor Function* | The function of the motor. This is a dropdown list. If your motor function is not listed, please contact the Program.
Number of Units* | The number of units to receive the retrofit. May also be referred to as quantity.
NEMA Design Type* | The NEMA type of motor to be installed. Used to calculate baseline efficiency.
Number of Poles* | Number of poles in the motor.
Motor Enclosure* | The motor enclosure type.
Motor Replacement* | Select if the motor is new construction or a replace on burnout.
Horsepower* | The horsepower of the pre and post motor must match.
Manufacturer* | This is the manufacturer of the equipment to be installed. See specific tab for which piece of equipment.
Model Number* | This is the model number of the equipment to be installed. See individual tab for which piece of equipment.
Efficiency* | In premium motors, this is the efficiency of the new NEMA motor.
Control Type* | In VFD's this is the type of control on the fan/pump. If yours is not listed, or you are unsure of which type you have, contact the Program team.
Baseline Motor Type* | This is the baseline motor type for ECM applications.
Equipment Size* | This is the HP size for the ECM motor application. It must be less than or equal to 1 HP.
Fan Application* | This designates if the fan is for heating, cooling, or both.
Glossary of Outputs
kWh Savings | This is the anticipated kWh savings of the line item or measure. | kWh
kW savings | This is the anticipated peak kW savings of the line item/measure.
Incentive | This is the estimated incentive based on project cost and kWh savings.
Run Hours | This is the prescriptive hours of use based on location and facility type.
Coincidence Factor | This is the prescriptive coincidence factor based on the location and facility type.
Motor Efficiency | This is the NEMA efficiency in the Motors tab based on NEMA inputs.
ESF | This is a Energy Savings Factor based on inputs from the VFD tab.
DSF | This is a Demand Savings Factor based on inputs from the VFD tab.

## Project Summary
[5 empty] | HIDE |  | Version | 5.01
[7 empty] | Last Updated | 2026-08-25
Project Summary
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information. | [8 empty] | List
Date | [8 empty] | #REF!
Project Name
Address
Installation Date
Project Cost*
Rate Code*
Zip Code
Location*
Building Type*
Measure | kWh Savings | kW Summer Savings | kW Winter Savings | kW Avg. Savings | Uncapped Incentive | Incentive
Premium Efficiency Motors | 0 | 0 | 0 | 0 | 0 | 0
Variable Frequency Drives (VFDs) | 0 | 0 | 0 | 0 | 0 | 0
ECM Circulating Fans | 0 | 0 | 0 | 0 | 0 | 0
VSD on Kitchen Exhaust Fan | 0 | 0 | 0 | 0 | 0 | 0
ECM Circulator Pump | 0 | 0 | 0 | 0 | 0 | 0
High Efficiency Pumps | 0 | 0 | 0 | 0 | 0 | 0
Total | 0 | 0 | 0 | 0 | 0 | 0

## Premium Eff Motor (hidden)
[6 empty] | HIDE | [5 empty] | HIDE | HIDE |  | HIDE | HIDE |  | HIDE | HIDE |  |  |  |  | HIDE
Premium Efficiency Motors
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information. | [25 empty] | List
This is for constant speed and uniformly loaded motors in new construction and replace on burnout measures. Replacements where old motors and new motors have different horsepowers are considered a custom measure. Motor with variable speeds are considered a custom measure. Systems with multiple motors in a lead-lag setup are also considered custom measures.
#VALUE!
| Motor Information | [16 empty] | Calculations | [6 empty] | Total Incentive
Line Item | Motor ID | Manufacturer | Model Number | Motor Function* | Number of Units* | Load Factor | NEMA Design Type* | Number of Poles* | Motor Enclosure* | Motor Replacement* | Motor Horsepower* | Efficiency | RHRS | ETDF summer | ETDF winter | Horsepower | Efficiency* | Baseline kWh | EE kWh | kWh Savings | kW Summer Savings | kW Winter Savings | Total kW Savings | Uncapped Incentive
1 | [11 empty] | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | [11 empty] | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | [11 empty] | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | [11 empty] | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | [11 empty] | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | [11 empty] | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | [11 empty] | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | [11 empty] | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | [11 empty] | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | [11 empty] | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0

## VFDs
|  |  | HIDE | HIDE |  | HIDE |  |  |  |  | HIDE |  |  | HIDE | HIDE |  |  | HIDE | HIDE |  | HIDE
Variable Frequency Drive (VFD) Improvements
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
The protocol is for standard commercial application where the baseline motor is without a VFD control.
| Motor Information | [7 empty] | Baseline Information |  |  | VFD Information |  | Calculations | [10 empty] | Total Incentive
Line Item | Motor ID | Equipment Type | Ref cell 1 | Ref cell 2 | Motor Function* | Load Factor | Horsepower* | Efficiency* | Control Type* | Quantity* | RHRS | Manufacturer | Model Number | kWhbase | kWhee | PLRsummer peak, base | PLRsummer peak, ee | PLRwinter peak, base | PLRwinter peak, ee | kWh Savings | Uncapped Incentive | kW Summer Savings | kW Winter Savings | Total kW Savings
1 | [5 empty] | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0
2 | [5 empty] | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0
3 | [5 empty] | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0
4 | [5 empty] | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0
5 | [5 empty] | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0
6 | [5 empty] | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0
7 | [5 empty] | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0
8 | [5 empty] | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0
9 | [5 empty] | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0
10 | [5 empty] | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0
Eligibility:
The following protocol for the measurement of energy and demand savings applies to the installation of Variable Frequency Drives (VFDs) in standard commercial building applications – supply and return fans, cooling tower fans, chilled water pumps, and heating water pumps. The baseline condition is a motor without a VFD control. The efficient condition is a motor with a VFD control.
Installations of new equipment with VFDs which are required by energy codes adopted by the State of Pennsylvania are not eligible for incentives.

## ECM Fan (hidden)
[8 empty] | HIDE |  | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE |  | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
ECM Circulating Fan
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
This measure is for the retrofit of existing shaded-pole (SP) or permanent-split capacitor (PSC) evaporator fan motors in an air handling unit to a electronically commutated motor (ECM). This measure only applies to motors of one horsepower or less. Anything greater than 1 HP are governed by NEMA standard. The targeted fan can be for cooling, heating, or both.
| Efficient Unit |  |  | Baseline Unit | [6 empty] | Proposed Unit |  | Calculations | [17 empty] | Total Incentive
Line Item | Unit ID | Manufacturer | Model | Baseline Motor Type* | Motor HP | Quantity* | Fan Application* | Motor Eff | Ventilation Only Hours | Watts | Equipment Type | Watts | LF | EFLH heat | EFLH cool | IF kWh | IF kW | ETDF summer | ETDF winter | kWh heat | kW heat | kWh cool | kW cool | kWh vent | kW vent | kWh savings | kW savings | Uncapped Incentive | kW Summer Savings | kW Winter Savings
1 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | #N/A | #N/A | 0 | #N/A | 0 | #N/A |  |  | 0 | 0 | 0 | 0 | 0
2 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | #N/A | #N/A | 0 | #N/A | 0 | #N/A |  |  | 0 | 0 | 0 | 0 | 0
3 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | #N/A | #N/A | 0 | #N/A | 0 | #N/A |  |  | 0 | 0 | 0 | 0 | 0
4 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | #N/A | #N/A | 0 | #N/A | 0 | #N/A |  |  | 0 | 0 | 0 | 0 | 0
5 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | #N/A | #N/A | 0 | #N/A | 0 | #N/A |  |  | 0 | 0 | 0 | 0 | 0
6 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | #N/A | #N/A | 0 | #N/A | 0 | #N/A |  |  | 0 | 0 | 0 | 0 | 0
7 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | #N/A | #N/A | 0 | #N/A | 0 | #N/A |  |  | 0 | 0 | 0 | 0 | 0
8 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | #N/A | #N/A | 0 | #N/A | 0 | #N/A |  |  | 0 | 0 | 0 | 0 | 0
9 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | #N/A | #N/A | 0 | #N/A | 0 | #N/A |  |  | 0 | 0 | 0 | 0 | 0
10 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | #N/A | #N/A | 0 | #N/A | 0 | #N/A |  |  | 0 | 0 | 0 | 0 | 0
Eligibility:
This measure is targeted to non-residential customers whose air handling equipment currently uses a SP or PSC fan motor rather than an ECM. This measure applies only to circulating fan motors of 1 HP or less. Motors larger than 1 HP are governed by NEMA standards and would see little to no efficiency benefit by adding an ECM. Additionally, new construction and replace-on-burnout vintages are not eligible to participate, as ECM technology is required in new equipment by federal efficiency standards
The targeted fan can supply heating, cooling, ventilation, or any combination of these. A default savings option is offered if motor input wattage is not known. However, these parameters should be collected by EDCs for greatest accuracy. Acceptable baseline conditions are an existing circulating fan with a SP or PSC fan motor 1 HP or less. Efficient conditions are a circulating fan with an ECM.

## VSD Kitchen Fan
[6 empty] | HIDE | HIDE | [5 empty] | HIDE
VSD on Kitchen Exhaust Fan
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
This measure is for the installation of variable speed drives (VSD) on commercial kitchen exhaust fans. The VSD must vary the exhaust rate of kitchen ventilation based on the energy and effluent output from the cooking appliances. This involves installing a temperature sensor in the hood exhaust collar and/or an optic sensor on the end of the hood that can sense cooking conditions.
Line Item | Motor Information |  |  |  |  | Calculations | [7 empty] | Total Incentive
| Unit ID | Manufacturer | Model | Horsepower* | Quantity* | Run Hours | ETDF summer | ETDF winter | kWh Savings | kW Savings | kW Summer Savings | kW Winter Savings | Uncapped Incentive
1 | [5 empty] | 4423 | 0.0001566 | 0.0001309 | 0 | 0 | 0 | 0 | 0
2 | [5 empty] | 4423 | 0.0001566 | 0.0001309 | 0 | 0 | 0 | 0 | 0
3 | [5 empty] | 4423 | 0.0001566 | 0.0001309 | 0 | 0 | 0 | 0 | 0
4 | [5 empty] | 4423 | 0.0001566 | 0.0001309 | 0 | 0 | 0 | 0 | 0
5 | [5 empty] | 4423 | 0.0001566 | 0.0001309 | 0 | 0 | 0 | 0 | 0
6 | [5 empty] | 4423 | 0.0001566 | 0.0001309 | 0 | 0 | 0 | 0 | 0
7 | [5 empty] | 4423 | 0.0001566 | 0.0001309 | 0 | 0 | 0 | 0 | 0
8 | [5 empty] | 4423 | 0.0001566 | 0.0001309 | 0 | 0 | 0 | 0 | 0
9 | [5 empty] | 4423 | 0.0001566 | 0.0001309 | 0 | 0 | 0 | 0 | 0
10 | [5 empty] | 4423 | 0.0001566 | 0.0001309 | 0 | 0 | 0 | 0 | 0

## ECM Circulator Pump
[8 empty] | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE |  |  |  |  | HIDE
ECM Circulating Pump
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
""
Line Item | Efficient Unit | [7 empty] | Baseline Unit | Calculations | [12 empty] | Total Incentive
| Unit ID | Manufacturer | Model | Motor HP | Quantity* | Pump Application* | Pump Control Type* | Watts | Watts | LF | EFLH heat | HOUdhw-base | HOUdhw-ee | EDTF summer | EDTF Winter | kWh heating | kWh dhw | kWh savings | kW Savings | kW summer savings | kW Winter Savings | Uncapped Incentive | Capped Incentive
1 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 |  | 0 | 0
2 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 |  | 0 | 0
3 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 |  | 0 | 0
4 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 |  | 0 | 0
5 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 |  | 0 | 0
6 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 |  | 0 | 0
7 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 |  | 0 | 0
8 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 |  | 0 | 0
9 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 |  | 0 | 0
10 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 |  | 0 | 0

## Appendix D (Manual) (hidden)
Pennsylvania Act 129 Motor & VFD Audit and Design Tool
MANUAL
Table of Contents:
I. Purpose
II. Organization
III. User Guide
IV. Disclaimer
I. Purpose
The purpose of the Motor & VFD Audit and Design Tool is two-fold:
1. To document the pre- and post-installation cases.
2. To facilitate the calculation of energy savings and demand reduction for motor and VFD installations.
II. Organization
The Motor & VFD Audit and Design Tool is organized into 6 sheets.
(1) Manual
The "Manual" sheet contains the instruction manual for using the Motor & VFD Audit and Design Tool.
(2) Changelog
The "Changelog" sheet provides a brief description of major changes from the previous version.
(3) General Information
The "General Information" sheet should be populated with basic information about the project, like project and facility name. Fields for Utility, Facility Type, and Weather Location are necessary to properly pull in default values from the TRM.
(4) 3.3.1 Premium Efficiency Motors
The "3.3.1 Premium Efficiency Motors" sheet collects all relevant information to calculate energy savings and peak demand reduction for motor replacements. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes. Note that the requirements of Section 3.3.1 (Premium Efficiency Motors) in the 2026 TRM restrict the protocol to only motor replacements without VFDs. This form must be used to calculate savings for motor replacement measures only (i.e. replacement of old motors with new energy efficient motors of the same rated horsepower).
The energy efficiency motor and configuration details should be entered in the "Post-Retrofit Details" section (columns E-N). Baseline motor efficiency will be automatically populated using tables as defined in the 2026 TRM. The energy and peak demand savings resulting from the motor replacement alone will be automatically calculated in cells AD6 and AC6 respectively. To calculate savings resulting from VFD measures, refer to the notes described below.
(5) 3.3.2 VFD Improvements
The "3.3.2 VFD Improvements" sheet collects all relevant information to calculate energy savings and peak demand reduction for VFDs. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes. This form must be used to calculate savings for VFD measures only, not the combination of new motors and VFDs.
The motor and configuration details should be entered in the "Post-Retrofit Details" section (Columns E-N) for a motor with VFD. A custom motor load profile can be selected if the appropriate fields are populated on the 'VFD Custom Load Profile' tab. Select the baseline control configuration from the pull down menu in Column O. The energy and peak demand savings resulting from installation of a VFD will be automatically calculated in cells BF6 and BE6 respectively. Note that custom protocols must be followed if the existing motor already has a VFD installed or if the VFD Baseline is not listed in the options.
(6) VFD Custom Load Profile
The "VFD Custom Load Profile" sheet should be used to define custom fan or pump load profiles for a VFD project. Up to 10 custom profiles can be entered.
(7) Lookups
This tab houses lookup tables used in both the motor and VFD calculation worksheets. Tables taken from the TRM include default hours of use and motor baseline efficiency.
III. User Guide
The tool contains all information regarding motors and VFDs required for the calculation of savings pursuant to the PA TRM. The use of this tool is encouraged but not required. Users of the Motor and VFD Audit and Design Tool must complete the "Motor Inventory" and/or "VFD Inventory" depending on the measures installed for the project. For VFD measures in conjunction with a motor replacement measure, the savings must be calculated separately using the "Motor Form" and "VFD Form". To find out how to calculate savings resulting from motor replacement and VFD measures separately, refer to the notes described above. The designer must select the appropriate facility type, utility, and weather file from the drop down menu. Use one line for each unique motor, i.e. motors with different operating conditions or different motor specifications. Complete all green fields to calculate the peak demand reduction and annual energy savings. Gray fields are computed automatically. Roll mouse over the field heading for additional help. Projects with facility types or motor functions not included on the drop down menu must follow custom protocols to determine appropriate run hours and coincidence factor values. Motor replacements with the following conditions should also follow custom protocols:
* Variable frequency drive (VFD) control on the existing (baseline) motor
* Two-speed motor (existing and/or new)
* Single speed motor with variable loading (not standard)
* Industrial process applications
* Applications where the building type or motor usage group is not listed in Table 3-84 through 3-96 of the 2026 TRM
* New motor has a different rated horsepower than the existing motor
* Change in annual operating hours is anticipated
IV. Disclaimer
This document does not modify any requirements of the PA TRM and is provided for convenience only. If any discrepancy between the TRM and this document exist, the TRM should be followed.

## Appendix D (General Information (hidden)
Phase V TRM Appendix D: Motor & VFD Audit and Design Tool
GENERAL INFORMATION
| KEY: | Input Field |  |  | Example Cell |  | Cell Creating Error in Calculations
|  | Calculated Value |  |  | Intermediate Calc.
❶ Project / Site Information
Provide basic project information below.
Applicant Name:
Facility Name:
Installation Address:
| City: |  |  | State: |  | Zip:
| Utility: |  | Account No.:
Contact Name & Title:
Phone:
Email:
Facility Type:
Weather Location:
Installation Date:

## Appendix D (3.3.1 PEM) (hidden)
Phase V TRM Appendix D: Motor & VFD Audit and Design Tool
3.3.1 Premium Efficiency Motors
MOTORS Total
[29 empty] | 0 | 0 | 0
SAVINGS
|  |  |  | POST-RETROFIT DETAILS | [9 empty] | BASELINE DETAILS |  |  | Analysis | [11 empty] | MOTORS
Line Item | Program Year | Unique Motor I.D.(s) | Motor Function | Manufacturer | Model Number | Motor Horsepower | NEMA Design Type | Number of Poles | Enclosure Type | Motor Efficiency | Number of Identical Units | Default Load Factor (LF) | Custom Load Factor (LF) | Default Annual Run Hours | Custom Annual Run Hours | Baseline Nominal Efficiency | Analysis Hours | Analysis LF | Energy to Demand Factor, Summer | Energy to Demand Factor, Winter | Base Full Load kW | Base Annual kWh | Base Peak kW, Summer | Base Peak kW, Winter | Energy Efficient Full Load kW | Energy Efficient Annual kWh | Energy Efficient Peak kW, Summer | Energy Efficient Peak kW, Winter | Energy (kWh) | Peak Demand, Summer (kW) | Peak Demand, Winter (kW) | Lamps Removed Counter | Lamps Installed Counter
Ex. | PY18 | CHWP-1 | SF | Baldor | A12345 | 10 | NEMA Design A | 4 | ODP | 96% | 2 | 0.76 |  | N/A |  | 91.7% | N/A | 0.76 | N/A | N/A | 12.3655 |  |  |  | 11.8117
1 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
2 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
3 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
4 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
5 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
6 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
7 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
8 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
9 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
10 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
Note on J10: Mary-Hall: 3600 RPM 2 Pole 1800 RPM 4 Pole 1200 RPM 6 Pole 900 RPM 8 Pole
Note on N10: Mary-Hall: default value is 0.79 for pumps and 0.76 for fans
Note on O10: Mary-Hall: Use this column to overwrite the default.
Note on Q10: Mary-Hall: Enter custom operating hours to override the default

## Appendix D (3.3.2 VFD Imp) (hidden)
Phase V TRM Appendix D: Motor & VFD Audit and Design Tool
3.3.3 Variable Frequency Drive (VFD) Improvements
Total VFDs
[58 empty] | 0 | 0 | 0
SAVINGS
|  |  | POST-RETROFIT DETAILS | [11 empty] | BASELINE DETAILS | Load Profile | [10 empty] | Baseline Power Part Load Ratios | [10 empty] | VFD Power Part Load Ratios | [10 empty] | Analysis
Line Item | Unique Motor I.D.(s) | Motor Function | Manufacturer | Model Number | Motor Horsepower | Motor Efficiency | Default Load Factor (LF) | Custom Load Factor (LF) | Default Annual Run Hours | Custom Annual Run Hours | Load Profile | Power Part Load Ratio | Avg Flow Fraction During Summer Peak | Avg Flow Fraction During Winter Peak | Baseline Control Type | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% | Analysis Hours | Analysis LF | Full Load kW | Summer Base Peak kW | Winter Base Peak kW | Base Annual kWh | Energy Efficient Summer Peak kW | Energy Efficient Winter Peak kW | Energy Efficient Annual kWh | Summer Peak Demand (kW) | Winter Peak Demand (kW) | Energy (kWh) | Notes
Ex. | SF-1 | SF | Baldor | A12345 | 10 | 90.5% | 0.76 |  | N/A |  | HVAC fan | Fan: VFD with Duct Static Pressure Controls | 90% | 70% | Fan: Constant Volume | 0% | 0% | 1% | 5% | 16% | 22% | 25% | 19% | 9% | 3% | 0% | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [11 empty] | N/A | 0.76 | 6.2648 | 6.2648 | 6.2648
1 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
2 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
3 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
4 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
5 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
6 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
7 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
8 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
9 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
10 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
0
Note on I10: Mary-Hall: default value is 0.79 for pumps and 0.76 for fans
Note on J10: Mary-Hall: Use this column to overwrite the default.
Note on L10: Mary-Hall: Enter custom operating hours to override the default
Note on O10: Josh Baker: Default Values… 90%: CHWP, CTF, CW Pump, and SF 0%: HHW
Note on P10: Mary-Hall: Default Values… 0%: CHWP, CTF, and CW Pump 70%: HHW and SF

## Appendix D (VFD CLP) (hidden)
Phase V TRM Appendix D: Motor & VFD Audit and Design Tool
VFD Custom Load Profile Input
% Capacity | Default HVAC Fan | Default HVAC Pump | Custom Load Profile 1 | Custom Load Profile 2 | Custom Load Profile 3 | Custom Load Profile 4 | Custom Load Profile 5 | Custom Load Profile 6 | Custom Load Profile 7 | Custom Load Profile 8 | Custom Load Profile 9 | Custom Load Profile 10 | MOTORS | Total
0% | 0% | 0%
10% | 0% | 0%
20% | 1% | 0%
30% | 5% | 5%
40% | 16% | 10%
50% | 22% | 20%
60% | 25% | 30%
70% | 19% | 20%
80% | 9% | 10%
90% | 3% | 5%
100% | 0% | 0%
Total | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Note on E5: Mary-Hall: Load Profile can be renamed
Note on F5: Mary-Hall: Load profile can be renamed
Note on G5: Mary-Hall: Load profile can be renamed
Note on H5: Mary-Hall: Load Profile can be renamed
Note on I5: Mary-Hall: Load Profile can be renamed
Note on J5: Mary-Hall: Load Profile can be renamed
Note on K5: Mary-Hall: Load Profile can be renamed
Note on L5: Mary-Hall: Load Profile can be renamed
Note on M5: Mary-Hall: Load Profile can be renamed
Note on N5: Mary-Hall: Load Profile can be renamed
Note on E17: Mary-Hall: Total should equal 100%.
Note on F17: Mary-Hall: Total should equal 100%.
Note on G17: Mary-Hall: Total should equal 100%.

## Appendix D (Lookups) (hidden)
Phase V TRM Appendix D: Motor & VFD Audit and Design Tool
LOOKUPS
[17 empty] | Tables 3-87 through 3-91 | [11 empty] | Table 3-92 Default ETDFs for Fan and Pump Motors in Commercial Buildings | [6 empty] | Table 3-94: Default Load Profiles for HVAC Fans and Pumps
| Table 3‑84: Baseline Efficiencies for NEMA Design A and NEMA Design B Motors | [8 empty] | Table 3‑86: Baseline Motor Nominal Full-Load Efficiencies for NEMA Design C Motors | [6 empty] | Application | Facility Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Default Load Factor | Facility Type | Parameter | Supply Fan Motors | Chilled Water Pump Motors | Cooling Tower Fan Motors | Heating Hot Water Pump Motors | Condenser Water Pump Motors | Flow Fraction (%) | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
Motor Function | HP | 2 Pole (3600 RPM) |  | 4 Pole (1800 RPM) |  | 6 Pole (1200 RPM) |  | 8 Pole (900 RPM) |  | HP | 4 Pole (1800 RPM) |  | 6 Pole (1200 RPM) |  | 8 Pole (900 RPM) |  | SF | Education - College/University | 5798 | 6028 | 5419 | 5720 | 4955 | 5756 | 5646 | 5513 | 5818 | 0.76 | - | - | SF | CHWP | CTF | HHWP | CW Pump | HVAC Fan | 0% | 0% | 1% | 5% | 16% | 22% | 25% | 19% | 9% | 3% | 0%
CHWP |  | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open |  | Enclosed | Open | Enclosed | Open | Enclosed | Open | SF | Education - Other | 4203 | 4563 | 4174 | 4260 | 3647 | 4230 | 4167 | 4212 | 4313 |  | Education - College/University | ETDFs | 0.000163 | 0.0005511 | 0.0004543 | 7.89e-05 | 0.0005511 | HVAC Pump | 0% | 0% | 0% | 5% | 10% | 20% | 30% | 20% | 10% | 5% | 0%
CTF |  | TEFC2 | ODP2 | TEFC4 | ODP4 | TEFC6 | ODP6 | TEFC8 | ODP8 | HP | TEFC4 | ODP4 | TEFC6 | ODP6 | TEFC8 | ODP8 | SF | Grocery | 6437 | 6735 | 6024 | 6278 | 5659 | 6435 | 6340 | 6309 | 6612 |  | Education - College/University | ETDFw | 0.0001443 | 7.6e-06 | 1.33e-05 | 0.0002103 | 7.6e-06 | Custom Load Profile 1 | bar: 0% to 100%
CW Pump | 1 | 77% | 77% | 85.5% | 85.5% | 82.5% | 82% | 75.5% | 75.5% | 1 | 85.5% | 85.5% | 82.5% | 82.5% | 75.5% | 75.5% | SF | Health - Hospital | 8406 | 8722 | 7749 | 8162 | 7407 | 8452 | 8268 | 8219 | 8631 |  | Education - Other | ETDFs | 0.000163 | 0.0005511 | 0.0004543 | 7.89e-05 | 0.0005511 | Custom Load Profile 2 | bar: 0% to 100%
HHWP | 1.5 | 84% | 84% | 86.5% | 86.5% | 87.5% | 86.5% | 78.5% | 77% | 1.5 | 86.5% | 86.5% | 87.5% | 86.5% | 78.5% | 77% | SF | Health - Other | 8406 | 8722 | 7749 | 8162 | 7407 | 8452 | 8268 | 8219 | 8631 |  | Education - Other | ETDFw | 0.0001443 | 7.6e-06 | 1.33e-05 | 0.0002103 | 7.6e-06 | Custom Load Profile 3 | bar: 0% to 100%
SF | 2 | 85.5% | 85.5% | 86.5% | 86.5% | 88.5% | 87.5% | 84% | 86.5% | 2 | 86.5% | 86.5% | 88.5% | 87.5% | 84% | 86.5% | SF | Industrial Manufacturing | 3676 | 3964 | 3609 | 3705 | 3187 | 3703 | 3652 | 3661 | 3773 |  | Grocery | ETDFs | 0.0001853 | 0 | 0 | 0 | 0 | Custom Load Profile 4 | bar: 0% to 100%
| 3 | 86.5% | 85.5% | 89.5% | 89.5% | 89.5% | 88.5% | 85.5% | 87.5% | 3 | 89.5% | 89.5% | 89.5% | 88.5% | 85.5% | 87.5% | SF | Institutional/Public Service | 4979 | 5201 | 4643 | 4861 | 4373 | 5004 | 4909 | 4885 | 5108 |  | Grocery | ETDFw | 0.0001143 | 0 | 0 | 0 | 0 | Custom Load Profile 5 | bar: 0% to 100%
Utility | 5 | 88.5% | 86.5% | 89.5% | 89.5% | 89.5% | 89.5% | 86.5% | 88.5% | 5 | 89.5% | 89.5% | 89.5% | 89.5% | 86.5% | 88.5% | SF | Lodging | 8406 | 8722 | 7749 | 8162 | 7407 | 8452 | 8268 | 8219 | 8631 |  | Health - Hospital | ETDFs | 0.0001222 | 0.0003023 | 0.0002982 | 0.0001047 | 0.0003023 | Custom Load Profile 6 | bar: 0% to 100%
Duquesne Light | 7.5 | 89.5% | 88.5% | 91.7% | 91% | 91% | 90.2% | 86.5% | 89.5% | 7.5 | 91.7% | 91% | 91% | 90.2% | 86.5% | 89.5% | SF | Office | 4026 | 4454 | 4157 | 4138 | 3456 | 3920 | 4002 | 3967 | 4078 |  | Health - Hospital | ETDFw | 0.0001036 | 1.15e-05 | 1.04e-05 | 0.000132 | 1.15e-05 | Custom Load Profile 7 | bar: 0% to 100%
Met-Ed (FirstEnergy) | 10 | 90.2% | 89.5% | 91.7% | 91.7% | 91% | 91.7% | 89.5% | 90.2% | 10 | 91.7% | 91.7% | 91% | 91.7% | 89.5% | 90.2% | SF | Restaurant | 6028 | 2668 | 5739 | 5930 | 5287 | 6007 | 5946 | 5925 | 6194 |  | Health - Other | ETDFs | 0.0001509 | 0.0003904 | 0.0003793 | 0.0001393 | 0.0003904 | Custom Load Profile 8 | bar: 0% to 100%
Penn Power (FirstEnergy) | 15 | 91% | 90.2% | 92.4% | 93% | 91.7% | 91.7% | 89.5% | 90.2% | 15 | 92.4% | 93% | 91.7% | 91.7% | 89.5% | 90.2% | SF | Retail | 4930 | 5166 | 4630 | 4806 | 4319 | 4913 | 4857 | 4831 | 5059 |  | Health - Other | ETDFw | 0.0001266 | 1.77e-05 | 1.18e-05 | 0.000122 | 1.77e-05 | Custom Load Profile 9 | bar: 0% to 100%
Penelec (FirstEnergy) | 20 | 91% | 91% | 93% | 93% | 91.7% | 92.4% | 90.2% | 91% | 20 | 93% | 93% | 91.7% | 92.4% | 90.2% | 91% | SF | Warehouse - Other | 4834 | 5167 | 4652 | 4865 | 4211 | 4987 | 4823 | 4867 | 4954 |  | Industrial Manufacturing | ETDFs | 0.000195 | 0.0006284 | 0.0006211 | 0 | 0.0006284 | Custom Load Profile 10 | bar: 0% to 100%
West Penn Power (FirstEnergy) | 25 | 91.7% | 91.7% | 93.6% | 93.6% | 93% | 93% | 90.2% | 91% | 25 | 93.6% | 93.6% | 93% | 93% | 90.2% | 91% | SF | Warehouse - Refrigerated | 3878 | 4024 | 3575 | 3765 | 3417 | 3899 | 3814 | 3791 | 3982 |  | Industrial Manufacturing | ETDFw | 0.0001268 | 4e-06 | 2e-07 | 0 | 4e-06
PECO | 30 | 91.7% | 91.7% | 93.6% | 94.1% | 93% | 93.6% | 91.7% | 91.7% | 30 | 93.6% | 94.1% | 93% | 93.6% | 91.7% | 91.7% | CHWP | Education - College/University | 5450 | 3402 | 4303 | 5061 | 4503 | 5259 | 4621 | 5321 | 4414 | 0.79 | Institutional / Public Service | ETDFs | 0.0001674 | 0 | 0 | 0 | 0
PPL | 40 | 92.4% | 92.4% | 94.1% | 94.1% | 94.1% | 94.1% | 91.7% | 91.7% | 40 | 94.1% | 94.1% | 94.1% | 94.1% | 91.7% | 91.7% | CHWP | Education - Other | 3701 | 1831 | 2267 | 3023 | 3030 | 4276 | 3158 | 3211 | 2933 |  | Institutional / Public Service | ETDFw | 0.0001136 | 0 | 0 | 0 | 0
| 50 | 93% | 93% | 94.5% | 94.5% | 94.1% | 94.1% | 92.4% | 92.4% | 50 | 94.5% | 94.5% | 94.1% | 94.1% | 92.4% | 92.4% | CHWP | Grocery | [10 empty] | Lodging | ETDFs | 0.0001845 | 0.0002853 | 0.0002514 | 8.62e-05 | 0.0002853
Facility Types | 60 | 93.6% | 93.6% | 95% | 95% | 94.5% | 94.5% | 92.4% | 93% | 60 | 95% | 95% | 94.5% | 94.5% | 92.4% | 93% | CHWP | Health - Hospital | 7600 | 4753 | 5792 | 7102 | 6346 | 7425 | 6600 | 7320 | 6416 |  | Lodging | ETDFw | 0.000116 | 4.65e-05 | 5.2e-06 | 0.0001165 | 4.65e-05
Education - College/University | 75 | 93.6% | 93.6% | 95.4% | 95% | 94.5% | 94.5% | 93.6% | 94.1% | 75 | 95.4% | 95% | 94.5% | 94.5% | 93.6% | 94.1% | CHWP | Health - Other | 5293 | 3062 | 3603 | 4804 | 4555 | 5533 | 4602 | 5157 | 4353 |  | Office | ETDFs | 0.0001769 | 0.0005857 | 0.0005877 | 0.0001947 | 0.0005857
Education - Other | 100 | 94.1% | 93.6% | 95.4% | 95.4% | 95% | 95% | 93.6% | 94.1% | 100 | 95.4% | 95.4% | 95% | 95% | 93.6% | 94.1% | CHWP | Industrial Manufacturing | 2360 | 1293 | 1510 | 2013 | 1934 | 2307 | 1895 | 2166 | 1862 |  | Office | ETDFw | 0.0001345 | 5e-06 | 3.4e-06 | 0.0001874 | 5e-06
Grocery | 125 | 95% | 94.1% | 95.4% | 95.4% | 95% | 95% | 94.1% | 94.1% | 125 | 95.4% | 95.4% | 95% | 95% | 94.1% | 94.1% | CHWP | Institutional/Public Service | [10 empty] | Restaurant | ETDFs | 0.0001565 | 0 | 0 | 0 | 0
Health - Hospital | 150 | 95% | 94.1% | 95.8% | 95.8% | 95.8% | 95.4% | 94.1% | 94.1% | 150 | 95.8% | 95.8% | 95.8% | 95.4% | 94.1% | 94.1% | CHWP | Lodging | 7949 | 4992 | 6177 | 7225 | 6710 | 7516 | 6709 | 7860 | 6585 |  | Restaurant | ETDFw | 0.0001305 | 0 | 0 | 0 | 0
Health - Other | 200 | 95.4% | 95% | 96.2% | 95.8% | 95.8% | 95.4% | 94.5% | 94.1% | 200 | 96.2% | 95.8% | 95.8% | 95.4% | 94.5% | 94.1% | CHWP | Office | 2433 | 1388 | 1653 | 2203 | 2002 | 2484 | 2052 | 2277 | 1951 |  | Retail | ETDFs | 0.000177 | 0.000472 | 0.0002762 | 0.0001031 | 0.000472 | Tables 3-95 and 3-96: Power Part Load Ratios
Industrial Manufacturing | 250 | 95.8% | 95% | 96.2% | 95.8% | 95.8% | 95.8% | 95% | 95% | Custom 1 | Edit | Edit | Edit | Edit | Edit | Edit | CHWP | Restaurant | [10 empty] | Retail | ETDFw | 0.000118 | 1.19e-05 | 1.3e-05 | 9.45e-05 | 1.19e-05 | Flow Fraction (%) | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
Institutional/Public Service | 300 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A | Custom 2 | Edit | Edit | Edit | Edit | Edit | Edit | CHWP | Retail | 4022 | 2392 | 2797 | 3688 | 3424 | 3935 | 3298 | 3802 | 3304 |  | Warehouse - Other | ETDFs | 0.000195 | 0 | 0 | 0 | 0 | Fan: VFD | 0.0475 | 0.0475 | 0.0537 | 0.08 | 0.1289 | 0.2027 | 0.3038 | 0.4346 | 0.5975 | 0.795 | 1.0293
Lodging | 350 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A | Custom 3 | Edit | Edit | Edit | Edit | Edit | Edit | CHWP | Warehouse - Other | [10 empty] | Warehouse - Other | ETDFw | 0.0001268 | 0 | 0 | 0 | 0 | Pump: VFD | 0.27448 | 0.19124 | 0.14325 | 0.1305 | 0.15298 | 0.21071 | 0.30368 | 0.43188 | 0.59533 | 0.79402 | 1.0279
Office | 400 | 95.8% | 95.8% | 96.2% | 95.8% | N/A | N/A | N/A | N/A | [7 empty] | CHWP | Warehouse - Refrigerated | [10 empty] | Warehouse - Refrigerated | ETDFs | 0.000195 | 0 | 0 | 0 | 0 | Fan: Forward Curved with Inlet Guide Vanes | 0.2 | 0.20643 | 0.2157 | 0.2332 | 0.26435 | 0.31454 | 0.38917 | 0.49364 | 0.63334 | 0.81369 | 1.0401
Restaurant | 450 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A | [7 empty] | CTF | Education - College/University | 5448 | 3401 | 4303 | 5061 | 4503 | 5257 | 4619 | 5320 | 4413 | 0.76 | Warehouse - Refrigerated | ETDFw | 0.0001268 | 0 | 0 | 0 | 0 | Fan: Air Foil / Backward Incline with Inlet Guide Vanes | 0.47262 | 0.52642 | 0.55755 | 0.57439 | 0.58535 | 0.59884 | 0.62324 | 0.66697 | 0.73841 | 0.84597 | 0.99806
Retail | 500 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A | [7 empty] | CTF | Education - Other | 3729 | 1832 | 2271 | 3027 | 3046 | 4291 | 3168 | 3215 | 2969 | 0.76 | [7 empty] | Fan: Two-Speed CT Fan | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1
Warehouse - Other | Custom 1 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CTF | Grocery | [17 empty] | Fan: Forward Curved | 0.20419 | 0.22262 | 0.25596 | 0.30419 | 0.36732 | 0.44536 | 0.53829 | 0.64612 | 0.76885 | 0.90649 | 1.059
Warehouse - Refrigerated | Custom 2 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CTF | Health - Hospital | 7598 | 4750 | 5789 | 7099 | 6343 | 7422 | 6597 | 7316 | 6414 | [8 empty] | Fan: Air Foil / Backward Incline | 0.53 | 0.5256 | 0.53276 | 0.57235 | 0.63599 | 0.71526 | 0.80178 | 0.88713 | 0.96293 | 1.0208 | 1.0522
| Custom 3 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CTF | Health - Other | 5296 | 3062 | 3604 | 4805 | 4558 | 5535 | 4604 | 5158 | 4354 | [8 empty] | Fan: Constant Volume | bar: 0% to 100%
NEMA Design Types | [16 empty] | CTF | Industrial Manufacturing | 2360 | 1293 | 1510 | 2013 | 1934 | 2307 | 1895 | 2166 | 1862 | [8 empty] | Pump: Throttle Valve | 0.55212 | 0.61392 | 0.67192 | 0.72612 | 0.77652 | 0.82312 | 0.86592 | 0.90492 | 0.94012 | 0.97152 | 0.99912
NEMA Design A | [16 empty] | CTF | Institutional/Public Service | [17 empty] | Pump: Constant Volume | bar: 0% to 100%
NEMA Design B | Table 3‑84/85: Baseline Efficiencies for NEMA Design A and NEMA Design B Motors | [15 empty] | CTF | Lodging | 7948 | 4989 | 6174 | 7224 | 6708 | 7514 | 6706 | 7856 | 6581
NEMA Design C | HP | 2 Pole (3600 RPM) |  | 4 Pole (1800 RPM) |  | 6 Pole (1200 RPM) |  | 8 Pole (900 RPM) | [8 empty] | CTF | Office | 2433 | 1388 | 1653 | 2203 | 2002 | 2484 | 2052 | 2277 | 1951
|  | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open | [7 empty] | CTF | Restaurant
City |  | TEFC2 | ODP2 | TEFC4 | ODP4 | TEFC6 | ODP6 | TEFC8 | ODP8 | [7 empty] | CTF | Retail | 4022 | 2392 | 2797 | 3688 | 3424 | 3936 | 3298 | 3803 | 3304
Allentown | 1 | 77% | 77% | 85.5% | 85.5% | 82.5% | 82% | 75.5% | 75.5% | [7 empty] | CTF | Warehouse - Other
Binghamton | 1.5 | 84% | 84% | 86.5% | 86.5% | 87.5% | 86.5% | 78.5% | 77% | [7 empty] | CTF | Warehouse - Refrigerated
Bradford | 2 | 85.5% | 85.5% | 86.5% | 86.5% | 88.5% | 87.5% | 84% | 86.5% | [7 empty] | HHWP | Education - College/University | 4548 | 5271 | 5900 | 5036 | 4250 | 4014 | 4572 | 4638 | 4487 | 0.79
Erie | 3 | 86.5% | 85.5% | 89.5% | 89.5% | 89.5% | 88.5% | 85.5% | 87.5% | [7 empty] | HHWP | Education - Other | 3651 | 4251 | 4722 | 4080 | 3492 | 3341 | 3705 | 3830 | 3658
Harrisburg | 5 | 88.5% | 86.5% | 89.5% | 89.5% | 89.5% | 89.5% | 86.5% | 88.5% | [7 empty] | HHWP | Grocery
Philadelphia | 7.5 | 89.5% | 88.5% | 91.7% | 91% | 91% | 90.2% | 86.5% | 89.5% | [7 empty] | HHWP | Health - Hospital | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
Pittsburgh | 10 | 90.2% | 89.5% | 91.7% | 91.7% | 91% | 91.7% | 89.5% | 90.2% | [7 empty] | HHWP | Health - Other | 5934 | 6627 | 7170 | 6280 | 5823 | 5477 | 5991 | 6223 | 6045
Scranton | 15 | 91% | 90.2% | 92.4% | 93% | 91.7% | 91.7% | 89.5% | 90.2% | [7 empty] | HHWP | Industrial Manufacturing | 1258 | 1684 | 1944 | 1555 | 1184 | 1028 | 1287 | 1393 | 1277
Williamsport | 20 | 91% | 91% | 93% | 93% | 91.7% | 92.4% | 90.2% | 91% | [7 empty] | HHWP | Institutional/Public Service
| 25 | 91.7% | 91.7% | 93.6% | 93.6% | 93% | 93% | 90.2% | 91% | [7 empty] | HHWP | Lodging | 6469 | 7072 | 7587 | 6829 | 6155 | 6077 | 6574 | 6628 | 6387
Program Year | 30 | 91.7% | 91.7% | 93.6% | 94.1% | 93% | 93.6% | 91.7% | 91.7% | [7 empty] | HHWP | Office | 3214 | 3876 | 4446 | 3611 | 3014 | 2690 | 3246 | 3336 | 3169
PY18 | 40 | 92.4% | 92.4% | 94.1% | 94.1% | 94.1% | 94.1% | 91.7% | 91.7% | [7 empty] | HHWP | Restaurant
PY19 | 50 | 93% | 93% | 94.5% | 94.5% | 94.1% | 94.1% | 92.4% | 92.4% | [7 empty] | HHWP | Retail | 2676 | 3183 | 3568 | 2960 | 2561 | 2398 | 2908 | 2841 | 2660
PY20 | 60 | 93.6% | 93.6% | 95% | 95% | 94.5% | 94.5% | 92.4% | 93% | [7 empty] | HHWP | Warehouse - Other
PY21 | 75 | 93.6% | 93.6% | 95.4% | 95% | 94.5% | 94.5% | 93.6% | 94.1% | [7 empty] | HHWP | Warehouse - Refrigerated
PY22 | 100 | 95% | 94.5% | 96.2% | 96.2% | 95.8% | 95.8% | 94.5% | 95% | [7 empty] | CW Pump | Education - College/University | 4797 | 2909 | 3428 | 4258 | 3998 | 4917 | 4424 | 4865 | 3977 | 0.79
| 125 | 95.4% | 94.5% | 96.2% | 96.2% | 95.8% | 95.8% | 95% | 95% | [7 empty] | CW Pump | Education - Other | 3329 | 1716 | 2125 | 2834 | 2818 | 4082 | 2843 | 3008 | 2762
| 150 | 95.4% | 94.5% | 96.2% | 96.2% | 96.2% | 95.8% | 95% | 95% | [7 empty] | CW Pump | Grocery
| 200 | 95.8% | 95.4% | 96.5% | 96.2% | 96.2% | 95.8% | 95.4% | 95% | [7 empty] | CW Pump | Health - Hospital | 5372 | 3511 | 4577 | 5140 | 4093 | 5085 | 4830 | 5161 | 4184
| 250 | 96.2% | 95.4% | 96.5% | 96.2% | 96.2% | 96.2% | 95.4% | 95.4% | [7 empty] | CW Pump | Health - Other | 4998 | 3069 | 3593 | 4718 | 4135 | 5251 | 4214 | 5125 | 4243
| 300 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A | [7 empty] | CW Pump | Industrial Manufacturing | 2360 | 1292 | 1507 | 2009 | 1928 | 2305 | 1890 | 2166 | 1860
| 350 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A | [7 empty] | CW Pump | Institutional/Public Service
| 400 | 95.8% | 95.8% | 96.2% | 95.8% | N/A | N/A | N/A | N/A | [7 empty] | CW Pump | Lodging | 7540 | 4545 | 5475 | 6625 | 6182 | 7181 | 6182 | 7441 | 6074
| 450 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A | [7 empty] | CW Pump | Office | 2422 | 1375 | 1636 | 2181 | 1989 | 2473 | 2041 | 2267 | 1940
| 500 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A | [7 empty] | CW Pump | Restaurant
| Custom 1 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CW Pump | Retail | 3929 | 2357 | 2761 | 3636 | 3358 | 3886 | 3253 | 3756 | 3246
| Custom 2 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CW Pump | Warehouse - Other
| Custom 3 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CW Pump | Warehouse - Refrigerated

## Appendix D (Changelog) (hidden)
Pennsylvania Act 129 Motors and Drives Audit and Design Tool
CHANGELOG
Version 7 (Effective June 3, 2010)
1) | Released with TRM Order in June 2010
Version 8 (Submitted October 27, 2011. Effective June 1, 2011)
1) | Created Changelog
2) | Revised "Manual" and "Glossary" to improve user guide and increase usability
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM
Version 9 (Submitted September 13, 2011 for 2012 TRM Tentative Order)
1) | In "Motor and VFD Form", revised formulas in Columns O, P, and S to correct referencing errors
2) | In "Motor and VFD Form", added Column Q (Full Load kW) to correct a calculation error incorrectly applying DSF
3) | In "Motor and VFD Form", revised Column G (Coincidence Factor) to reflect TRM values (0.74 for single, 0.37 for duplex)
4) | In "Glossary", revised definition of coincidence factor to reflect above change.
5) | In "Glossary", added definition for "Full Load kW"
6) | In "Glossary", revised definition of "Nominal Efficiency" to reflect ability to custom input efficiency values for the new motor efficiency and baseline motor efficiency if the new motor is for new construction or replace on burnout.
7) | In "Manual", updated TRM reference from Table 6-12 to Table 3-15
Version 10 (Submitted December 5, 2011 for 2012 TRM Final Order)
1) | In "Motor and VFD Form", updated operating hours lookup table to reflect TRM table.
2) | In "Motor and VFD Form", corrected formulas for efficiency lookups, post-installation peak kW calculation, and total kWh calculation for post-installation line item #7.
3) | In "Motor and VFD Form", updated form to include new ESF and DSF values.
4) | In "Glossary", updated entries to reflect new column O and definition of "baseline".
Version 11 (Submitted August 31, 2012 for 2013 TRM Tentative Order)
1) | Created "Motor Form" and "VFD Form" to calculate savings for motors and VFD measures separately to be consistent with TRM protocols.
2) | In "Motor Form" and "VFD Form", updated operating hours lookup table to reflect TRM table.
3) | In "VFD Form", updated ESF and DSF values lookup table to reflect TRM table.
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D
Version 12 (Submitted December 07, 2012 for 2013 TRM Final Order)
1) | Changed the definition of "Load Factor" in Glossary to be consistent with TRM protocols.
Version 13 (Submitted August 29, 2013 for 2014 TRM Tentative Order)
1) | Revised the algorithms in Column R of the "VFD Form" tab used to calculate energy and peak demand savings to be consistent with TRM protocols. Removed a conversion factor of 0.746 to convert from HP to kW.
Version 13 (Submitted December 05, 2013 for 2014 TRM Final Order)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Removed motor efficiency tables from "VFD Form".
3) | Revised "Motor Form" and added "Motor Custom Input" to allow for addition of custom motor applications.
4) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D.
Version 14 (Submitted August 05, 2014)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Updated "Coincidence Factor" , "Operating Hours" and "Facility Type" lookup tables to reflect new changes to the TRM.
3) | Formulas for Coincidence Factor and Operating hours are updated to reflect changes to the TRM.
4) | Consolidated all lookup tables under single tab "Lookup Tables"; updated references to lookup tables.
5) | Added "City" to the general information section for "Motor Form" , "VFD Form" , "Motor Custom Input" and "Summary"
6) | Linked general information cells of "Motor Form" , "VFD Form" and "Motor Custom Input" to cells in "Summary". Locked the cells to protect their links.
7) | Motor Configuration column is deleted from "Motor Form" and "VFD Form"
8) | Installation date cell is modified to allow entry of a date between 6/1/2015 and 5/31/2016 only. For all other dates , an error message is displayed.
9) | Program Year is limited to Program Year 7.
10) | "VFD on Motor" column is deleted from "VFD Form". The formulas for ESF, DSF and Full Load kW are updated to exclude the deleted column.
11) | "Full Load kW" on "VFD Form" revised - previously displayed a horsepower value. "Peak kW" and "Annual kWh" adjusted to account for change made to "Full Load kW."
12) | Introduced a macro button on "Motor Form" and "VFD Form" that increases number of motor line items for user's convenience.
13) | Added 900 RPM option to "Synchronous Speed" for "Motor Form", "VFD Form" and "Motor Custom Form."
14) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D.
15) | References to "Hot Water Pump" changed to "Heating Hot Water Pump" to be consistent with TRM. References to "HWP" changed to "HHWP."
Version 15 (Submitted February 20, 2015)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Removed "Nema Design Type", "Synchronous Speed" and "Enclosure Type" fields from post-installation data in "Motor Form"
Version 16 (Submitted June 1, 2015)
1) Relocated "Summary" form before the other input forms
2) Updated selectable program years to reflect Phase III program years
3) Updated TRM table references in "Lookup Tables"
Version 17 (Submitted June 1, 2015)
1) Major revisions to the 'VFD Form' tab:
1.1) Renamed to '3.3.2 VFD Improvements'
1.2) Algorithms changed to reflect 2021 TRM. Instead of defined ESF/DSFs, new algorithm uses load profiles, and baseline and VFD part load factors.
1.3) Capability to define custom load profiles added. (See 'VFD Custom Load Profile' tab.) Default 'HVAC Fan' and 'HVAC Pump' profiles included.
2) Reformatted 'Motor Form' to align with new 'VFD Inventory' format, including name change to '3.3.1 Premium Efficiency Motors'
3) 'General Information' tab created to house basic project information.
Version 18 (Submitted May 2024 for 2026 TRM Tentative Order)
1) Major revisions and modifications to worksheet "Lookup" tables
1.1) Annual Run Hours table revised to reflect updated values
1.2) ETDF Table Added
1.3) Two (2) VFD Flow Fraction options added to "Tables 3-74 and 3-75: Power Part Load Ratios"
1.3a) Revision to "Fan: Air Foil / Backward Incline" value at 0%, from 0.56 to 0.53
1.4) Added Program Year lookup list to column A
1.5) Added new lookup table (NEMA_Design_A_or_B_2027) to provide updated baseline efficiency
1.6) Removal of unused lists
1.6a) Baseline Control Types
1.6b) Default Load Profile & VFD Control Type in Motor Function Table
2) Minor revisions to worksheet 3.3.1 Premium Efficiency Motors
2.1) Default Annual Run Hours MATCH function change to accommodate Lookup worksheet table modifications
2.2) Added Program Year input allowing for updated PY19 NEMA Design A and B motor efficiencies per federal standards
2.3) ETDF Implementation
2.3a) Columns and formulas added to lookup summer and winter ETDF values
2.3b) Summer and winter peak demand savings calculations with ETDF additions
2.3c) Removal of coincident factors
3) 3.3.2 VFD Improvements
3.1) Default Load Factor (LF) LOOKUP function change to accommodate Lookup worksheet table modifications
3.2) Default Annual Run Hours MATCH function change to accommodate Lookup worksheet table modifications
3.3) Column N (Power Part Load Ratio) drop menu added into the post-retrofit details inputs
3.2a) This was necessary since there are now multiple power part load ratio curves for fans
3.4) "Summer" and "Winter" peak demand savings separated into columns BH and BI respectively
3.4a) Necessitated the division of Energy Efficient Peak Demand into "Summer" and "Winter" columns BE and BF respectively
3.4b) Necessitated the division of Average Flow Fraction During Peak into "Summer" and "Winter" columns O and P respectively
4) VFD Custom Load Profile worksheet updates
4.1) Revised HVAC Fan load profile flow fraction values to align with TRM
4.2) Default HVAC Fan load profile linked to values in the Lookup worksheet
4.3) Default HVAC Pump load profile linked to values in the Lookup worksheet
Version 19 (Submitted Septmber 2024 for 2026 TRM Tentative Order)
1) Corrected Look-up Table Numbers to align with the 2026 TRM
2) Corrected formula lookup errors on sheet 3.3.1 for Load Factor and Run Hours

## High Efficiency Pumps (hidden)
[8 empty] | HIDE |  |  | HIDE |  | HIDE |  | HIDE | HIDE | HIDE |  |  |  |  | HIDE
High Efficiency Pumps
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
""
Line Item | Pump/Motor Information | [13 empty] | Calculations | [7 empty] | Total Incentive
| Motor ID | Manufacturer | Model Number | Pump Function* | Pump Type | Pump Speed* | Quantity* | Load Factor | Horsepower* | Motor Efficiency* | RHRS | ETDF Summer | ETDF Winter | Pump Energy Index Efficient Case (PEIee) | PEIbase | Baseline kWh | EE kWh | kWh Savings | kW Savings | kW Summer Savings | kW Winter Savings | Uncapped Incentive | Capped Incentive
1 | [14 empty] | #N/A |  |  | 0 | 0 | 0 | 0 | 0
2 | [14 empty] | #N/A |  |  | 0 | 0 | 0 | 0 | 0
3 | [14 empty] | #N/A |  |  | 0 | 0 | 0 | 0 | 0
4 | [14 empty] | #N/A |  |  | 0 | 0 | 0 | 0 | 0
5 | [14 empty] | #N/A |  |  | 0 | 0 | 0 | 0 | 0
6 | [14 empty] | #N/A |  |  | 0 | 0 | 0 | 0 | 0
7 | [14 empty] | #N/A |  |  | 0 | 0 | 0 | 0 | 0
8 | [14 empty] | #N/A |  |  | 0 | 0 | 0 | 0 | 0
9 | [14 empty] | #N/A |  |  | 0 | 0 | 0 | 0 | 0
10 | [14 empty] | #N/A |  |  | 0 | 0 | 0 | 0 | 0

## Methodology (hidden)
Calculator Methodology
Premium Efficiency Motors
The energy savings is calculated from the 2016 PA TRM with errata. Reference that document for any greater detail than what is provided.
VFD Improvement
The energy savings is calculated from the 2026 PA TRM with errata. Reference that document for any greater detail than what is provided.
ECM Motors
The energy savings is calculated from the 2016 PA TRM with errata. Reference that document for any greater detail than what is provided.
VSD on Kitchen Exhaust Fans
The energy savings is calculated from the 2016 PA TRM with errata. Reference that document for any greater detail than what is provided.

## Lookup Table (hidden)
Table 1: Location |  | Table 2A: Facility Type | Table 2B: Facility Type | Table 3: Motor Replace |  | Table 4: Nema Type |  |  | Table 5: Motor Function | Load Factor |  | Table 6: Motor Enclosure |  | Table 7: Horsepower |  | Table 8: Poles
Allentown |  | Education - College / University | Education - College / University | New Construction |  | Type A |  |  | Supply Fan | 0.76 |  | Open |  | 1 |  | 2 | [6 empty] | Supply Fan |  |  | Condensor Water Pump
Binghamton |  | Education - Other | Education - Other | Replace on Burnout |  | Type B |  |  | Cooling Tower Fan | 0.76 |  | Enclosed |  | 1.5 |  | 4 | [6 empty] | Education - College / University |  |  | Education - College / University
Bradford |  | Grocery | Health - Hospital | Early Replacement |  | Type C |  |  | Chilled Water Pump | 0.79 |  |  |  | 2 |  | 6 | [6 empty] | Education - Other |  |  | Education - Other
Erie |  | Health - Hospital | Health - Other | [5 empty] | Heating Hot Water Pump | 0.79 |  |  |  | 3 |  | 8 | [6 empty] | Grocery |  |  | Health - Hospital
Harrisburg |  | Health - Other | Industrial Manufacturing | [5 empty] | Condenser Water Pump | 0.79 |  |  |  | 5 | [8 empty] | Health - Hospital |  |  | Health - Other
Philadelphia |  | Industrial Manufacturing | Lodging | [10 empty] | 7.5 | [8 empty] | Health - Other |  |  | Industrial Manufacturing
Pittsburgh |  | Institutional / Public Service | Office | [10 empty] | 10 | [8 empty] | Industrial Manufacturing |  |  | Lodging
Scranton |  | Lodging | Lodging | [10 empty] | 15 | [8 empty] | Institutional / Public Service |  |  | Office
Williamsport |  | Multifamily (Common Areas) | Retail | [10 empty] | 20 | [8 empty] | Lodging |  |  | Lodging
|  | Office | [11 empty] | 25 | [8 empty] | Multifamily (Common Areas) |  |  | Retail
|  | Restaurant | [11 empty] | 30 | [8 empty] | Office
|  | Retail | [11 empty] | 40 | [8 empty] | Restaurant
|  | Warehouse - Other | [11 empty] | 50 | [8 empty] | Retail
|  | Warehouse - Refrigerated | [11 empty] | 60 | [8 empty] | Warehouse - Other
[14 empty] | 75 | [8 empty] | Warehouse - Refrigerated
|  | CHANGE INCENTIVE LEVELS HERE TO CHANGE INCENTIVES ON ALL TABS | [11 empty] | 100
|  | Incentive / kWh | 0.1 | [10 empty] | 125
|  | Incentive / kW | 0 | [10 empty] | 150
200
250
300
350
400
450
500
Calculation 1: Calculating Baseline Efficiency for Premium Motors
Line Item | NC? | Nema Type | Poles | Open | Horsepower | Table Lookup | 2 close |  | 2 open | 4 close | 4 open | 6 close | 6 open | 8 close | 8 open | 2 Pole | 4 Pole | 6 Pole | 8 Pole | Efficiency
1 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
2 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
3 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
4 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
5 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
6 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
7 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
8 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
9 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
10 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
Table 9: Type A/B | [10 empty] | Table 10: Type C Motors
| 2 Poles |  | 4 Poles |  | 6 Poles |  | 8 Poles |  |  |  |  | 4 Poles |  | 6 Poles |  | 8 Poles
HP | Close | Open | Close | Open | Close | Open | Close |  | Open |  | HP | Close | Open | Close | Open | Close | Open
1 | 77% | 77% | 85.5% | 85.5% | 82.5% | 82% | 75.5% |  | 75.5% |  | 1 | 0.855 | 0.855 | 0.825 | 0.825 | 0.755 | 0.755
1.5 | 84% | 84% | 86.5% | 86.5% | 87.5% | 86.5% | 78.5% |  | 77% |  | 1.5 | 0.865 | 0.865 | 0.875 | 0.865 | 0.785 | 0.77
2 | 85.5% | 85.5% | 86.5% | 86.5% | 88.5% | 87.5% | 84% |  | 86.5% |  | 2 | 0.865 | 0.865 | 0.885 | 0.875 | 0.84 | 0.865
3 | 86.5% | 85.5% | 89.5% | 89.5% | 89.5% | 88.5% | 85.5% |  | 87.5% |  | 3 | 0.895 | 0.895 | 0.895 | 0.885 | 0.855 | 0.875
5 | 88.5% | 86.5% | 89.5% | 89.5% | 89.5% | 89.5% | 86.5% |  | 88.5% |  | 5 | 0.895 | 0.895 | 0.895 | 0.895 | 0.865 | 0.885
7.5 | 89.5% | 88.5% | 91.7% | 91% | 91% | 90.2% | 86.5% |  | 89.5% |  | 7.5 | 0.917 | 0.91 | 0.91 | 0.902 | 0.865 | 0.895
10 | 90.2% | 89.5% | 91.7% | 91.7% | 91% | 91.7% | 89.5% |  | 90.2% |  | 10 | 0.917 | 0.917 | 0.91 | 0.917 | 0.895 | 0.902
15 | 91% | 90.2% | 92.4% | 93% | 91.7% | 91.7% | 89.5% |  | 90.2% |  | 15 | 0.924 | 0.93 | 0.917 | 0.917 | 0.895 | 0.902
20 | 91% | 91% | 93% | 93% | 91.7% | 92.4% | 90.2% |  | 91% |  | 20 | 0.93 | 0.93 | 0.917 | 0.924 | 0.902 | 0.91
25 | 91.7% | 91.7% | 93.6% | 93.6% | 93% | 93% | 90.2% |  | 91% |  | 25 | 0.936 | 0.936 | 0.93 | 0.93 | 0.902 | 0.91
30 | 91.7% | 91.7% | 93.6% | 94.1% | 93% | 93.6% | 91.7% |  | 91.7% |  | 30 | 0.936 | 0.941 | 0.93 | 0.936 | 0.917 | 0.917
40 | 92.4% | 92.4% | 94.1% | 94.1% | 94.1% | 94.1% | 91.7% |  | 91.7% |  | 40 | 0.941 | 0.941 | 0.941 | 0.941 | 0.917 | 0.917
50 | 93% | 93% | 94.5% | 94.5% | 94.1% | 94.1% | 92.4% |  | 92.4% |  | 50 | 0.945 | 0.945 | 0.941 | 0.941 | 0.924 | 0.924
60 | 93.6% | 93.6% | 95% | 95% | 94.5% | 94.5% | 92.4% |  | 93% |  | 60 | 0.95 | 0.95 | 0.945 | 0.945 | 0.924 | 0.93
75 | 93.6% | 93.6% | 95.4% | 95% | 94.5% | 94.5% | 93.6% |  | 94.1% |  | 75 | 0.954 | 0.95 | 0.945 | 0.945 | 0.936 | 0.941
100 | 94.1% | 93.6% | 95.4% | 95.4% | 95% | 95% | 93.6% |  | 94.1% |  | 100 | 0.954 | 0.954 | 0.95 | 0.95 | 0.936 | 0.941
125 | 95% | 94.1% | 95.4% | 95.4% | 95% | 95% | 94.1% |  | 94.1% |  | 125 | 0.954 | 0.954 | 0.95 | 0.95 | 0.941 | 0.941
150 | 95% | 94.1% | 95.8% | 95.8% | 95.8% | 95.4% | 94.1% |  | 94.1% |  | 150 | 0.958 | 0.958 | 0.958 | 0.954 | 0.941 | 0.941
200 | 95.4% | 95% | 96.2% | 95.8% | 95.8% | 95.4% | 94.5% |  | 94.1% |  | 200 | 0.962 | 0.958 | 0.958 | 0.954 | 0.945 | 0.941
250 | 95.8% | 95% | 96.2% | 95.8% | 95.8% | 95.8% | 95% |  | 95%
300 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A |  | N/A |  | Table 3-92: ETDF (premium Eff motor) | [8 empty] | Table 3-99 ETDF (ECM Fan) |  |  | Table 3-103 ETDF (ECM Circulatory Pump) |  |  | Table 3-106 ETDF (High Efficiency Pumps)
350 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A |  | N/A |  | Type | Parameter | Supply Fan | Chilled Water Pump | Cooling Tower Fan | Heating Hot Water Pump | Condenser Water Pump |  |  | Building Type | ETDF Summer | ETDF Winter | Building Type | ETDF Summer | ETDF Winter | Building Type | ETDF Summer | ETDF Winter
400 | 95.8% | 95.8% | 96.2% | 95.8% | N/A | N/A | N/A |  | N/A |  | Education - College / University | EDTF Summer | 0.000163 | 0.0005511 | 0.0004543 | 7.89e-05 | 0.0005511 | Supply Fan | 3 | Education - College / University | 0.000163 | 0.0001443 | Education - College / University | 0.0002026 | 0.0001374 | Education - College / University | 0.0002026 | 0.0001374
450 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A |  | N/A |  | Education - Other | EDTF Summer | 0.000163 | 0.0005511 | 0.0004543 | 7.89e-05 | 0.0005511 | Chilled Water Pump | 4 | Education - Other | 0.000163 | 0.0001443 | Education - Other | 0.000163 | 0.0001443 | Education - Other | 0.000163 | 0.0001443
500 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A |  | N/A |  | Grocery | EDTF Summer | 0.0001853 | 0 | 0 | 0 | 0 | Cooling Tower Fan | 5 | Grocery | 0.0001633 | 0.0001241 | Grocery | 0.0001633 | 0.0001241 | Grocery | 0.0001633 | 0.0001241
[11 empty] | Health - Hospital | EDTF Summer | 0.0001222 | 0.0003023 | 0.0002982 | 0.0001047 | 0.0003023 | Heating Hot Water Pump | 6 | Health - Hospital | 0.0001222 | 0.0001036 | Health - Hospital | 0.0001222 | 0.0001036 | Health - Hospital | 0.0001222 | 0.0001036
Table 3-87 - 3-91: RHRS | [10 empty] | Health - Other | EDTF Summer | 0.0001509 | 0.0003904 | 0.0003793 | 0.0001393 | 0.0003904 | Condenser Water Pump | 7 | Health - Other | 0.0001509 | 0.0001266 | Health - Other | 0.0001509 | 0.0001266 | Health - Other | 0.0001509 | 0.0001266
City | Type | Type Combined | Chilled Water Pump | Cooling Tower Fan | Condenser Water Pump | Heating Hot Water Pump | Supply Fan |  |  |  | Industrial Manufacturing | EDTF Summer | 0.000195 | 0.0006284 | 0.0006211 | 0 | 0.0006284 |  |  | Industrial Manufacturing | 0.000195 | 0.0001268 | Industrial Manufacturing | 0.000195 | 0.0001268 | Industrial Manufacturing | 0.000195 | 0.0001268 | sss
Allentown | Education - College / University | Allentown Education - College / University | 5450 | 5448 | 4797 | 4548 | 5798 |  |  |  | Institutional / Public Service | EDTF Summer | 0.0001674 | 0 | 0 | 0 | 0 |  |  | Institutional / Public Service | 0.0001674 | 0.0001136 | Institutional / Public Service | 0.0001674 | 0.0001136 | Institutional / Public Service | 0.0001674 | 0.0001136
Allentown | Education - Other | Allentown Education - Other | 3701 | 3729 | 3329 | 3651 | 4203 |  |  |  | Lodging | EDTF Summer | 0.0001845 | 0.0002853 | 0.0002514 | 8.62e-05 | 0.0002853 |  |  | Lodging | 0.0001847 | 0.0001175 | Lodging | 0.0001847 | 0.0001175 | Lodging | 0.0001847 | 0.0001175
Allentown | Grocery | Allentown Grocery | N/A | N/A | N/A | N/A | 6437 |  |  |  | Office | EDTF Summer | 0.0001769 | 0.0005857 | 0.0005877 | 0.0001947 | 0.0005857 |  |  | Office | 0.0001665 | 0.0001242 | Office | 0.0001665 | 0.0001242 | Office | 0.0001665 | 0.0001242
Allentown | Health - Hospital | Allentown Health - Hospital | 7600 | 7598 | 5372 | 8760 | 8406 |  |  |  | Restaurant | EDTF Summer | 0.0001565 | 0 | 0 | 0 | 0 |  |  | Restaurant | 0.0001566 | 0.0001309 | Restaurant | 0.0001566 | 0.0001309 | Restaurant | 0.0001566 | 0.0001309
Allentown | Health - Other | Allentown Health - Other | 5293 | 5296 | 4998 | 5934 | 8406 |  |  |  | Retail | EDTF Summer | 0.000177 | 0.000472 | 0.0002762 | 0.0001031 | 0.000472 |  |  | Retail | 0.0001633 | 0.0001241 | Retail | 0.0001633 | 0.0001241 | Retail | 0.0001633 | 0.0001241
Allentown | Industrial Manufacturing | Allentown Industrial Manufacturing | 2360 | 2360 | 2360 | 1258 | 3676 |  |  |  | Warehouse - Other | EDTF Summer | 0.000195 | 0 | 0 | 0 | 0 |  |  | Warehouse - Other | 0.000195 | 0.0001268 | Warehouse - Other | 0.000195 | 0.0001268 | Warehouse - Other | 0.000195 | 0.0001268
Allentown | Institutional / Public Service | Allentown Institutional / Public Service | N/A | N/A | N/A | N/A | 4979 |  |  |  | Warehouse - Refrigerated | EDTF Summer | 0.000195 | 0 | 0 | 0 | 0 |  |  | Warehouse - Refrigerated | 0.000195 | 0.0001268 | Warehouse - Refrigerated | 0.000195 | 0.0001268 | Warehouse - Refrigerated | 0.000195 | 0.0001268
Allentown | Lodging | Allentown Lodging | 7949 | 7948 | 7540 | 6469 | 8406 |  |  |  | Education - College / University | EDTF Winter | 0.0001443 | 7.6e-06 | 1.33e-05 | 0.0002103 | 7.6e-06
Allentown | Office | Allentown Office | 2433 | 2433 | 2422 | 3214 | 4026 |  |  |  | Education - Other | EDTF Winter | 0.0001443 | 7.6e-06 | 1.33e-05 | 0.0002103 | 7.6e-06
Allentown | Restaurant | Allentown Restaurant | N/A | N/A | N/A | N/A | 6028 |  |  |  | Grocery | EDTF Winter | 0.0001143 | 0 | 0 | 0 | 0
Allentown | Retail | Allentown Retail | 4022 | 4022 | 3929 | 2676 | 4930 |  |  |  | Health - Hospital | EDTF Winter | 0.0001036 | 1.15e-05 | 1.04e-05 | 0.000132 | 1.15e-05
Allentown | Warehouse - Other | Allentown Warehouse - Other | N/A | N/A | N/A | N/A | 4834 |  |  |  | Health - Other | EDTF Winter | 0.0001266 | 1.77e-05 | 1.18e-05 | 0.000122 | 1.77e-05
Allentown | Warehouse - Refrigerated | Allentown Warehouse - Refrigerated | N/A | N/A | N/A | N/A | 3878 |  |  |  | Industrial Manufacturing | EDTF Winter | 0.0001268 | 4e-06 | 2e-07 | 0 | 4e-06
Binghamton | Education - College / University | Binghamton Education - College / University | 3402 | 3401 | 2909 | 5271 | 6028 |  |  |  | Institutional / Public Service | EDTF Winter | 0.0001136 | 0 | 0 | 0 | 0
Binghamton | Education - Other | Binghamton Education - Other | 1831 | 1832 | 1716 | 4251 | 4563 |  |  |  | Lodging | EDTF Winter | 0.000116 | 4.65e-05 | 5.2e-06 | 0.0001165 | 4.65e-05
Binghamton | Grocery | Binghamton Grocery | N/A | N/A | N/A | N/A | 6735 |  |  |  | Office | EDTF Winter | 0.0001345 | 5e-06 | 3.4e-06 | 0.0001874 | 5e-06
Binghamton | Health - Hospital | Binghamton Health - Hospital | 4753 | 4750 | 3511 | 8760 | 8722 |  |  |  | Restaurant | EDTF Winter | 0.0001305 | 0 | 0 | 0 | 0
Binghamton | Health - Other | Binghamton Health - Other | 3062 | 3062 | 3069 | 6627 | 8722 |  |  |  | Retail | EDTF Winter | 0.000118 | 1.19e-05 | 1.3e-05 | 9.45e-05 | 1.19e-05
Binghamton | Industrial Manufacturing | Binghamton Industrial Manufacturing | 1293 | 1293 | 1292 | 1684 | 3964 |  |  |  | Warehouse - Other | EDTF Winter | 0.0001268 | 0 | 0 | 0 | 0
Binghamton | Institutional / Public Service | Binghamton Institutional / Public Service | N/A | N/A | N/A | N/A | 5201 |  |  |  | Warehouse - Refrigerated | EDTF Winter | 0.0001268 | 0 | 0 | 0 | 0
Binghamton | Lodging | Binghamton Lodging | 4992 | 4989 | 4545 | 7072 | 8722
Binghamton | Office | Binghamton Office | 1388 | 1388 | 1375 | 3876 | 4454
Binghamton | Restaurant | Binghamton Restaurant | N/A | N/A | N/A | N/A | 2668
Binghamton | Retail | Binghamton Retail | 2392 | 2392 | 2357 | 3183 | 5166
Binghamton | Warehouse - Other | Binghamton Warehouse - Other | N/A | N/A | N/A | N/A | 5167
Binghamton | Warehouse - Refrigerated | Binghamton Warehouse - Refrigerated | N/A | N/A | N/A | N/A | 4024
Bradford | Education - College / University | Bradford Education - College / University | 4303 | 4303 | 3428 | 5900 | 5419
Bradford | Education - Other | Bradford Education - Other | 2267 | 2271 | 2125 | 4722 | 4174
Bradford | Grocery | Bradford Grocery | N/A | N/A | N/A | N/A | 6024
Bradford | Health - Hospital | Bradford Health - Hospital | 5792 | 5789 | 4577 | 8760 | 7749
Bradford | Health - Other | Bradford Health - Other | 3603 | 3604 | 3593 | 7170 | 7749
Bradford | Industrial Manufacturing | Bradford Industrial Manufacturing | 1510 | 1510 | 1507 | 1944 | 3609
Bradford | Institutional / Public Service | Bradford Institutional / Public Service | N/A | N/A | N/A | N/A | 4643
Bradford | Lodging | Bradford Lodging | 6177 | 6174 | 5475 | 7587 | 7749
Bradford | Office | Bradford Office | 1653 | 1653 | 1636 | 4446 | 4157
Bradford | Restaurant | Bradford Restaurant | N/A | N/A | N/A | N/A | 5739
Bradford | Retail | Bradford Retail | 2797 | 2797 | 2761 | 3568 | 4630
Bradford | Warehouse - Other | Bradford Warehouse - Other | N/A | N/A | N/A | N/A | 4652
Bradford | Warehouse - Refrigerated | Bradford Warehouse - Refrigerated | N/A | N/A | N/A | N/A | 3575
Erie | Education - College / University | Erie Education - College / University | 5061 | 5061 | 4258 | 5036 | 5720
Erie | Education - Other | Erie Education - Other | 3023 | 3027 | 2834 | 4080 | 4260
Erie | Grocery | Erie Grocery | N/A | N/A | N/A | N/A | 6278
Erie | Health - Hospital | Erie Health - Hospital | 7102 | 7099 | 5140 | 8760 | 8162
Erie | Health - Other | Erie Health - Other | 4804 | 4805 | 4718 | 6280 | 8162
Erie | Industrial Manufacturing | Erie Industrial Manufacturing | 2013 | 2013 | 2009 | 1555 | 3705
Erie | Institutional / Public Service | Erie Institutional / Public Service | N/A | N/A | N/A | N/A | 4861
Erie | Lodging | Erie Lodging | 7225 | 7224 | 6625 | 6829 | 8162
Erie | Office | Erie Office | 2203 | 2203 | 2181 | 3611 | 4138
Erie | Restaurant | Erie Restaurant | N/A | N/A | N/A | N/A | 5930
Erie | Retail | Erie Retail | 3688 | 3688 | 3636 | 2960 | 4806
Erie | Warehouse - Other | Erie Warehouse - Other | N/A | N/A | N/A | N/A | 4865
Erie | Warehouse - Refrigerated | Erie Warehouse - Refrigerated | N/A | N/A | N/A | N/A | 3765
Harrisburg | Education - College / University | Harrisburg Education - College / University | 4503 | 4503 | 3998 | 4250 | 4955
Harrisburg | Education - Other | Harrisburg Education - Other | 3030 | 3046 | 2818 | 3492 | 3647
Harrisburg | Grocery | Harrisburg Grocery | N/A | N/A | N/A | N/A | 5659
Harrisburg | Health - Hospital | Harrisburg Health - Hospital | 6346 | 6343 | 4093 | 8760 | 7407
Harrisburg | Health - Other | Harrisburg Health - Other | 4555 | 4558 | 4135 | 5823 | 7407
Harrisburg | Industrial Manufacturing | Harrisburg Industrial Manufacturing | 1934 | 1934 | 1928 | 1184 | 3187
Harrisburg | Institutional / Public Service | Harrisburg Institutional / Public Service | N/A | N/A | N/A | N/A | 4373
Harrisburg | Lodging | Harrisburg Lodging | 6710 | 6708 | 6182 | 6155 | 7407
Harrisburg | Office | Harrisburg Office | 2002 | 2002 | 1989 | 3014 | 3456
Harrisburg | Restaurant | Harrisburg Restaurant | N/A | N/A | N/A | N/A | 5287
Harrisburg | Retail | Harrisburg Retail | 3424 | 3424 | 3358 | 2561 | 4319
Harrisburg | Warehouse - Other | Harrisburg Warehouse - Other | N/A | N/A | N/A | N/A | 4211
Harrisburg | Warehouse - Refrigerated | Harrisburg Warehouse - Refrigerated | N/A | N/A | N/A | N/A | 3417
Philadelphia | Education - College / University | Philadelphia Education - College / University | 5259 | 5257 | 4917 | 4014 | 5756
Philadelphia | Education - Other | Philadelphia Education - Other | 4276 | 4291 | 4082 | 3341 | 4230
Philadelphia | Grocery | Philadelphia Grocery | N/A | N/A | N/A | N/A | 6435
Philadelphia | Health - Hospital | Philadelphia Health - Hospital | 7425 | 7422 | 5085 | 8760 | 8452
Philadelphia | Health - Other | Philadelphia Health - Other | 5533 | 5535 | 5251 | 5477 | 8452
Philadelphia | Industrial Manufacturing | Philadelphia Industrial Manufacturing | 2307 | 2307 | 2305 | 1028 | 3703
Philadelphia | Institutional / Public Service | Philadelphia Institutional / Public Service | N/A | N/A | N/A | N/A | 5004
Philadelphia | Lodging | Philadelphia Lodging | 7516 | 7514 | 7181 | 6077 | 8452
Philadelphia | Office | Philadelphia Office | 2484 | 2484 | 2473 | 2690 | 3920
Philadelphia | Restaurant | Philadelphia Restaurant | N/A | N/A | N/A | N/A | 6007
Philadelphia | Retail | Philadelphia Retail | 3935 | 3936 | 3886 | 2398 | 4913
Philadelphia | Warehouse - Other | Philadelphia Warehouse - Other | N/A | N/A | N/A | N/A | 4987
Philadelphia | Warehouse - Refrigerated | Philadelphia Warehouse - Refrigerated | N/A | N/A | N/A | N/A | 3899
Pittsburgh | Education - College / University | Pittsburgh Education - College / University | 4621 | 4619 | 4424 | 4572 | 5646
Pittsburgh | Education - Other | Pittsburgh Education - Other | 3158 | 3168 | 2843 | 3705 | 4167
Pittsburgh | Grocery | Pittsburgh Grocery | N/A | N/A | N/A | N/A | 6340
Pittsburgh | Health - Hospital | Pittsburgh Health - Hospital | 6600 | 6597 | 4830 | 8760 | 8268
Pittsburgh | Health - Other | Pittsburgh Health - Other | 4602 | 4604 | 4214 | 5991 | 8268
Pittsburgh | Industrial Manufacturing | Pittsburgh Industrial Manufacturing | 1895 | 1895 | 1890 | 1287 | 3652
Pittsburgh | Institutional / Public Service | Pittsburgh Institutional / Public Service | N/A | N/A | N/A | N/A | 4909
Pittsburgh | Lodging | Pittsburgh Lodging | 6709 | 6706 | 6182 | 6574 | 8268
Pittsburgh | Office | Pittsburgh Office | 2052 | 2052 | 2041 | 3246 | 4002
Pittsburgh | Restaurant | Pittsburgh Restaurant | N/A | N/A | N/A | N/A | 5946
Pittsburgh | Retail | Pittsburgh Retail | 3298 | 3298 | 3253 | 2908 | 4857
Pittsburgh | Warehouse - Other | Pittsburgh Warehouse - Other | N/A | N/A | N/A | N/A | 4823
Pittsburgh | Warehouse - Refrigerated | Pittsburgh Warehouse - Refrigerated | N/A | N/A | N/A | N/A | 3814
Scranton | Education - College / University | Scranton Education - College / University | 5321 | 5320 | 4865 | 4638 | 5513
Scranton | Education - Other | Scranton Education - Other | 3211 | 3215 | 3008 | 3830 | 4212
Scranton | Grocery | Scranton Grocery | N/A | N/A | N/A | N/A | 6309
Scranton | Health - Hospital | Scranton Health - Hospital | 7320 | 7316 | 5161 | 8760 | 8219
Scranton | Health - Other | Scranton Health - Other | 5157 | 5158 | 5125 | 6223 | 8219
Scranton | Industrial Manufacturing | Scranton Industrial Manufacturing | 2166 | 2166 | 2166 | 1393 | 3661
Scranton | Institutional / Public Service | Scranton Institutional / Public Service | N/A | N/A | N/A | N/A | 4885
Scranton | Lodging | Scranton Lodging | 7860 | 7856 | 7441 | 6628 | 8219
Scranton | Office | Scranton Office | 2277 | 2277 | 2267 | 3336 | 3967
Scranton | Restaurant | Scranton Restaurant | N/A | N/A | N/A | N/A | 5925
Scranton | Retail | Scranton Retail | 3802 | 3803 | 3756 | 2841 | 4831
Scranton | Warehouse - Other | Scranton Warehouse - Other | N/A | N/A | N/A | N/A | 4867
Scranton | Warehouse - Refrigerated | Scranton Warehouse - Refrigerated | N/A | N/A | N/A | N/A | 3791
Williamsport | Education - College / University | Williamsport Education - College / University | 4414 | 4413 | 3977 | 4487 | 5818
Williamsport | Education - Other | Williamsport Education - Other | 2933 | 2969 | 2762 | 3658 | 4313
Williamsport | Grocery | Williamsport Grocery | N/A | N/A | N/A | N/A | 6612
Williamsport | Health - Hospital | Williamsport Health - Hospital | 6416 | 6414 | 4184 | 8760 | 8631
Williamsport | Health - Other | Williamsport Health - Other | 4353 | 4354 | 4243 | 6045 | 8631
Williamsport | Industrial Manufacturing | Williamsport Industrial Manufacturing | 1862 | 1862 | 1860 | 1277 | 3773
Williamsport | Institutional / Public Service | Williamsport Institutional / Public Service | N/A | N/A | N/A | N/A | 5108
Williamsport | Lodging | Williamsport Lodging | 6585 | 6581 | 6074 | 6387 | 8631
Williamsport | Office | Williamsport Office | 1951 | 1951 | 1940 | 3169 | 4078
Williamsport | Restaurant | Williamsport Restaurant | N/A | N/A | N/A | N/A | 6194
Williamsport | Retail | Williamsport Retail | 3304 | 3304 | 3246 | 2660 | 5059
Williamsport | Warehouse - Other | Williamsport Warehouse - Other | N/A | N/A | N/A | N/A | 4954
Williamsport | Warehouse - Refrigerated | Williamsport Warehouse - Refrigerated | N/A | N/A | N/A | N/A | 3982
Default Load Profiles for HVAC Fans and Pumps
[10 empty] | Equipment Type | Flow Fraction (%)
[11 empty] | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
[10 empty] | HVAC Fan | 0 | 0 | 0.01 | 0.05 | 0.16 | 0.22 | 0.25 | 0.19 | 0.09 | 0.03 | 0
[10 empty] | HVAC Pump | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.3 | 0.2 | 0.1 | 0.05 | 0
Supply/Return and Cooling Tower Fan Power Part Load Ratios
[10 empty] | Control Type | Flow Fraction (%) 0: Flow Fraction (%)
[10 empty] | Constant Volume | [11 empty] | 1 | bar: Flow Fraction (%) 0 to Flow Fraction (%) 100
[10 empty] | Two-Speed | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 0.78
[10 empty] | Air Foil/Backward Incline | 0.53 | 0.5256 | 0.53276 | 0.57235 | 0.63599 | 0.71526 | 0.80178 | 0.88713 | 0.96293 | 1.0208 | 1.0522 | 0.77935
[10 empty] | Air Foil/Backward Incline with Inlet Guide Vanes | 0.47262 | 0.52642 | 0.55755 | 0.57439 | 0.58535 | 0.59884 | 0.62324 | 0.66697 | 0.73841 | 0.84597 | 0.99806 | 0.63407
[10 empty] | Outlet Damper Forward Curved | 0.20419 | 0.22262 | 0.25596 | 0.30419 | 0.36732 | 0.44536 | 0.53829 | 0.64612 | 0.76885 | 0.90649 | 1.059 | 0.52825
[10 empty] | Forward Curved with Inlet Guide Vanes | 0.2 | 0.20643 | 0.2157 | 0.2332 | 0.26435 | 0.31454 | 0.38917 | 0.49364 | 0.63334 | 0.81369 | 1.0401 | 0.39781
Table 13: Vlookup Column |  |  | VFD Control Type dropdown |  | VFD Motor Function dropdown |  |  |  |  | Variable Frequency Drive | 0.0475 | 0.0475 | 0.0537 | 0.08 | 0.1289 | 0.2027 | 0.3038 | 0.4346 | 0.5975 | 0.795 | 1.0293 | 0.3059
Type | Number |  | HVAC Fan | HVAC Pump | HVAC Fan Motor Function | HVAC Pump Motor Function
Chilled Water Pump | 2 |  | Constant Volume | Constant Volume | Cooling Tower Fan | Chilled Water Pump |  |  |  | HVAC Pump Power Part Load Ratios
Cooling Tower Fan | 3 |  | Two-Speed | Throttle Valve | Supply Fan | Condenser Water Pump |  |  |  | Control Type | Flow Fraction (%) 0: Flow Fraction (%)
Condenser Water Pump | 4 |  | Air Foil/Backward Incline | Variable Frequency Drive |  | Heating Hot Water Pump |  |  |  | Constant Volume | [11 empty] | 1 | bar: Flow Fraction (%) 0 to Flow Fraction (%) 100
Heating Hot Water Pump | 5 |  | Air Foil/Backward Incline with Inlet Guide Vanes | [6 empty] | Throttle Valve | 0.55212 | 0.61392 | 0.67192 | 0.72612 | 0.77652 | 0.82312 | 0.86592 | 0.90492 | 0.94012 | 0.97152 | 0.99912 | 0.86193
Supply Fan | 6 |  | Outlet Damper Forward Curved | [6 empty] | Variable Frequency Drive | 0.27448 | 0.19124 | 0.14325 | 0.1305 | 0.15298 | 0.21071 | 0.30368 | 0.43188 | 0.59533 | 0.79402 | 1.0279 | 0.34068
Forward Curved with Inlet Guide Vanes
|  |  | Variable Frequency Drive | [6 empty] | Rate Codes
Small Business (GS1 & GS3 Rate Codes)
Large Business (LP4 & LP5 Rate Codes)
Table 15: EFLH Heat | [10 empty] | Flow Fraction (%) 0: Table 16: EFLH Cool
Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport |  | Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Education - College / University | 654 | 984 | 938 | 763 | 442 | 418 | 592 | 733 | 629 |  | Education - College / University | 870 | 436 | 513 | 664 | 729 | 895 | 701 | 741 | 678
Education - Other | 579 | 910 | 886 | 593 | 593 | 581 | 804 | 823 | 629 |  | Education - Other | 363 | 161 | 193 | 257 | 344 | 421 | 322 | 302 | 272
Grocery | 667 | 1068 | 929 | 475 | 1015 | 1095 | 513 | 1546 | 1362 |  | Grocery | 889 | 537 | 753 | 884 | 503 | 654 | 753 | 603 | 504
Health - Hospital | 134 | 81 | 62 | 85 | 289 | 311 | 380 | 94 | 148 |  | Health - Hospital | 1401 | 967 | 1358 | 1443 | 990 | 1292 | 930 | 1421 | 1155
Health - Other | 859 | 1432 | 1418 | 1161 | 683 | 725 | 931 | 1062 | 920 |  | Health - Other | 649 | 393 | 487 | 669 | 599 | 834 | 603 | 649 | 543
Industrial Manufacturing | 369 | 500 | 494 | 421 | 299 | 305 | 364 | 392 | 332 |  | Industrial Manufacturing | 775 | 357 | 430 | 571 | 684 | 832 | 625 | 619 | 545
Institutional / Public Service | 1072 | 1489 | 1496 | 1279 | 878 | 1009 | 1058 | 1247 | 1023 |  | Institutional / Public Service | 1024 | 511 | 632 | 844 | 910 | 1326 | 833 | 874 | 781
Lodging | 2158 | 3219 | 3346 | 2739 | 1727 | 1815 | 2194 | 2306 | 2307 |  | Lodging | 1885 | 1193 | 1507 | 1935 | 1691 | 2113 | 1744 | 1874 | 1578
Multifamily (Common Areas) | 252 | 320 | 308 | 287 | 210 | 233 | 240 | 250 | 267 |  | Multifamily (Common Areas) | 1897 | 647 | 802 | 1069 | 1645 | 2009 | 1388 | 1377 | 1199
Office | 292 | 159 | 458 | 376 | 264 | 253 | 313 | 293 | 326 |  | Office | 623 | 211 | 449 | 573 | 627 | 859 | 851 | 695 | 531
Restaurant | 1047 | 1865 | 1835 | 1501 | 832 | 894 | 1219 | 1336 | 1191 |  | Restaurant | 748 | 425 | 520 | 713 | 655 | 965 | 746 | 726 | 677
Retail | 736 | 1085 | 1062 | 872 | 518 | 569 | 711 | 761 | 648 |  | Retail | 1000 | 530 | 645 | 862 | 824 | 1111 | 963 | 838 | 739
Warehouse - Other | 771 | 1108 | 1094 | 991 | 674 | 810 | 890 | 897 | 768 |  | Warehouse - Other | 237 | 96 | 120 | 158 | 261 | 422 | 227 | 181 | 203
Warehouse - Refrigerated | 330 | 613 | 581 | 475 | 246 | 200 | 372 | 391 | 315 |  | Warehouse - Refrigerated | 4257 | 3018 | 4184 | 4281 | 3511 | 3904 | 3677 | 4301 | 3574
[12 empty] | Table 18: Fan Application |  | Motor Type | Assumed Efficiency
[12 empty] | Heating Only |  | SP | 0.4
[12 empty] | Cooling Only |  | PSC | 0.5
[12 empty] | Ventilation Only |  | ECM | 0.7
Heating & Cooling
Heating & Ventilation
Cooling & Ventilation
Heating & Cooling & Ventilation
Table 18: Pump Application
Heating Circulation
Domestic Hot Water
[10 empty] | Pump Type | Flow Fraction (%) 0: PEIbase
[11 empty] | Constant Speed | Variable Speed
[10 empty] | ESCC, 1800 RPM | Flow Fraction (%) 0: 1; Flow Fraction (%) 10: 0.49
[10 empty] | ESCC, 3600 RPM | Flow Fraction (%) 0: 0.96; Flow Fraction (%) 10: 0.51
[10 empty] | ESFM, 1800 RPM | Flow Fraction (%) 0: 0.98; Flow Fraction (%) 10: 0.49
[10 empty] | ESFM, 3600 RPM | Flow Fraction (%) 0: 0.99; Flow Fraction (%) 10: 0.51
[10 empty] | IL | Flow Fraction (%) 0: 0.99; Flow Fraction (%) 10: 0.5
[10 empty] | RSV | Flow Fraction (%) 0: 0.98; Flow Fraction (%) 10: 0.5
[10 empty] | ST | Flow Fraction (%) 0: 0.96; Flow Fraction (%) 10: 0.6

## Data Export (hidden)
| Description_Product_Style__c | Quantity__c | Incentive_Amount_Custom__c |  | Total_Incentive_New__c | Make__c | Model__c |  | Compressor_Control_Type__c | Efficient_Motor_Horsepower_hp_number__c | Motor_Type__c | Efficient_Motor_Efficiency__c | Average_Annual_Hours_of_Use__c |  | HVAC_Fan_Pump_Control_Type__c | Average_Demand_Savings_kW__c | Annual_Electric_Energy_Savings_kwh__c |  |  | Building_Type__c |  | Baseline_Wattage__c | Efficient_Wattage__c | Summer_Coincident_Peak_Demand_Savings_kW__c | Child___WC_Peak_Demand_Savings_kW__c | Date_Installed__c | Incentive_Unit__c | Child___ETDF_Summer__c | Child___ETDF_Winter__c | Housing_Type__c | Baseline_Motor_Load_Factor__c | Type__c | Installation_Type__c | Equipment_Type__c
Measure Type | Measure Code | Quantity | Per Unit Incentive | Non PPL Incentive Amount Received | Total PPL Incentive | Manufacturer | Model # | Nozzle Size | Compressor Control Type | Motor Rated Horsepower (HP) | Motor Type | ηmotor | Annual Run Hours of Motor (RHRS) | PSIG - Orifice Diameter | HVAC Fan/Pump Control Type | Total kW Savings | Total kWh savings | Facility schedule | Pressure | Space Type | Pump Type | Baseline Watts | Energy Efficient Watts | Total Summer kW Savings | Total Winter kW Savings | Date Installed | Per Unit Incentive | ETDFsummer | ETDFwinter | Housing Type | Load Factor | Type | Installation Type | Equipment Type

## Version Log (hidden)
Version Log
Original Author: |  | Tom Cosgro | QA/QC Engineer(s):
Primary Developer: |  | Jeremy Selwyn | Senior Engineer Approval: |  | Current Version: | 4.12
[5 empty] | Date Updated: | 2026-08-25
Version | Date | Reason for Change | Change Description | Contact, Department
1 | 2016-04-20 | Document created | Adapted the TRM Motor & Drives tool for use in the PPL Program | Jeremy Selwyn, Engineering
1.1 | 2017-01-16 | Unprotect input fields | ECM Circ Fan and VSD Kitchen have protected user inputs | Jeannie Sikora, Engineering
2 | 2017-03-28 | TRM Errata | Correction to Energy Interactive Factor within kWh equation, Change to HP option set and wattage lookup values | Mary Clayton, Core Engineering
3 | 2018-07-16 | Update format | Update format of calculator to match other PPL Calculator | Ryan Novosedliak, Engineering
3 | 2018-11-30 | PPl branding |  | Tom Cosgro
4 | 2021-06-01 | Phase IV Update | Update to 2021 TRM for Phase IV | Michael Stevenson
4.1 | 2021-12-28 | Incentives | 2022 incentive update | Tom Cosgro, Engineering
4.2 | 2022-04-12 | Bug fix | Fixed dropdowns and formulas on VFDs tab | Conor McGrail, Engineering
4.3 | 2023-01-11 | Bug fix | Adjusted Fan/Pump Power Part Load Ratio tables to show full value without rounding to match EEMIS/Appendix D | Conor McGrail, Engineering
4.4 | 2023-05-19 | Update to PY15 Incentive rate | Adjusted PY15 incentive rate from .075 cents and $215 to $0.05 per kWh and $0 for kW. | Garrett Broussard, Engineering
4.4.1 | 2023-08-25 | Update for PY15 and QC | Updated calculation issues on Premium Eff Motor, VFDs, and High Efficiency Pumps tabs. Corrected formulas in dropdowns | Avery Taylor, Engineering
4.5 | 2023-10-06 | Zip code lookup | Added zip code lookup to Project Summary tab, changed all mentions of Williamsburg to Williamsport | Conor McGrail, Engineering
4.6 | 2024-01-04 | Bug fix | Savings was not calculating on VFD tab due to drop down issues. Updated dropdowns. | Meredith Dunn, Engineering
4.7 | 2024-08-01 | EFLH for Supply fans | Adding uniques building type selction for supply fans based on TRM | Nick Momenee, Engineering
4.8 | 2025-02-04 | Removed Const Vol / Bug Fix | Removed constant volume control type in VFDs tab. Adjusted building type options for Premium Eff Motor. | Younes Ben, Engineering
4.9 | 2025-03-01 | LCI Bonus Incentive | Added rate code selection on summary tab and corresponding PY16 LCI incentive rates of $0.10/kWh for prescriptive. SCI Customers get regular incentive rates. | Nick Momenee, Engineering
4.11 | 2025-04-02 | Zipcode Lookup Rename | Binghamton, NY zipcode lookup renamed to Binghamton to match EFLH tables | Nick Momenee, Engineering
4.12 | 2025-08-14 | Incentive Update | Updated incentives for small business class as $0.10/kWh. | Nick Momenee /Wafa, Engineering
Experimental | 2026-03-19 | Phase V Update | Updated to phase 5 TRM / Incentive rate | Michael Farber
5 | 2026-05-14 | Phase V Update, Bug Fix | Updated error in VSD Kitchen Fan which was dividing the Unit ID by 2 for the Horsepower field. Added IFERROR to High Efficiency Pumps / ECM Fan kW savings | Dan Augustine
5.01 | 2026-08-25 | Lookup Table bug fixes/ Updated Zipcode lookups | Adjusted partial load ratios table on lookup tab to match Appendix D tool standard. Also added Appendix D tabs to calculator Updated ZCTA zipcode lookups table | Michael Farber/Nick Momenee

## Utility Admin (hidden)
The workbook is currenlty configured for: |  |  | PPL | PPL Electric
Incentive Manager |  |  |  |  | Workbook Headers (Named Range 'Logo') | Report Logos (Named Range 'Report Logo')
Utility | $/kWh | $/kW |  |  | PPL Logo | PPL Logo
PPL | 0.1 | 0 | PPL Electric
PECO | 0.1 | 0 | PECO
FirstEnergy | 0.04 | 250 | FirstEnergy Pennsylvania
[5 empty] | PECO Logo | PECO Logo
[5 empty] | First Energy Logo | First Energy Logo

## Supply Fans (hidden)
Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Education - College / University | CF | 0.43 | 0.3 | 0.24 | 0.32 | 0.44 | 0.47 | 0.42 | 0.38 | 0.44 | Education - College / University | Run Hours | 6042 | 6054 | 6126 | 6139 | 5860 | 5966 | 5982 | 5876 | 5905 | Education - College / University | CF | 0.43 | 0.3 | 0.24 | 0.32 | 0.44 | 0.47 | 0.42 | 0.38 | 0.44
Education - College / University | Run Hours | 6042 | 6054 | 6126 | 6139 | 5860 | 5966 | 5982 | 5876 | 5905 | Education - Other | Run Hours | 4380 | 4583 | 4718 | 4572 | 4313 | 4384 | 4415 | 4490 | 4377 | Education - Other | CF | 0.12 | 0.08 | 0.07 | 0.09 | 0.17 | 0.18 | 0.18 | 0.12 | 0.15
Education - Other | CF | 0.12 | 0.08 | 0.07 | 0.09 | 0.17 | 0.18 | 0.18 | 0.12 | 0.15 | Grocery | Run Hours | 6708 | 6764 | 6810 | 6738 | 6692 | 6669 | 6718 | 6725 | 6710 | Grocery | CF | 0.24 | 0.21 | 0.19 | 0.22 | 0.24 | 0.26 | 0.29 | 0.21 | 0.24
Education - Other | Run Hours | 4380 | 4583 | 4718 | 4572 | 4313 | 4384 | 4415 | 4490 | 4377 | Health - Hospital | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health - Hospital | CF | 0.43 | 0.24 | 0.29 | 0.39 | 0.45 | 0.51 | 0.45 | 0.4 | 0.41
Grocery | CF | 0.24 | 0.21 | 0.19 | 0.22 | 0.24 | 0.26 | 0.29 | 0.21 | 0.24 | Health - Other | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health - Other | CF | 0.24 | 0.21 | 0.17 | 0.23 | 0.29 | 0.31 | 0.29 | 0.25 | 0.28
Grocery | Run Hours | 6708 | 6764 | 6810 | 6738 | 6692 | 6669 | 6718 | 6725 | 6710 | Industrial Manufacturing | Run Hours | 3831 | 3981 | 4080 | 3977 | 3769 | 3838 | 3869 | 3902 | 3829 | Industrial Manufacturing | CF | 0.48 | 0.34 | 0.28 | 0.38 | 0.53 | 0.57 | 0.5 | 0.43 | 0.46
Health - Hospital | CF | 0.43 | 0.24 | 0.29 | 0.39 | 0.45 | 0.51 | 0.45 | 0.4 | 0.41 | Institutional / Public Service | Run Hours | 5188 | 5223 | 5248 | 5217 | 5172 | 5186 | 5201 | 5207 | 5184 | Institutional / Public Service | CF | 0.53 | 0.38 | 0.34 | 0.45 | 0.6 | 0.72 | 0.56 | 0.47 | 0.52
Health - Hospital | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Lodging | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Lodging | CF | 0.64 | 0.64 | 0.6 | 0.65 | 0.71 | 0.71 | 0.73 | 0.65 | 0.71
Health - Other | CF | 0.24 | 0.21 | 0.17 | 0.23 | 0.29 | 0.31 | 0.29 | 0.25 | 0.28 | Office | Run Hours | 4195 | 4473 | 4699 | 4441 | 4087 | 4063 | 4240 | 4228 | 4139 | Office | CF | 0.3 | 0.26 | 0.21 | 0.28 | 0.37 | 0.39 | 0.35 | 0.32 | 0.34
Health - Other | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Restaurant | Run Hours | 6282 | 2680 | 6487 | 6365 | 6252 | 6226 | 6300 | 6315 | 6286 | Restaurant | CF | 0.38 | 0.19 | 0.28 | 0.37 | 0.42 | 0.5 | 0.49 | 0.39 | 0.45
Industrial Manufacturing | CF | 0.48 | 0.34 | 0.28 | 0.38 | 0.53 | 0.57 | 0.5 | 0.43 | 0.46 | Retail | Run Hours | 5137 | 5188 | 5234 | 5158 | 5108 | 5092 | 5146 | 5149 | 5134 | Retail | CF | 0.5 | 0.4 | 0.36 | 0.44 | 0.53 | 0.56 | 0.54 | 0.45 | 0.49
Industrial Manufacturing | Run Hours | 3831 | 3981 | 4080 | 3977 | 3769 | 3838 | 3869 | 3902 | 3829 | Warehouse - Other | Run Hours | 5037 | 5189 | 5259 | 5222 | 4980 | 5168 | 5110 | 5188 | 5028 | Warehouse - Other | CF | 0.18 | 0.11 | 0.1 | 0.13 | 0.24 | 0.3 | 0.23 | 0.15 | 0.2
Institutional / Public Service | CF | 0.53 | 0.38 | 0.34 | 0.45 | 0.6 | 0.72 | 0.56 | 0.47 | 0.52 | Warehouse - Refrigerated | Run Hours | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | Warehouse - Refrigerated | CF | 0.5 | 0.46 | 0.43 | 0.48 | 0.52 | 0.53 | 0.51 | 0.48 | 0.51
Institutional / Public Service | Run Hours | 5188 | 5223 | 5248 | 5217 | 5172 | 5186 | 5201 | 5207 | 5184
Lodging | CF | 0.64 | 0.64 | 0.6 | 0.65 | 0.71 | 0.71 | 0.73 | 0.65 | 0.71
Lodging | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
Office | CF | 0.3 | 0.26 | 0.21 | 0.28 | 0.37 | 0.39 | 0.35 | 0.32 | 0.34
Office | Run Hours | 4195 | 4473 | 4699 | 4441 | 4087 | 4063 | 4240 | 4228 | 4139
Restaurant | CF | 0.38 | 0.19 | 0.28 | 0.37 | 0.42 | 0.5 | 0.49 | 0.39 | 0.45
Restaurant | Run Hours | 6282 | 2680 | 6487 | 6365 | 6252 | 6226 | 6300 | 6315 | 6286
Retail | CF | 0.5 | 0.4 | 0.36 | 0.44 | 0.53 | 0.56 | 0.54 | 0.45 | 0.49
Retail | Run Hours | 5137 | 5188 | 5234 | 5158 | 5108 | 5092 | 5146 | 5149 | 5134
Warehouse - Other | CF | 0.18 | 0.11 | 0.1 | 0.13 | 0.24 | 0.3 | 0.23 | 0.15 | 0.2
Warehouse - Other | Run Hours | 5037 | 5189 | 5259 | 5222 | 4980 | 5168 | 5110 | 5188 | 5028
Warehouse - Refrigerated | CF | 0.5 | 0.46 | 0.43 | 0.48 | 0.52 | 0.53 | 0.51 | 0.48 | 0.51
Warehouse - Refrigerated | Run Hours | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041

## Chilled Water Pumps (hidden)
Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Education – College / University | CF | 0.41 | 0.27 | 0.23 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.4 | Education - College / University | Run Hours | 4007 | 3436 | 3096 | 3641 | 4057 | 4311 | 3916 | 3828 | 3872 | Education - College / University | CF | 0.41 | 0.27 | 0.23 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.4
Education – College / University | Run Hours | 4007 | 3436 | 3096 | 3641 | 4057 | 4311 | 3916 | 3828 | 3872 | Education - Other | Run Hours | 2721 | 1849 | 1631 | 2175 | 2730 | 3505 | 2676 | 2310 | 2573 | Education - Other | CF | 0.1 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.16
Education - Other | CF | 0.1 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.16 | Health - Hospital | Run Hours | 5588 | 4801 | 4167 | 5109 | 5717 | 6086 | 5593 | 5266 | 5628 | Health - Hospital | CF | 0.46 | 0.38 | 0.31 | 0.42 | 0.5 | 0.54 | 0.48 | 0.44 | 0.47
Education - Other | Run Hours | 2721 | 1849 | 1631 | 2175 | 2730 | 3505 | 2676 | 2310 | 2573 | Health - Other | Run Hours | 3892 | 3093 | 2592 | 3456 | 4104 | 4535 | 3900 | 3710 | 3818 | Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26
Health - Hospital | CF | 0.46 | 0.38 | 0.31 | 0.42 | 0.5 | 0.54 | 0.48 | 0.44 | 0.47 | Industrial Manufacturing | Run Hours | 1735 | 1306 | 1086 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633 | Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.53 | 0.58 | 0.54 | 0.48 | 0.5
Health - Hospital | Run Hours | 5588 | 4801 | 4167 | 5109 | 5717 | 6086 | 5593 | 5266 | 5628 | Lodging | Run Hours | 5845 | 5042 | 4444 | 5198 | 6045 | 6161 | 5686 | 5655 | 5776 | Lodging | CF | 0.61 | 0.58 | 0.53 | 0.6 | 0.66 | 0.67 | 0.69 | 0.59 | 0.66
Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26 | Office | Run Hours | 1789 | 1402 | 1189 | 1585 | 1804 | 2036 | 1739 | 1638 | 1711 | Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Health - Other | Run Hours | 3892 | 3093 | 2592 | 3456 | 4104 | 4535 | 3900 | 3710 | 3818 | Retail | Run Hours | 2957 | 2416 | 2012 | 2653 | 3085 | 3225 | 2795 | 2735 | 2898 | Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.53 | 0.58 | 0.54 | 0.48 | 0.5
Industrial Manufacturing | Run Hours | 1735 | 1306 | 1086 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633
Lodging | CF | 0.61 | 0.58 | 0.53 | 0.6 | 0.66 | 0.67 | 0.69 | 0.59 | 0.66
Lodging | Run Hours | 5845 | 5042 | 4444 | 5198 | 6045 | 6161 | 5686 | 5655 | 5776
Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Office | Run Hours | 1789 | 1402 | 1189 | 1585 | 1804 | 2036 | 1739 | 1638 | 1711
Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Retail | Run Hours | 2957 | 2416 | 2012 | 2653 | 3085 | 3225 | 2795 | 2735 | 2898

## Cooling Tower Fan (hidden)
Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Education – College / University | CF | 0.41 | 0.26 | 0.23 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.39 | Education - College / University | Run Hours | 4006 | 3435 | 3096 | 3641 | 4057 | 4309 | 3914 | 3827 | 3871 | Education - College / University | CF | 0.41 | 0.26 | 0.23 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.39
Education – College / University | Run Hours | 4006 | 3435 | 3096 | 3641 | 4057 | 4309 | 3914 | 3827 | 3871 | Education - Other | Run Hours | 2742 | 1851 | 1634 | 2178 | 2744 | 3517 | 2685 | 2313 | 2604 | Education - Other | CF | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17
Education - Other | CF | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17 | Health - Hospital | Run Hours | 5587 | 4798 | 4165 | 5107 | 5714 | 6084 | 5591 | 5263 | 5626 | Health - Hospital | CF | 0.45 | 0.37 | 0.31 | 0.41 | 0.49 | 0.54 | 0.47 | 0.44 | 0.46
Education - Other | Run Hours | 2742 | 1851 | 1634 | 2178 | 2744 | 3517 | 2685 | 2313 | 2604 | Health - Other | Run Hours | 3894 | 3093 | 2593 | 3457 | 4106 | 4537 | 3902 | 3711 | 3819 | Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26
Health - Hospital | CF | 0.45 | 0.37 | 0.31 | 0.41 | 0.49 | 0.54 | 0.47 | 0.44 | 0.46 | Industrial Manufacturing | Run Hours | 1735 | 1306 | 1086 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633 | Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.54 | 0.59 | 0.54 | 0.48 | 0.5
Health - Hospital | Run Hours | 5587 | 4798 | 4165 | 5107 | 5714 | 6084 | 5591 | 5263 | 5626 | Lodging | Run Hours | 5844 | 5039 | 4442 | 5197 | 6043 | 6159 | 5683 | 5652 | 5773 | Lodging | CF | 0.61 | 0.58 | 0.53 | 0.61 | 0.67 | 0.68 | 0.7 | 0.59 | 0.66
Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26 | Office | Run Hours | 1789 | 1402 | 1189 | 1585 | 1804 | 2036 | 1739 | 1638 | 1711 | Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Health - Other | Run Hours | 3894 | 3093 | 2593 | 3457 | 4106 | 4537 | 3902 | 3711 | 3819 | Retail | Run Hours | 2957 | 2416 | 2012 | 2653 | 3085 | 3226 | 2795 | 2736 | 2898 | Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.54 | 0.59 | 0.54 | 0.48 | 0.5
Industrial Manufacturing | Run Hours | 1735 | 1306 | 1086 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633
Lodging | CF | 0.61 | 0.58 | 0.53 | 0.61 | 0.67 | 0.68 | 0.7 | 0.59 | 0.66
Lodging | Run Hours | 5844 | 5039 | 4442 | 5197 | 6043 | 6159 | 5683 | 5652 | 5773
Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Office | Run Hours | 1789 | 1402 | 1189 | 1585 | 1804 | 2036 | 1739 | 1638 | 1711
Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Retail | Run Hours | 2957 | 2416 | 2012 | 2653 | 3085 | 3226 | 2795 | 2736 | 2898

## Heating Hot Water Pumps (hidden)
Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Education – College / University | CF | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0.01 | 0.01 | 0.01 | Education - College / University | Run Hours | 4548 | 5271 | 5900 | 5036 | 4250 | 4014 | 4572 | 4638 | 4487 | Education - College / University | CF | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0.01 | 0.01 | 0.01
Education – College / University | Run Hours | 4548 | 5271 | 5900 | 5036 | 4250 | 4014 | 4572 | 4638 | 4487 | Education - Other | Run Hours | 3651 | 4251 | 4722 | 4080 | 3492 | 3341 | 3705 | 3830 | 3658 | Education - Other | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Education - Other | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Health - Hospital | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health - Hospital | CF | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
Education - Other | Run Hours | 3651 | 4251 | 4722 | 4080 | 3492 | 3341 | 3705 | 3830 | 3658 | Health - Other | Run Hours | 5934 | 6627 | 7170 | 6280 | 5823 | 5477 | 5991 | 6223 | 6045 | Health - Other | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health - Hospital | CF | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | Industrial Manufacturing | Run Hours | 1258 | 1684 | 1944 | 1555 | 1184 | 1028 | 1287 | 1393 | 1277 | Industrial Manufacturing | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health - Hospital | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Lodging | Run Hours | 6469 | 7072 | 7587 | 6829 | 6155 | 6077 | 6574 | 6628 | 6387 | Lodging | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health - Other | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Office | Run Hours | 3214 | 3876 | 4446 | 3611 | 3014 | 2690 | 3246 | 3336 | 3169 | Office | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health - Other | Run Hours | 5934 | 6627 | 7170 | 6280 | 5823 | 5477 | 5991 | 6223 | 6045 | Retail | Run Hours | 2676 | 3183 | 3568 | 2960 | 2561 | 2398 | 2908 | 2841 | 2660 | Retail | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Industrial Manufacturing | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Industrial Manufacturing | Run Hours | 1258 | 1684 | 1944 | 1555 | 1184 | 1028 | 1287 | 1393 | 1277
Lodging | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lodging | Run Hours | 6469 | 7072 | 7587 | 6829 | 6155 | 6077 | 6574 | 6628 | 6387
Office | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office | Run Hours | 3214 | 3876 | 4446 | 3611 | 3014 | 2690 | 3246 | 3336 | 3169
Retail | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail | Run Hours | 2676 | 3183 | 3568 | 2960 | 2561 | 2398 | 2908 | 2841 | 2660

## Condenser Water Pumps (hidden)
Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Education - College / University | CF | 0.41 | 0.26 | 0.2 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.39 | Education - College / University | Run Hours | 3527 | 2938 | 2466 | 3063 | 3602 | 4030 | 3749 | 3500 | 3489 | Education - College / University | CF | 0.41 | 0.26 | 0.2 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.39
Education - College / University | Run Hours | 3527 | 2938 | 2466 | 3063 | 3602 | 4030 | 3749 | 3500 | 3489 | Education - Other | Run Hours | 2448 | 1733 | 1529 | 2039 | 2539 | 3346 | 2409 | 2164 | 2423 | Education - Other | CF | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17
Education - Other | CF | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17 | Health - Hospital | Run Hours | 3950 | 3546 | 3293 | 3698 | 3687 | 4168 | 4093 | 3713 | 3670 | Health - Hospital | CF | 0.45 | 0.37 | 0.29 | 0.41 | 0.49 | 0.54 | 0.47 | 0.44 | 0.46
Education - Other | Run Hours | 2448 | 1733 | 1529 | 2039 | 2539 | 3346 | 2409 | 2164 | 2423 | Health - Other | Run Hours | 3675 | 3100 | 2585 | 3394 | 3725 | 4304 | 3571 | 3687 | 3722 | Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26
Health - Hospital | CF | 0.45 | 0.37 | 0.29 | 0.41 | 0.49 | 0.54 | 0.47 | 0.44 | 0.46 | Industrial Manufacturing | Run Hours | 1735 | 1305 | 1084 | 1445 | 1737 | 1889 | 1602 | 1558 | 1632 | Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.54 | 0.59 | 0.54 | 0.48 | 0.5
Health - Hospital | Run Hours | 3950 | 3546 | 3293 | 3698 | 3687 | 4168 | 4093 | 3713 | 3670 | Lodging | Run Hours | 5544 | 4591 | 3939 | 4766 | 5569 | 5886 | 5239 | 5353 | 5328 | Lodging | CF | 0.61 | 0.58 | 0.53 | 0.61 | 0.67 | 0.68 | 0.7 | 0.59 | 0.66
Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26 | Office | Run Hours | 1781 | 1389 | 1177 | 1569 | 1792 | 2027 | 1730 | 1631 | 1702 | Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Health - Other | Run Hours | 3675 | 3100 | 2585 | 3394 | 3725 | 4304 | 3571 | 3687 | 3722 | Retail | Run Hours | 2889 | 2381 | 1986 | 2616 | 3025 | 3185 | 2757 | 2702 | 2847 | Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.54 | 0.59 | 0.54 | 0.48 | 0.5
Industrial Manufacturing | Run Hours | 1735 | 1305 | 1084 | 1445 | 1737 | 1889 | 1602 | 1558 | 1632
Lodging | CF | 0.61 | 0.58 | 0.53 | 0.61 | 0.67 | 0.68 | 0.7 | 0.59 | 0.66
Lodging | Run Hours | 5544 | 4591 | 3939 | 4766 | 5569 | 5886 | 5239 | 5353 | 5328
Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Office | Run Hours | 1781 | 1389 | 1177 | 1569 | 1792 | 2027 | 1730 | 1631 | 1702
Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Retail | Run Hours | 2889 | 2381 | 1986 | 2616 | 3025 | 3185 | 2757 | 2702 | 2847