## Instructions (hidden)
CLEAResult Calculator
Description, purpose, and limitations of the calculator. Contact for questions and updates.
Input Instructions
Yellow cells indicate that user input is required. Cells with a * are required.
Grey cells are calculated values.
Worksheet Summary
Methodology
Summary of Methdology Worksheet
Calculator
Summary of required inputs and outputs of the Calculator
Calculations
Summary of Calculations Worksheet
Version Log
The Version Log Worksheet tracks updates and changes made to the workbook.
Glossary of Inputs
Input 1 [units] | Description of input
Input 2 [units] | Description of input
Input 3 [units] | Description of input
Input 4 [units] | Description of input
Input 5 [units] | Description of input
Glossary of Outputs
Output 1 [units] | Description of output | kWh
Output 2 [units] | Description of output | $/year
Output 3 [units] | Description of output | kWh

## Instructions
PPL Calculator for HVAC Measures
Measure Description
This calculator will be used to calculate energy and demand savings for the following HVAC and Building Shell measures -
| 1. HVAC Systems: |  | Replacement of Air Cooled, Water Cooled or Evaporatively Cooled ACs, Split and Packaged Terminal Air Conditioners or Heat Pumps, and Air-Source Heat Pumps with higher efficiency units that exceed requirements of 2015 IECC.
| 2. Electric Chillers: |  | Replacement of Air-Cooled and Water-Cooled Chillers with higher efficiency chillers that exceed requirements of 2015 IECC.
| 3. Water-Source or Geothermal Heat Pumps: |  | Installation of Water Source (<65,000 BTU/hr) or Geothermal Heat Pumps (<135,000 BTU/hr), that exceed the efficiency of similarly sized Air Source Heat Pumps (New Construction) or existing Water-Source/Geothermal Heat Pumps.
| 4. Ductless Mini-Split Heat Pumps <5.4 tons: |  | Replacing existing electric resistance, lower efficiency Ductless Heat Pumps, PTHP, PTACs, Central Air conditioning with Ductless Mini-Split Heat Pumps meeting ENERGY STAR Requirements
| 5. Fuel Switching: |  | Replacing Electric Baseboard, electric furnace, PTHPs, or ASHPs <225,000 BTU/hr with Oil Furnace, Gas Furnace or Boiler that meets ENERGY STAR requirements
| 6. Refrigerant Charge Correction: |  | Savings from correcting refrigerant charge for Commercial and Industrial Air Conditioning units or Heat Pumps (< 20 tons capacity)
| 7. Room Air Conditioners: |  | Replacing lower efficiency Room Air Conditioners with higher efficiency units that meet ENERGY STAR Requirements
| 8. Guest Room Occupancy Controls: |  | This measure applies to the installation of control systems in hotel or motel guest rooms which automatically adjust heating/cooling temperature set-points and turn off equipment when guest rooms are unoccupied.
| 9. Air Side Economizers: |  | Savings from installation of dual enthalpy economizers on HVAC systems without an economizer control.
| 10. Ceiling and Wall Insulation: |  | Installation of higher efficiency ceiling and wall insulation.
The Savings methodologies, constants, default inputs and eligibility requirements for all measures are from Pennsylvania Public Utility Commission, Technical Reference Manual, February 2021 Revision.
Input Instructions
1. | Use the color coded reference cells. Only yellow cells need input.
Requires Input
Doesn't need an Input
Output Cell
2. | Use the Minimum Efficiency Requirements sheet to ensure the installed equipment efficiency exceeds program requirements.
3. | Default values for some constants are provided in dropdown lists in case the actual values cannot be collected.
4. | Refer to the PA TRM 2021 for detailed information on calculations or inputs.
|  |  | Equipment ID | Name of the unit for identification purposes
|  |  | Project Type | End of Useful Life or New Construction, Retrofit or Early Replacement
|  |  | Project Cost | Total of material and labor cost
|  |  | Standard/Non Standard Size | For PTACs and PTHPs: Non-Standard size units are generally for early replacements and are labeled as "Manufactured for nonstandard size applications only: not to be installed in new construction projects". Nonstandard size units have have an external wall opening of less than 16 in. high or less than 42 in. wide and having a cross-sectional area less than 670 in. Standard size units are generally for New Construction projects, and are for standard size wall openings.
|  |  | Rated Cooling Capacity (BTU/hr) | BTUcool/hr, Rated cooling capacity of the energy efficient unit
|  |  | Rated Heating Capacity (BTU/hr) | Rated heating capacity of the energy efficient unit
|  |  | Does the Unit have Electric Resistance Heating? | Yes/No check to see if units have Electric Resistance heat. Baseline efficiency values may change based on this inputs.
|  |  | IEER | Integrated energy efficiency ratio of the baseline or efficient unit. For ASHPs and Air cooled Air conditioners > 65,000BTU/hr, and Water cooled and Evaporatively Cooled Air Condtioners
|  |  | EER | Energy efficiency ratio of the baseline or efficient unit. For ASHPs and Air cooled Air conditioners < 65,000BTU/hr, this is calculated as 11.3/13* SEER
|  |  | SEER | Seasonal energy efficiency ratio of the baseline or efficient unit, for ASHPs and Air cooled Air conditioners < 65,000BTU/hr.
|  |  | COP | Coefficient of Performance of the baseline or efficient unit, for ASHPs > 65,000 BTU/hr, PTHPs, and geothermal or water source heat pumps
|  |  | HSPF | Heating seasonal performance factor of the baseline or efficient unit, for ASHPs < 65,000 BTU/hr
|  |  | CEER | Combined energy efficiency ratio for Room Air Conditioners
|  |  | IPLV | Integrated Part Load Value for baseline or efficient unit
|  |  | Full Load kW/ton | Design Rated Efficiency for baseline or efficient unit
|  |  | Remaining Useful Life (in years) | For Early Replacement projects - based on nameplate age of the unit.
|  |  | Motor Size (HP) | Horsepower of retrofit case ground loop pump motor
|  |  | Motor Efficiency | Efficiency of ground loop pump motor
|  |  | Pump Efficiency | Efficiency of ground loop pump at design point
|  |  | % Refrigerant Charge Corrected | % of total refrigerant charge added or removed from the AC unit
|  |  | Expansion Valve | Type of Expansion Valve on AC unit - Thermal Expansion (TXV) or Fixed Orifice
|  |  | AFUE | Annual Fuel Utilization Efficiency rating of the fossil fuel unit (oil or gas furnace, boiler)
|  |  | Blower Motor HP | Horsepower of fossil fuel equipment blower motor
|  |  | Blower Motor Efficiency (%) | Efficiency of fossil fuel equipment blower motor
|  |  | Area Served (sq.ft.) | Area of conditioned space served by controlled unit (for economizers)
|  |  | R-Value | R-value of wall or ceiling
|  |  | Existing Annual kWh Consumption | Calculated Baseline Annual Energy Consumption of the Equipment
|  |  | Existing Annual Peak kW | Calculated Baseline Peak Demand of the Equipment
|  |  | Proposed Annual kWh Consumption | Calculated Proposed Annual Energy Consumption of the Equipment
|  |  | Proposed Annual Peak kW | Calculated Proposed Peak Demand of the Equipment
|  |  | Annual kWh Savings | Calculated Annual Energy Savings from the measure
|  |  | Annual kWh Savings (%) | Calculated Annual Energy Savings from the measure as a percent of existing consumption
|  |  | Peak kW Savings | Calculated Annual Peak Demand Reduction from the measure
|  |  | Peak kW Savings (%) | Calculated Annual Peak Demand Reduction from the measure as a percent of existing peak demand
|  |  | Incremental Measure Cost | Difference between baseline and proposed costs
|  |  | Electric Cost Savings | Annual Electric cost Savings from implementing the measure
|  |  | Incentive | Calculated Incentive for PPL rates
Note: This calculator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this calculator is deemed acceptable for the PPL Electric Utilities Non-Residential Energy Efficiency Program. However, the assumptions used by the applicant to calculate the annual savings will be reviewed by the Program Team, which is solely responsible for the final determination of the annual energy savings to be used in calculating the incentive amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities. For any questions, or assistance using this calculator, please call 1-866-432-5501 or email us at pplbusiness@clearesult.com.

## Methodology (hidden)
Savings Methodologies
HVAC Systems | Ductless Mini-Splits | Nomenclature
Eligibility: New equipment must exceed the efficiency requirements of IECC 2009 and serve comfort cooling purposes only. For one to one replacement of Air Conditioning (includes central AC, air-cooled/water-cooled/evaporatively cooled DX, split systems, and packaged terminal AC) and Air Source and Packaged Terminal Heat Pump Systems. Savings Methodology: | Eligibility: For installation of ENERGY STAR ductless mini split heat pumps replacing an existing electric resistance, a lower-efficiency ductless heat pump system, a ducted heat pump, packaged terminal heat pump (PTHP), electric furnace, or a non-electric fuel-based system. The baseline cooling system could be a standard efficiency heat pump system, central air conditioning system, packaged terminal air conditioner (PTAC), or room air conditioner. The DHP could be a new device in an existing space, a new device in a new space, or could replace an existing heating/cooling device. The DHP systems could be installed as a single-zone system (one indoor unit, one outdoor unit) or a multi-zone system (multiple indoor units, one outdoor unit). Comfort Cooling Applications only. Savings Methodology: | Term | Values
|  | BTUcool/hr, Rated cooling capacity of the energy efficient unit | Nameplate data (AHRI or AHAM)
|  | BTUheat/hr, Rated heating capacity of the energy efficient unit | Nameplate data (AHRI or AHAM)
|  | IEERbase, Integrated energy efficiency ratio of the baseline unit. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | IEERee, Integrated energy efficiency ratio of the energy efficient unit. | Nameplate data (AHRI or AHAM)
|  | EERbase, Energy efficiency ratio of the baseline unit. For air-source AC and ASHP units < 65,000 BTU/hr SEER should be used for cooling savings | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | EERee, Energy efficiency ratio of the energy efficient unit. For air-source AC and ASHP units < 65,000 BTU/hr SEER should be used for cooling savings. | Nameplate data (AHRI or AHAM)
|  | SEERbase, Seasonal energy efficiency ratio of the baseline unit. For units > 65,000 BTU/hr , EER should be used for cooling savings. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | SEERee, Seasonal energy efficiency ratio of the energy efficient unit. For units > 65,000 BTU/hr , EER should be used for cooling savings. | Nameplate data (AHRI or AHAM)
|  | COPbase, Coefficient of performance of the baseline unit. For ASHP units < 65,000BTU/hr , HSPF should be used for heating savings. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | COPee, Coefficient of performance of the efficient unit. For ASHP units < 65,000BTU/hr , HSPF should be used for heating savings. | Nameplate data (AHRI or AHAM)
|  | HSPFbase , Heating seasonal performance factor of the baseline unit. For units > 65,000 BTU/hr, COP should be used for heating savings. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | HSPFee, Heating seasonal performance factor of the energy efficiency unit. For units > 65,000 BTU/hr, COP should be used for heating savings. | Nameplate data (AHRI or AHAM)
|  | CF , Demand Coincidence Factor | EDC Data Gathering. Defaults available.
|  | EFLHcool, Equivalent Full Load Hours for the cooling season – The kWh during the entire operating season divided by the kW at design conditions. | EDC Data Gathering. Defaults available.
|  | EFLHheat, Equivalent Full Load Hours for the heating season – The kWh during the entire operating season divided by the kW at design conditions. | EDC Data Gathering. Defaults available.
|  | Tonsee, The capacity of the chiller at site design conditions accepted by the program | Nameplate data (AHRI or AHAM)
|  | kW/tonbase, Design Rated Efficiency of the baseline chiller. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | kW/tonee, Design Rated Efficiency of the energy efficient chiller from the manufacturer data and equipment ratings in accordance with ARI Standards. | Nameplate data (AHRI or AHAM)
C
Chiller Systems | Refrigerant Charge Correction
Eligibility: New equipment must exceed the efficiency requirements of IECC 2009. Equipment can be installed in a new application or can replace equipment which has failed or which is expected to fail imminently. New equipment must be a single chiller serving a single comfort cooling load. All other chiller applications, including chiller plants having multiple chillers or serving multiple loads, and chillers used for process cooling must submitted as custom. Projects must be submitted as custom if equipment is replacing a different equipment type, if equipment being replaced is fully operational, or if an existing chiller is being retrofit with a variable speed drive. Savings Methodology: | Eligibility: This protocol is applicable for small commercial and industrial customers, and applies to documented tune-ups for package or split systems up to 20 tons. Comfort Cooling applications only. Savings Methodology: | IPLVbase, Integrated Part Load Value of the baseline unit. | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | IPLVee, Integrated Part Load Value of the efficient unit. | Nameplate data (AHRI or AHAM)
|  | CFpump, Demand Coincidence Factor for ground source loop pump | If unit runs 24/7/365, CF=1.0; If unit runs only with heat pump unit compressor, defaults available
|  | HPbasemotor, Horsepower of base case ground loop pump motor | Nameplate data
|  | LFbase, Load factor of the base case ground loop pump motor; ratio of the peak running load to the nameplate rating of the pump motor. | Based on spot metering and nameplate. Default = 0.75
|  | , efficiency of base case ground loop pump motor | Nameplate data. If unknown, assume the federal minimum efficiency requirements
|  | , efficiency of base case ground loop pump at design point | Nameplate data. If unknown, assume the federal minimum efficiency requirements
|  | HOURSbasepump, Run hours of base case ground loop pump motor | Based on Logging, BMS data or Modeling. Else EFLHcool + EFLHheat default values
|  | HPeemotor, Horsepower of retrofit case ground loop pump motor | Nameplate data
|  | Lfee , Load factor of the retrofit case ground loop pump motor; Ratio of the peak running load to the nameplate rating of the pump motor. | Based on spot metering and nameplate. Default = 0.75
|  | , efficiency of retrofit case ground loop pump motor | Nameplate data. If unknown, assume the federal minimum efficiency requirements
Insulation |  | , efficiency of retrofit case ground loop pump at design point | Nameplate data. If unknown, assume the federal minimum efficiency requirements
Eligibility: This measure applies to non-residential buildings or common areas in multifamily complexes heated and/or cooled using electricity. Existing construction buildings are required to meet or exceed the code requirement. New construction buildings must exceed the code requirement. Eligibility may vary by PA EDC; savings from chiller-cooled buildings are not included. Savings Methodology: |  | HOURSeepump, Run hours of retrofit case ground loop pump motor | Based on Logging, BMS data or Modeling. Else EFLHcool + EFLHheat default values
|  | CAPYcool, The cooling capacity of the indoor unit, given in Btu/hr as appropriate for the calculation. This protocol is limited to units < 65,000 Btu/hr (5.4 tons) | Nameplate data
|  | CAPYheat, The heating capacity of the indoor unit, given in Btu/hr as appropriate for the calculation. | Nameplate data
|  | HSPFb, Heating Seasonal Performance Factor, heating efficiency of the installed DHP | Varies based on baseline equipment type. Defaults available.
|  | SEERb, Seasonal Energy Efficiency Ratio cooling efficiency of baseline unit | Varies based on baseline equipment type. Defaults available.
|  | HSPFe, Heating Seasonal Performance Factor, heating efficiency of the installed DHP | Nameplate data
|  | SEERe, Seasonal Energy Efficiency Ratio cooling efficiency of the installed DHP | Nameplate data
|  | BTUfuel/hr, Rated heating capacity of the new fossil fuel unit | Nameplate data (AHRI or AHAM)
|  | BTUheat/hr, Rated heating capacity of the existing electric unit | Nameplate data (AHRI or AHAM) - default set to BTUfuel/hr
Ground and Water Source Heat Pumps | ENERGY STAR Room Air Conditioners | AFUEfuel, Annual Fuel Utilization Efficiency rating of the fossil fuel unit | Nameplate data (AHRI or AHAM) - default to ENERGY STAR minimums
Eligibility: New equipment must exceed the efficiency requirements of the IECC 2009. To be eligible, equipment must be of one of the following type and size: • Water source heat pump systems < 65,000 Btu/hr • Ground water source heat pumps < 135,000 Btu/hr • Ground source heat pumps < 135,000 Btu/hr. The new heat pump must be of the same type as the replaced system and must be used for comfort cooling/heating purposes. Heat pump systems coupled with non-heat pump systems such as chillers, rooftop AC units, boilers, or cooling towers must be submitted as custom. Projects must be submitted as custom if equipment is replacing a different equipment type, if equipment is installed in a new application, if equipment being replaced is still operational, or if the heat pump is used for process cooling/heating. Savings Methodology:There are three primary components that must be accounted for in the energy and demand calculations. The first component is the heat pump unit energy and power, the second is the circulating pump in the ground/water loop system energy and power, and the third is the well pump in the ground/water loop system energy and power. For projects where the retrofit system is similar to the baseline system, such as a standard efficiency ground source system replaced with a high efficiency ground source system, the pump energy is expected to be the same for both conditions and does not need to be calculated. The kWh savings should be calculated using the basic equations below. For baseline units rated in both EER and IEER, use IEER in place of EER where listed in energy savings calculations below. | Eligibility: For one to one replacement of standard-efficiency room air conditioners with ENERGY STAR room air conditioners. Comfort cooling applications only. Savings Methodology: | HPmotor, Gas furnace blower motor horsepower | Nameplate data. Default: 1/2HP for furnace
|  | , Efficiency of furnace blower motor | Nameplate data. Default: 0.5 for furnace
|  | RCF, COP Degradation Factor for Cooling | Defaults based on % charge added or removed
|  | CEERbase, EERbase - Efficiency rating of the baseline unit | Early Replacement: Nameplate data New Construction or Replace on Burnout: Default values from ASHRAE 90.1 - 2007
|  | CEERee, EERee - Efficiency rating of the efficient unit | Nameplate data (AHRI or AHAM)
|  | CAPY, Cooling capacity of controlled unit in tons | EDC data gathering
|  | ESF, Energy savings factor | Defaults based on operating hours, location etc.
|  | DSF, Demand savings factor | Defaults based on operating hours, location etc.
|  | SF , Savings factor; Annual cooling load savings per unit area of conditioned space in the building when compared with a baseline HVAC system with no economizer. | 0.002
|  | AREA , Area of conditioned space served by controlled unit | EDC data gathering
|  | FCHr, Free cooling hours with outdoor temperature between 60 F and 70 F. Typical operating hour conditions are defined below with standard climate zones for PA. | Defaults based on location
|  | Eff, Efficiency of existing HVAC equipment. Depending on the size and age, this will either be the SEER, IEER, or EER (use EER only if SEER or IEER are not available) | EDC data gathering. Defaults values from ASHRAE 90.1 - 2007
| Guest Room Occupancy Sensors | HDD, Heating degree days with 65 degree base | Calculated for different PA weather stations in TRM
| Eligibility: For one to one replacement of standard-efficiency room air conditioners with ENERGY STAR room air conditioners. Comfort cooling applications only. Savings Methodology: For hotel and motel guest rooms where manual heating/cooling temperature set-point and fan On/Off/Auto thermostat controls are replaced by energy management thermostats controls of the heating/cooling temperature set-points and operation state based on occupancy modes. | CDD, Cooling degree days with a 65 degree base | Calculated for different PA weather stations in TRM
|  | A_ceiling, Area of the ceiling/attic insulation that was installed | EDC data gathering
|  | A_wall, Area of the wall insulation that was installed | EDC data gathering
|  | Ceiling Ri, the R-value of the ceiling insulation and support structure before the additional insulation is installed | Defaults in TRM for NC buildings, or when existing value is uknown.
|  | Wall Ri, the R-value of the wall insulation and support structure before the additional insulation is installed | Defaults in TRM for NC buildings, or when existing value is uknown.
|  | Ceiling Rf, Total R-value of all ceiling/attic insulation after the additional insulation is installed | EDC data gathering
|  | WallRf, Total R-value of all wall insulation after the additional insulation is installed | EDC data gathering
Economizers
Eligibility: For HVAC equipment with no economizer installed or with a non-functional/disabled economizer. Efficient condition is an HVAC unit with an economizer and dual enthalpy (differential) control. Comfort cooling applications only. Savings Methodology:
Fuel Switching
Eligibility: This protocol excludes water source, ground source, and groundwater source heat pumps. The baseline for this measure is an existing commercial facility with an electric primary heating source. The heating source can be electric baseboards, packaged terminal heat pump (PTHP) units, electric furnace, or electric air source heat pump. The retrofit condition for this measure is the installation of a new standard efficiency natural gas, propane, or oil furnace or boiler. This algorithm does not apply to combination space and water heating units. This protocol applies to measures with input rating of less than 225,000 BTU/hr. Savings Methodology:

## Summary
|  |  |  | Version: | 4
|  |  |  | Last Updated: | 2021-06-01
Date | Measure Name | Equipment Cost | Savings |  | Incentive
Project Name |  |  | kW | kWh
Site Address | HVAC SYSTEMS |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Chiller |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Geothermal |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Ductless Mini Splits |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Fuel Switching |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Ref Charge Correction |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Room AC |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Guest Room Occ Sensor |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Economizer |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Computer Room AC |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Computer Room AC ECM and or VSD |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| High Volume Low Speed Fans |  | Enter Equipment Cost | Enter Equipment Cost | Enter Equipment Cost
| Total | 0 | 0 | 0 | 0

## HVAC Systems (hidden)
Last Updated: [Date], See Version Log
Calculator
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Proposed Unit |  |  | Output 1* | unit
| Date |  |  | Output 2* | unit
| Location* |  |  | Output 3* | unit
Address
| Building Type* | Grocery
Equiment Type
Project Type
Standered/ Non Standard Size
| Rated Cooling Capacity |  | BTU/hr
| Number or Units installed |  | #
| Rated Heating Capacity |  | BTU/hr
| Does the unit have Electric Resistance heating? |  | unit
| Project Cost |  | $
Baseline Unit
| Remaining Useful Life |  | Years
Project Site
Address
| Location* | Allentown
| Building Type* | Grocery
Project Type
| Input 1* | Hotel | unit
| Input 2* |  | unit
| Input 3* |  | unit
| Input 4* |  | unit
| Project Cost |  | $

## Data Export (hidden)
| Line Item | Measure Quantity | Measure Code Measure Description | Incentive | Project End Date | Total Energy Savings (kWh) | Total Energy Savings (kW) | Estimator Version Number | Efficient SEER | Efficient HSPF | Rating Condition | Efficient EER | Efficient IEER | Efficient COP | Cooling Capacity (btu/hr) | Heating Capacity (btu/hr) | Cooling Capacity Tons | Baseline IPLV | Efficient IPLV | Baseline Design Eff. kW/Ton Base | Efficient Design Eff. kW/Ton EE | CofO - Housekeeping Setback | Building Type | Area | Operating Schedule | Existing Heating System | Existing Cooling System | Baseline EER | Baseline IEER | Baseline COP | Baseline HSPF | Baseline SEER | HVAC System Type | Efficient CEER | Baseline CEER | Fuel Switching (Y/N) | Fuel Switching Savings therms | Nameplate Capacity | DSMT Measure Name
HVAC Systems | [38 empty] | 0
0
0
0
0
0
0
0
0
0
Chiller | [31 empty] | 15 |  |  | 0
0
Geothermal
Ductless Mini-Splits
Fuel Switching | [32 empty] | 0
0
0
0
0
0
0
0
0
0
Refrigerant Charge Correction |  |  |  | 0
0
0
0
0
0
0
0
0
0
Room AC |  |  |  | 0
0
0
0
0
0
0
0
0
0
Guest Room Occ
Economizers
Computer Room AC |  |  |  | 0
0
0
0
0
0
0
0
0
0
Computer Room AC ECM or VSD |  |  |  | 0
0
0
0
0
0
0
0
0
0
High Vol Low Speed Fans

## HVAC SYSTEMS
Last Updated: See Version Log
HVAC Systems
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required.See Instructions Worksheet for more information.
Date
Project Site
Address
Nearest Location*
Building Type*
| Project Type* | Proposed Unit | [13 empty] | Financial Summary
|  | Equipment ID | Project Cost* | Equipment Type* | Standard / Non Standard Size* | Rated Cooling Capacity (BTU/hr) * | Rated Heating Capacity (BTU/hr)* | Does the Unit have Electric Resistance Heating? | Quantity | Cooling Efficiency* |  |  | Heating Efficiency*
[10 empty] | IEER | EER | SEER | COP | HSPF |  | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh | Proposed Annual Peak kW | Annual kWh Savings | Annual kW Savings (%) | Peak kW Savings | Peak kW Savings (%) | Incremental Measure Cost | Incentive
1 | [23 empty] | 0
2 | [23 empty] | 0
3 | [23 empty] | 0
4 | [23 empty] | 0
5 | [23 empty] | 0
6 | [23 empty] | 0
7 | [23 empty] | 0
8 | [23 empty] | 0
9 | [23 empty] | 0
10 | [23 empty] | 0
[15 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline Equipment
|  | Model # / Equipment Notes |  |  | Remaining Useful life (In Years) | Cooling Efficiency* |  |  | Heating Efficiency*
[6 empty] | IEER | EER | SEER | COP | HSPF
| 1 | [6 empty] | 10 |  |  | 0
| 2 | [9 empty] | 0
| 3 | [9 empty] | 0
| 4 | [9 empty] | 0
| 5 | [9 empty] | 0
| 6 | [9 empty] | 0
| 7 | [9 empty] | 0
| 8 | [9 empty] | 0
| 9 | [9 empty] | 0
| 10 | [9 empty] | 0

## Chiller
Last Updated: See Version Log
Chiller
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells.Cells with a * are required.See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Project Type* | Proposed Unit | [9 empty] | Financial Summary
|  | Chiller ID | Equipment Type* | Project Cost | Fixed or Variable Speed | Rated Cooling Capacity (tons) | Quantity | Cooling Efficiency*
[8 empty] | IPLV [in EER for Air Cooled; kW/ton for Water Cooled] | Full Load kW/ton | Full Load EER |  | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh | Proposed Annual peak kW | Annual kWh Savings | Annual kWh Savings (%) | Peak kW Savings | Peak kW Savings (%) | Incremental Measure Cost | Incentive
1 | [19 empty] | 0
2 | [19 empty] | 0
3 | [19 empty] | 0
4 | [19 empty] | 0
5 | [19 empty] | 0
6 | [19 empty] | 0
7 | [19 empty] | 0
8 | [19 empty] | 0
9 | [19 empty] | 0
10 | [19 empty] | 0
[11 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline Equipment
|  | Model # / Equipment Notes |  |  | Remaining Useful life (In Years) | Cooling Efficiency*
[6 empty] | IPLV | Full Load kW/ton | Full Load EER
| 1 | [7 empty] | 0
| 2 | [7 empty] | 0
| 3 | [7 empty] | 0
| 4 | [7 empty] | 0
| 5 | [7 empty] | 0
| 6 | [7 empty] | 0
| 7 | [7 empty] | 0
| 8 | [7 empty] | 0
| 9 | [7 empty] | 0
| 10 | [7 empty] | 0

## Geothermal
Last Updated: See Version Log
Water Source and Geothermal
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Project Type* | Proposed Unit | [13 empty] | Financial Summary
|  | Equipment ID | Proposed Equipment Type* | Existing Equipment Type | Rated Cooling Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Project Cost | Quantity | Cooling Efficiency* | Heating Efficiency* | Ground Loop Motor Information*
[9 empty] | EER | COP | Motor Quantity | Motor Size | Motor Efficiency | Pump Efficiency |  | Existing kWh | Existing kW | Proposed kWh | Proposed kW | kWh Savings | kWh Savings (%) | kW Savings | kW Savings (%) | Incremental Measure Cost | Incentive
1 | [23 empty] | 0
2 | [23 empty] | 0
3 | [23 empty] | 0
4 | [23 empty] | 0
5 | [23 empty] | 0
6 | [23 empty] | 0
7 | [23 empty] | 0
8 | [23 empty] | 0
9 | [23 empty] | 0
10 | [23 empty] | 0
[15 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline Equipment
| Model # / Equipment Notes |  |  | Remaining Useful life (In Years) | Does The Unit have Electric Resistance? | Cooling Efficiency |  |  | Heating Efficiency |  | Ground Loop Motor Information
[6 empty] | IEER | EER | SEER | COP | HSPF | Motor Quantity | Motor Size (HP) | Motor Efficiency | Pump Efficiency
1 | [14 empty] | 0
2 | [14 empty] | 0
3 | [14 empty] | 0
4 | [14 empty] | 0
5 | [14 empty] | 0
6 | [14 empty] | 0
7 | [14 empty] | 0
8 | [14 empty] | 0
9 | [14 empty] | 0
10 | [14 empty] | 0
TRUE

## Ductless Mini Splits
Last Updated: See Version Log
Ductless Mini Splits
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Equipment ID | Proposed Equipment | [6 empty] | Financial Summary
|  | Project Cost | Rated Cooling Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Number of Zones Served (or Quantity) | Cooling Efficiency* | Heating Efficiency
[6 empty] | SEER | HSPF |  | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh | Proposed Annual peak kW | Annual kWh Savings | Annual kWh Savings (%) | Peak kW Savings | Peak kW Savings (%) | Incremental Measure Cost | Incentive
1 | [16 empty] | 0
2 | [16 empty] | 0
3 | [16 empty] | 0
4 | [16 empty] | 0
5 | [16 empty] | 0
6 | [16 empty] | 0
7 | [16 empty] | 0
8 | [16 empty] | 0
9 | [16 empty] | 0
10 | [16 empty] | 0
[8 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline Equipment
| Model # / Equipment Notes |  |  | Cooling Equipment Type | Standard/ Non Standard Size | Heating Equipment Type | Standard/ Non Standard Size
1 | [7 empty] | 0
2 | [7 empty] | 0
3 | [7 empty] | 0
4 | [7 empty] | 0
5 | [7 empty] | 0
6 | [7 empty] | 0
7 | [7 empty] | 0
8 | [7 empty] | 0
9 | [7 empty] | 0
10 | [7 empty] | 0

## Fuel Switching
Last Updated: See Version Log
Fuel Switching
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Project Type* | Proposed Unit | [8 empty] | Financial Summary
|  | Equipment ID* | Proposed Equipment Type* | Project Cost* | Rated Heating Capacity* (BTU/hr) | Proposed Quantity* | AFUE* (%) | Blower Motor Size* (HP) | Blower Motor Efficiency* (%) |  | Annual kWh Savings | Peak kW Savings | Increase in Annual Fuel Consumption (therms) | Incremental Measure Cost | Incentive
1 | [11 empty] | 0 |  | 0
2 | [11 empty] | 0 |  | 0
3 | [11 empty] | 0 |  | 0
4 | [11 empty] | 0 |  | 0
5 | [11 empty] | 0 |  | 0
6 | [11 empty] | 0 |  | 0
7 | [11 empty] | 0 |  | 0
8 | [11 empty] | 0 |  | 0
9 | [11 empty] | 0 |  | 0
10 | [11 empty] | 0 |  | 0
[10 empty] | Total | 0 | 0 | 0 | 0 | 0
Baseline Equipment
| Model # / Equipment Notes* |  | Remaining Useful Life* (in Years) | Equipment Type* | Standard/Non Standard Size* | Rated Heating Capacity* (BTU/hr) | Existing Quantity* | Heating Efficiency
[8 empty] | COP* | HSPF*
1
2
3
4
5
6
7
8
9
10

## Ref Charge Correction
Last Updated: See Version Log
Refrigerant Charge Correction
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Project Type* | Proposed Unit | [13 empty] | Refrigerant Adjustment |  | Calculation |  |  | Financial Summary
|  | Equipment ID | Project Cost | Equipment Type* | Standard / Non Standard Size | Capacity Group | Rated Cooling Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Does the Unit have Electric Resistance Heating? | Quantity | Cooling Efficiency* |  |  | Heating Efficiency* |  | % Refrigerant Charge Corrected | Expansion Valve | kWh Saved | Peak kW Savings | Incentive
[11 empty] | IEER | EER | SEER | COP | HSPF | [5 empty] | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh | Proposed Annual Peak kW | Annual kWh Savings | Annual kW Savings (%) | Peak kW Savings | Peak kW Savings | Incremental Measure Cost | Incentive
1 | [17 empty] | 0 | 0 | 0 | 0 | 4.8673 | 9900 | 5.5 | -9900 |  | -0.63274 | -13% | 0 | Project does not qualify; check efficiency requirements
2 | [17 empty] | 0 | 0 | 0 | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% | 0 | Project does not qualify; check efficiency requirements
3 | [17 empty] | 0 | 0 | 0 | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% | 0 | Project does not qualify; check efficiency requirements
4 | [17 empty] | 0 | 0 | 0 | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% | 0 | Project does not qualify; check efficiency requirements
5 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
6 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
7 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
8 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
9 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
10 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
[17 empty] | Total | 0 | 0 | 0

## Room AC
Last Updated: See Version Log
Room Air Conditioner
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells.Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Project Type* | Proposed Unit | [7 empty] | Results |  |  | Financial Summary
|  | Equipment ID | Project Cost | Equipment Type* | Cooling Capacity Range | Cooling Capacity | New Unit CEER | New Unit EER | Quantity | kWh Savings | Peak kW Savings | Incentive
[13 empty] | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh | Proposed Annual Peak kW | Annual kWh Savings | Annual kW Savings (%) | Peak kW Savings | Peak kW Savings | Incremental Measure Cost | Incentive
1 | [9 empty] | 0 | 0 | 0 | 0 | 4.8673 | 9900 | 5.5 | -9900 |  | -0.63274 | -13% | 0 | Project does not qualify; check efficiency requirements
2 | [9 empty] | 0 | 0 | 0 | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% | 0 | Project does not qualify; check efficiency requirements
3 | [9 empty] | 0 | 0 | 0 | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% | 0 | Project does not qualify; check efficiency requirements
4 | [9 empty] | 0 | 0 | 0 | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% | 0 | Project does not qualify; check efficiency requirements
5 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
6 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
7 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
8 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
9 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
10 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
[9 empty] | Total | 0 | 0 | 0
0
0
0
0
0
0
0
0
0
0

## Guest Room Occ Sensor
Last Updated: See Version Log
Guest Room Occ Sensor
Instructions: Enter the project information in the yellow cells below.Cells with a * are required. Do not enter data in grayed-out cells. See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Facility Information | [5 empty] | Financial Summary
| Equipment ID | Project Cost | Is There Housekeeping Setback? | Rated Cooling Capacity (tons) | Equipment Type |  | kWh Savings | kW Savings | Incremental Measure Cost | Incentive
1 | [8 empty] | 0
2 | [8 empty] | 0
3 | [8 empty] | 0
4 | [8 empty] | 0
5 | [8 empty] | 0
6 | [8 empty] | 0
7 | [8 empty] | 0
8 | [8 empty] | 0
9 | [8 empty] | 0
10 | [8 empty] | 0
[6 empty] | Total | 0 | 0 | 0 | 0

## Economizers
Last Updated: See Version Log
HVAC Economizer Calculator
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Site
Address
Location*
Building Type*
| Facility Information | [5 empty] | Financial Summary
| Equipment ID | Project Cost | HVAC Nameplate Efficiency Values | Operating Hours | Area Served (sq. ft.) |  | kWh Savings | kW Savings | Incremental Measure Cost | Incentive
1 | [7 empty] | 0 | 0
2 | [7 empty] | 0 | 0
3 | [7 empty] | 0 | 0
4 | [7 empty] | 0 | 0
5 | [7 empty] | 0 | 0
6 | [7 empty] | 0 | 0
7 | [7 empty] | 0 | 0
8 | [7 empty] | 0 | 0
9 | [7 empty] | 0 | 0
10 | [7 empty] | 0 | 0
[6 empty] | Total | 0 | 0 | 0 | 0
Baseline Equipment
| Equipment Type | Rated Cooling Capacity (BTU/hr) | Does the Unit have Electric Resistance Heating? | Cooling Efficiency
|  |  |  | IEER | EER | SEER
1
2
3
4
5
6
7
8
9
10

## Insulation (hidden)
Last Updated: See Version Log
Insulation
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Project Type* | Project Information | [10 empty] | Financial Summary
|  | Equipment ID | Project Cost | Remaining Useful Life of Existing Insulation (in years) | Are Existing Insulation R-Values Known? | Ceiling Insulation |  |  | Wall Insulation |  |  |  | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh Consumption | Proposed Annual Peak kW | Annual kWh Savings | Annual kWh Savings (%) | Peak kW Savings | Peak kW Savings (%) | Incremental Measure Cost | Incentive
|  |  |  | Remaining Useful Life of Existing Insulation (in years) | Are Existing Insulation R-Values Known? | Area of Ceiling (sq. ft.) | R-Value of Existing Ceiling Insulation | R-Value of Proposed Ceiling Insulation | Area of Wall (sq. ft.) | R-Value of Existing Wall Insulation | R-Value of Proposed Wall Insulation |  |  |  | Proposed Annual kWh Consumption | Proposed Annual Peak kW | [5 empty] | Incentive
1 | [20 empty] | 0
2 | [20 empty] | 0
3 | [20 empty] | 0
4 | [20 empty] | 0
5 | [20 empty] | 0
6 | [20 empty] | 0
7 | [20 empty] | 0
8 | [20 empty] | 0
9 | [20 empty] | 0
10 | [20 empty] | 0
[12 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC Equipment Information
| Equipment Type | Rated Cooling Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Does the Unit have Electric Resistance Heating? | Are HVAC Equipment Efficiency Values Known? | Cooling Efficiency |  |  | Heating Efficiency
|  | Rated Cooling Capacity (BTU/hr) | Rated Heating Capacity (BTU/hr) | Does the Unit have Electric Resistance Heating? | Are HVAC Equipment Efficiency Values Known? | IEER | EER | SEER | COP | HSPF
1 | [10 empty] | 0
2 | [10 empty] | 0
3 | [10 empty] | 0
4 | [10 empty] | 0
5 | [10 empty] | 0
6 | [10 empty] | 0
7 | [10 empty] | 0
8 | [10 empty] | 0
9 | [10 empty] | 0
10 | [10 empty] | 0

## Computer Room AC
Last Updated: See Version Log
Computer Room Air Conditioner
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Proposed Unit | [6 empty] | Results |  |  | Financial Summary
| Equipment ID | Project Cost | Equipment Type* | Upflow / Downflow | Cooling Capacity (Btu/hr) | New Unit SCOP | Quantity | kWh Savings | Peak kW Savings | Incentive
[11 empty] | Existing Annual kWh Consumption | Existing Annual Peak kW | Proposed Annual kWh | Proposed Annual Peak kW | Annual kWh Savings | Annual kW Savings (%) | Peak kW Savings | Peak kW Savings | Incremental Measure Cost | Incentive
1 | [7 empty] | 0 | 0 | 0 | 0 | 4.8673 | 9900 | 5.5 | -9900 |  | -0.63274 | -13% | 0 | Project does not qualify; check efficiency requirements
2 | [7 empty] | 0 | 0 | 0 | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% | 0 | Project does not qualify; check efficiency requirements
3 | [7 empty] | 0 | 0 | 0 | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% | 0 | Project does not qualify; check efficiency requirements
4 | [7 empty] | 0 | 0 | 0 | 847.0645 | 0.20353 | 989.381 | 0.14667 | -142.3165 | -16.8% | 0.056867 | 27.94% | 0 | Project does not qualify; check efficiency requirements
5 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
6 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
7 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
8 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
9 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
10 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
[7 empty] | Total | 0 | 0 | 0

## Computer Room AC ECM or VFD
Last Updated: See Version Log
Computer Room Air Conditioner EC Motor or VSD on AC Fan Motors
Instructions: Enter the project information in the yellow cells below. Do not enter data in grayed-out cells. Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Proposed Unit | [6 empty] | Results
| Equipment ID | Project Cost | ECM or VSD Measure Installation | Horsepower if Known | Location of Fan Plug - Required for ECM | Hours if Other than 8760 | Quantity | kWh Savings | Peak kW Savings | Incentive
1
2
3
4
5
6
7
8
9
10
[7 empty] | Total | 0 | 0 | 0

## Drop down (hidden)
Drop Down Table 1 | Drop Down Table 2 | Drop Down Table 3 | Drop Down Table 4 | Drop Down Table 5 | Drop Down Table 6 | Drop Down Table 7 | Drop Down Table 8 | Drop Down Table 9 | Drop Down Table 10 | Drop Down Table 11 | Drop Down Table 12 | Drop Down Table 13 | Drop Down Table 14 | Drop Down Table 15 | Drop Down Table 16 | Drop Down Table 17 | Drop Down Table 18 | Drop Down Table 19 | Drop Down Table 20 | Drop Down Table 21 | Drop Down Table 22 | Drop Down Table 23 | Drop Down Table 24 | Drop Down Table 25 | Drop Down Table 26
yBuilding_Type_HVAC | yBuilding Type_Chillers | yBuildingType_GuestRooms | yProject_Type | yEfficiencyKnown | xBuilding_Location | HVAC Equipment Type | Economizer HVAC Equipment Type | Chiller Equipment Type | Geothermal Equipment Type | yGR_EqmtType_Motel | yGR_EqmtType_Hotel | Electric Resistance? | Fuel Switching Equipment Type_Electric | Fuel Switching Equipment Type_NonElectric | PTAC/PTHP Type | yOperating_Schedule | xExpValve | yRefCharge% | yDHPBaseHeatingEquipment Type | yDHPBaseCoolingEquipment Type | yMotorSize | yMotorType | yMotorPoles | y_RACeqmttype | yRAC_options
Assembly | Education - Community College | Hotel | Early Replacement | Nameplate Efficiency Values known | Allentown | Air-Source Air Conditioner | Air-Source Air Conditioner | Air Cooled Chiller | Air-Source Heat Pumps | PTAC with Electric Resistance Heat | PTAC with Electric Resistance Heat | Yes | Air-Source Heat Pumps | Gas Furnace | Standard | 1 Shift, 5 days per week | TXV | 0.6 | Standard Ductless Heat Pump | Standard Ductless Heat Pump | 1 | Open | 2 poles | Room Air Conditioners | Without Louvered Sides
Education - Community College | Education - Secondary School | Motel | End of Useful Life or New Construction | Nameplate Efficiency Values NOT known | Erie | Air-Source Heat Pumps | Air-Source Heat Pumps | Water Cooled Chiller: Positive Displacement or Reciprocating | Water-Source Heat Pumps | PTAC with Gas Heat | PTAC with Gas Heat | No | Electric Furnace | Oil Furnace | Non Standard | 2 Shift, 5 days per week | Orifice | 0.59 | Electric Resistance | Central Air Conditioning | 1.5 | Enclosed | 4 poles | Reverse Cycle Room Air Conditioners | With Louvered Sides
Education - Primary School | Education - University |  |  |  | Harrisburg | Water Cooled Air Conditioners | Water Cooled Air Conditioners | Water Cooled Chiller: Centrifugal | Ground Water Source Heat Pumps | PTHP | PTHP |  | Baseboard Heating | Gas/Propane Steam Boiler |  | 3 Shift, 5 days per week |  | 0.58 | Air-Source Heat Pump | Air-Source Heat Pump | 2 |  | 6 poles | Casement-Only Room Air Conditioners
Education - Relocatable Classroom | Health/Medical - Hospital |  |  |  | Philadelphia | Evaporatively Cooled Air Conditioners | Evaporatively Cooled Air Conditioners |  |  | Ground Source Heat Pumps |  | Central HW Fan Coil with Electric Resistance Heat |  | PTHP | Gas/Propane Hot Water Boiler |  | 24/7 |  | 0.57 | Electric Furnace | Room Air Conditoner | 3 |  | 8 poles | Casement-Slider Room Air Conditioners
Education - Secondary School | Health/Medical - Nursing Home |  |  |  | Pittsburgh | PTAC |  |  |  | Other |  | Central HW Fan Coil with Gas Heat |  |  | Oil Steam Boiler |  |  |  | 0.56 | PTHP | PTAC | 5
Education - University | Lodging - Hotel |  |  |  | Scranton | PTHP | [8 empty] | Oil Hot Water Boiler |  |  |  | 0.55 | New Space/No existing heat/Non-electric Heat | PTHP | 7.5
Grocery | Manufacturing – Bio Tech/High Tech |  |  |  | Williamsport | [16 empty] | 0.54 | New Space/No existing cooling | New Space/No existing cooling | 10
Health/Medical - Hospital | Office - Large | [20 empty] | 0.53 |  | 0.35 | 15
Health/Medical - Nursing Home | Office - Small | [20 empty] | 0.52 |  | 0.34 | 20
Lodging - Hotel | Retail - Multistory Large | [20 empty] | 0.51 |  | 0.33 | Other
Manufacturing – Bio Tech/High Tech | [21 empty] | 0.5 |  | 0.32 | Other
Manufacturing – 1 Shift/Light Industrial | [21 empty] | 0.49 |  | 0.31
Multi-Family (Common Areas) | [21 empty] | 0.48 |  | 0.3
Office - Large | [21 empty] | 0.47 |  | 0.29
Office - Small | [21 empty] | 0.46 |  | 0.28
Restaurant - Fast-Food | [21 empty] | 0.45 |  | 0.27
Restaurant - Sit-Down | [21 empty] | 0.44 |  | 0.26
Retail - Multistory Large | [21 empty] | 0.43 |  | 0.25
Retail - Single-Story Large | [21 empty] | 0.42 |  | 0.24
Retail - Small | [21 empty] | 0.41 |  | 0.23
Storage - Conditioned | [21 empty] | 0.4
Warehouse - Refrigerated | [21 empty] | 0.39
0.38
0.37
0.36
0.22
0.21
0.2
0.19
0.18
0.17
0.16
0.15
0.14
0.13
0.12
0.11
0.1
0.09
0.08
0.07
0.06
0.05
0.04
0.03
0.02
0.01
0
-0.01
-0.02
-0.03
-0.04
-0.05
-0.06
-0.07
-0.08
-0.09
-0.1
-0.11
-0.12
-0.13
-0.14
-0.15
-0.16
-0.17
-0.18
-0.19
-0.2
-0.21
-0.22
-0.23
-0.24
-0.25
-0.26
-0.27
-0.28
-0.29
-0.3
-0.31
-0.32
-0.33
-0.34
-0.35

## Hi Vol Low Speed Fans
Circulation Fan: High Volume Low Speed Fans Calculator
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Site
Address
Location
Building Type*
| Proposed Unit | [5 empty] | Results
| Equipment ID | No. of Conventional Fans Removed* | No. of HVLS Circulating Fans Installed* | Conventional Fan Size* | Fan Size (Diameter)* | Total Equipment Cost* | Annual Savings (Fans) (kWh) | Peak Demand Savings (kW) | Incentive
1
2
3
4
5
6
7
8
9
10
[6 empty] | Total | 0 | 0 | 0

## Lookups (hidden)
Lookups | [29 empty] | TRM 2021 Table 3-43
Air Conditioning EFLHs | [9 empty] | Chiller EFLHs | [9 empty] | Free Cooling Hours by Operating Schedule | [9 empty] | Refrigerant Charge Correction Factor |  |  | Guest Room Controls | [6 empty] | Motor Efficiencies |  |  |  |  | Ground Pump Efficiencies |  | Degree Days | [7 empty] | MEASURE_CODE | MEASURE_DESC
Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Operating Schedule | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | % of nameplate charge added (removed) | TXV | Orifice | Building Type | HVAC System Type | Housekeeping Setback | Helper Column | ESF Lookup | DSF Lookup |  | Poles | Type | Motor HP | Helper column | Efficiency | HP | Minimum Pump Efficiency at Design Point (ηpump) | Space and/or Building Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | CAC<5.4Tons | HVAC Systems | PPL MEASURE_DESC | DSMT Description/Product Style | Data Model | PPL Commercial Downstream Measure List
Education - College/University | 640 | 440 | 369 | 478 | 657 | 734 | 594 | 533 | 595 | Education - College/University | 665 | 416 | 368 | 490 | 696 | 770 | 600 | 524 | 619 | 1 Shift, 5 days per week | 444 | 396 | 354 | 406 | 402 | 432 | 422 | 487 | 407 | 60% | 68% | 13% | Motel | PTAC with Electric Resistance Heat | Yes | MotelPTAC with Electric Resistance HeatYes | 559 | 0.1 |  | 2 poles | Enclosed | 1 | 2 polesEnclosed1 | 77% | 1 | 65% | CDD | 787 | 620 | 955 | 1235 | 726 | 611 | 709 | CAC EER | HVAC Systems | Air-Cooled Electric Chillers | ACChill | Electric Chillers
Education - Other | 267 | 163 | 139 | 185 | 310 | 345 | 273 | 217 | 239 | Education - Other | 275 | 182 | 161 | 214 | 344 | 389 | 282 | 244 | 316 | 2 Shift, 5 days per week | 691 | 615 | 550 | 641 | 645 | 663 | 635 | 738 | 642 | 59% | 70% | 16% | Motel | PTAC with Electric Resistance Heat | No | MotelPTAC with Electric Resistance HeatNo | 1877 | 0.28 |  | 2 poles | Enclosed | 1.5 | 2 polesEnclosed1.5 | 84% | 1.5 | 65% | HDD | 5318 | 6353 | 4997 | 4709 | 5429 | 6176 | 5651 | CAC IEER | HVAC Systems | Commercial ASHP > 5.4 Tons EER | ASHP EER | HVAC Systems | Air Source Heat Pumps
Grocery | 654 | 542 | 542 | 636 | 453 | 536 | 638 | 434 | 442 | Health - Hospital | 1240 | 935 | 825 | 1100 | 1362 | 1556 | 1185 | 1134 | 1208 | 3 Shift, 5 days per week | 1119 | 997 | 892 | 1033 | 1066 | 1098 | 997 | 1169 | 1066 | 58% | 71% | 19% | Motel | PTAC with Gas Heat | Yes | MotelPTAC with Gas HeatYes | 85 | 0.1 |  | 2 poles | Enclosed | 2 | 2 polesEnclosed2 | 85.5% | 2 | 65% | [8 empty] | ASHP<5.4Tons | HVAC Systems | Commercial ASHP > 5.4 Tons IEER | ASHP IEER | HVAC Systems | Air Source Heat Pumps
Health - Hospital | 1030 | 977 | 977 | 1038 | 892 | 1059 | 788 | 1022 | 1013 | Health - Other | 459 | 347 | 306 | 408 | 520 | 622 | 472 | 418 | 462 | 24/7 | 1787 | 1643 | 1469 | 1652 | 1861 | 1772 | 1708 | 1870 | 1786 | 57% | 72% | 22% | Motel | PTAC with Gas Heat | No | MotelPTAC with Gas HeatNo | 287 | 0.28 |  | 2 poles | Enclosed | 3 | 2 polesEnclosed3 | 86.5% | 3 | 67% | Ceiling and Wall Insulation Values | [7 empty] | ASHP EER | HVAC Systems | Commercial ASHP <= 5.4 Tons | ASHP<5.4Tons | HVAC Systems | Air Source Heat Pumps
Health - Other | 477 | 397 | 350 | 481 | 540 | 684 | 511 | 467 | 476 | Industrial Manufacturing | 708 | 449 | 395 | 527 | 700 | 780 | 631 | 574 | 614 | [10 empty] | 56% | 73% | 25% | Motel | PTHP | Yes | MotelPTHPYes | 260 | 0.1 |  | 2 poles | Enclosed | 5 | 2 polesEnclosed5 | 88.5% | 5 | 70% | Building Type | Wall Ri-Value (New Construction) | Wall Ri-Value (Existing) | Ceiling Ri-Value (New Construction) | Ceiling Ri-Value (Existing) | PA TRM assumed type |  |  | ASHP IEER | HVAC Systems | Commercial CAC > 5.4 Tons EER | CAC EER | HVAC Systems | Packaged Split A/C
Industrial Manufacturing | 570 | 361 | 309 | 411 | 616 | 682 | 530 | 445 | 478 | Lodging | 1397 | 1178 | 988 | 1317 | 1511 | 1654 | 1432 | 1352 | 1415 | [10 empty] | 55% | 74% | 28% | Motel | PTHP | No | MotelPTHPNo | 1023 | 0.28 |  | 2 poles | Enclosed | 7.5 | 2 polesEnclosed7.5 | 89.5% | 7.5 | 73% | Assembly | 14 | 2.5 | 24.4 | 13.4 | Warehouse |  |  | WEAC | HVAC Systems | Commercial CAC > 5.4 Tons IEER | CAC IEER | HVAC Systems | Packaged/Split AC
Institutional/Public Service | 753 | 516 | 455 | 607 | 820 | 1087 | 706 | 629 | 685 | Office | 446 | 334 | 295 | 393 | 521 | 586 | 443 | 410 | 453 | [10 empty] | 54% | 76% | 31% | Hotel | PTAC with Electric Resistance Heat | Yes | HotelPTAC with Electric Resistance HeatYes | 322 | 0.04 |  | 2 poles | Enclosed | 10 | 2 polesEnclosed10 | 90.2% | 10 | 75% | Education - Community College | 13 | 2 | 20 | 9 | Education |  |  | WEAC IEER | HVAC Systems | Commercial CAC <= 5.4 Tons | CAC<5.4Tons | HVAC Systems | Packaged/Split AC
Lodging | 1386 | 1205 | 1084 | 1392 | 1523 | 1732 | 1478 | 1348 | 1384 | Retail | 749 | 518 | 457 | 609 | 836 | 897 | 699 | 659 | 742 | [10 empty] | 53% | 77% | 33% | Hotel | PTAC with Electric Resistance Heat | No | HotelPTAC with Electric Resistance HeatNo | 1083 | 0.1 |  | 2 poles | Enclosed | 15 | 2 polesEnclosed15 | 91% | 15 | 77% | Education - Primary School | 13 | 2 | 20 | 9 | Education |  |  | EAC | HVAC Systems | Custom CHP | CHP | Custom Combined Heat and Power | Custom
Multifamily (Common Areas) | 1395 | 654 | 577 | 769 | 1482 | 1647 | 1176 | 991 | 1052 | [20 empty] | 52% | 78% | 36% | Hotel | PTAC with Gas Heat | Yes | HotelPTAC with Gas HeatYes | 259 | 0.03 |  | 2 poles | Enclosed | 20 | 2 polesEnclosed20 | 91% | 20 | 77% | Education - Relocatable Classroom | 13 | 2 | 20 | 9 | Education |  |  | EAC IEER | HVAC Systems | Commercial DHP <5.4 Tons | CommDHP | Ductless mini-split heat pumps < 5.4 tons | Ductless Mini-split Heat Pump
Office | 458 | 213 | 323 | 412 | 565 | 704 | 721 | 500 | 466 | [20 empty] | 51% | 79% | 39% | Hotel | PTAC with Gas Heat | No | HotelPTAC with Gas HeatNo | 876 | 0.08 |  | 2 poles | Open | 1 | 2 polesOpen1 | 77% |  |  | Education - Secondary School | 13 | 2 | 20 | 9 | Education |  |  | ACChill | Electric Chillers | Custom HVAC | CustHVAC | Custom HVAC | Custom
Restaurant | 550 | 429 | 374 | 513 | 590 | 791 | 632 | 522 | 594 | [20 empty] | 50% | 80% | 41% | Hotel | PTHP | Yes | HotelPTHPYes | 283 | 0.03 |  | 2 poles | Open | 1.5 | 2 polesOpen1.5 | 84% |  |  | Education - University | 13 | 2 | 20 | 9 | Education |  |  | WCChill | Electric Chillers | Custom HVAC Optimization | CustHVACOpt | Custom HVAC Optimization | Custom
Retail | 735 | 535 | 464 | 620 | 742 | 911 | 816 | 603 | 648 | [20 empty] | 49% | 81% | 44% | Hotel | PTHP | No | HotelPTHPNo | 1113 | 0.09 |  | 2 poles | Open | 2 | 2 polesOpen2 | 85.5% |  |  | Grocery | 13 | 2 | 20 | 9 | Grocery |  |  | WCEChill | Electric Chillers | Evaporated Cooled AC EER | EAC | HVAC Systems | Packaged/Split AC
Warehouse - Other | 174 | 97 | 86 | 114 | 235 | 346 | 192 | 130 | 178 | [20 empty] | 48% | 82% | 46% | Hotel | Central HW Fan Coil with Electric Resistance Heat | Yes | HotelCentral HW Fan Coil with Electric Resistance HeatYes | 245 | 0.03 |  | 2 poles | Open | 3 | 2 polesOpen3 | 86.5% |  |  | Health/Medical - Hospital | 13 | 2 | 20 | 9 | Health |  |  | CommDHP | Ductless mini-split heat pumps < 5.4 tons | Evaporated Cooled AC IEER | EAC IEER | HVAC Systems | Packaged/Split AC
Warehouse - Refrigerated | 3130 | 3048 | 3010 | 3080 | 3163 | 3200 | 3116 | 3094 | 3135 | [20 empty] | 47% | 83% | 48% | Hotel | Central HW Fan Coil with Electric Resistance Heat | No | HotelCentral HW Fan Coil with Electric Resistance HeatNo | 822 | 0.08 |  | 2 poles | Open | 5 | 2 polesOpen5 | 88.5% |  |  | Health/Medical - Nursing Home | 13 | 2 | 20 | 9 | Health |  |  | GROOC Sensor | Guest Room Occupancy Sensor controls | Economizer> 5.4Tons IEER | EconIEER | Economizer controls | Economizer Controls
[30 empty] | 46% | 84% | 51% | Hotel | Central HW Fan Coil with Gas Heat | Yes | HotelCentral HW Fan Coil with Gas HeatYes | 182 | 0.02 |  | 2 poles | Open | 7.5 | 2 polesOpen7.5 | 89.5% |  |  | Lodging - Hotel | 13 | 2 | 20 | 9 | Lodging |  |  | EconSEER | Economizer controls | Economizer units <=5.4 Tons | EconSEER | Economizer controls | Economizer Controls
Heat Pump EFLHs | [29 empty] | 45% | 85% | 53% | Hotel | Central HW Fan Coil with Gas Heat | No | HotelCentral HW Fan Coil with Gas HeatNo | 615 | 0.06 |  | 2 poles | Open | 10 | 2 polesOpen10 | 90.2% |  |  | Manufacturing – Bio Tech/High Tech | 14 | 2.5 | 24.4 | 13.4 | Warehouse |  |  | EconIEER | Economizer controls | ENERGY STAR Room A/C | ESRAC | ENERGY STAR Room A/C | ENERGY STAR Room A/C
Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | [20 empty] | 44% | 86% | 55% | [7 empty] | 2 poles | Open | 15 | 2 polesOpen15 | 91% |  |  | Manufacturing – 1 Shift/Light Industrial | 14 | 2.5 | 24.4 | 13.4 | Warehouse |  |  | IncCorrect | Incentive Correction | Guest Room Occupancy Sensors | GROOC Sensor | Guest Room Occupancy Sensor controls | Guest Room Occupancy Sensor Controls
Education - College/University | 719 | 984 | 1078 | 857 | 552 | 464 | 651 | 824 | 655 | [20 empty] | 43% | 86% | 57% | [7 empty] | 2 poles | Open | 20 | 2 polesOpen20 | 91% |  |  | Multi-Family (Common Areas) | 13 | 2 | 20 | 9 | Lodging |  |  | IncAdjust | Incentive Adjustment | Water Centrifugal Chiller | WCChill | Electric Chillers | Water Cooled Chillers
Education - Other | 636 | 910 | 1018 | 666 | 741 | 646 | 884 | 925 | 655 | [20 empty] | 42% | 87% | 60% | [7 empty] | 4 poles | Enclosed | 1 | 4 polesEnclosed1 | 77% |  |  | Office - Large | 14 | 1.6 | 20 | 9 | Large Office |  |  | CustHVAC | Custom HVAC | Water Cooled Electric Chiller | WCEChill | Electric Chillers | Water Cooled Chillers
Grocery | 733 | 1068 | 1068 | 534 | 1269 | 1217 | 564 | 1737 | 1419 | [20 empty] | 41% | 88% | 62% | [7 empty] | 4 poles | Enclosed | 1.5 | 4 polesEnclosed1.5 | 84% |  |  | Office - Small | 14 | 3 | 24.4 | 13.4 | Small Office |  |  | CHP | Custom Combined Heat and Power | Water cooled EER | WEAC | HVAC Systems | Packaged/Split AC
Health - Hospital | 147 | 81 | 71 | 95 | 361 | 345 | 418 | 106 | 154 | [20 empty] | 40% | 89% | 64% | [7 empty] | 4 poles | Enclosed | 2 | 4 polesEnclosed2 | 85.5% |  |  | Restaurant - Fast-Food | 14 | 3.2 | 20 | 9 | Restaurant |  |  | HVLSFANSHVAC |  | Water cooled IEER | WEAC IEER | HVAC Systems | Packaged/Split AC
Health - Other | 944 | 1432 | 1630 | 1304 | 854 | 805 | 1023 | 1193 | 958 | [20 empty] | 39% | 89% | 65% | [7 empty] | 4 poles | Enclosed | 3 | 4 polesEnclosed3 | 85.5% |  |  | Restaurant - Sit-Down | 14 | 3.2 | 20 | 9 | Restaurant |  |  | CustHVACOpt | Custom HVAC Optimization | High Volume Low Speed fans | HVLSFANS | High Volume Low Speed fans | High Volume Low Speed Fans
Industrial Manufacturing | 406 | 500 | 568 | 473 | 374 | 339 | 400 | 441 | 346 | [20 empty] | 38% | 90% | 67% | [7 empty] | 4 poles | Enclosed | 5 | 4 polesEnclosed5 | 86.5% |  |  | Retail - Multistory Large | 14 | 3 | 20 | 9 | Large Retail |  |  | ESRAC | ENERGY STAR Room A/C
Institutional/Public Service | 1178 | 1489 | 1719 | 1437 | 1098 | 1121 | 1163 | 1401 | 1066 | Chiller CFs | [19 empty] | 37% | 91% | 69% | [7 empty] | 4 poles | Enclosed | 7.5 | 4 polesEnclosed7.5 | 88.5% |  |  | Retail - Single-Story Large | 14 | 3 | 20 | 9 | Large Retail
Lodging | 2371 | 3219 | 3846 | 3077 | 2159 | 2017 | 2411 | 2591 | 2403 | Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | [10 empty] | 36% | 91% | 71% | [7 empty] | 4 poles | Enclosed | 10 | 4 polesEnclosed10 | 89.5% |  |  | Retail - Small | 14 | 3 | 20 | 9 | Small Retail
Multifamily (Common Areas) | 277 | 320 | 354 | 322 | 263 | 259 | 264 | 281 | 278 | Education - College/University | 0.42 | 0.28 | 0.23 | 0.31 | 0.43 | 0.46 | 0.41 | 0.34 | 0.4 | [10 empty] | 35% | 92% | 73% | [7 empty] | 4 poles | Enclosed | 15 | 4 polesEnclosed15 | 90.2% |  |  | Storage - Conditioned | 14 | 2.5 | 24.4 | 13.4 | Warehouse
Office | 321 | 159 | 527 | 422 | 330 | 281 | 344 | 329 | 340 | Education - Other | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17 | [10 empty] | 34% | 92% | 74% | [7 empty] | 4 poles | Enclosed | 20 | 4 polesEnclosed20 | 91% |  |  | Warehouse - Refrigerated | 14 | 2.5 | 24.4 | 13.4 | Warehouse
Restaurant | 1151 | 1865 | 2109 | 1687 | 1040 | 993 | 1340 | 1501 | 1241 | Health - Hospital | 0.5 | 0.45 | 0.42 | 0.48 | 0.5 | 0.54 | 0.48 | 0.48 | 0.5 | [10 empty] | 33% | 93% | 76% | [7 empty] | 4 poles | Open | 1 | 4 polesOpen1 | 85.5%
Retail | 809 | 1085 | 1221 | 980 | 648 | 632 | 781 | 855 | 675 | Health - Other | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26 | [10 empty] | 32% | 94% | 77% | [7 empty] | 4 poles | Open | 1.5 | 4 polesOpen1.5 | 86.5%
Warehouse - Other | 847 | 1108 | 1258 | 1114 | 843 | 900 | 978 | 1008 | 800 | Industrial Manufacturing | 0.53 | 0.41 | 0.33 | 0.43 | 0.53 | 0.58 | 0.54 | 0.48 | 0.5 | [10 empty] | 31% | 94% | 79% | [7 empty] | 4 poles | Open | 2 | 4 polesOpen2 | 86.5%
Warehouse - Refrigerated | 363 | 613 | 668 | 534 | 307 | 222 | 409 | 439 | 328 | Lodging | 0.62 | 0.59 | 0.54 | 0.61 | 0.68 | 0.69 | 0.71 | 0.6 | 0.68 | [10 empty] | 30% | 95% | 80% | [7 empty] | 4 poles | Open | 3 | 4 polesOpen3 | 89.5%
[10 empty] | Office | 0.29 | 0.24 | 0.21 | 0.27 | 0.35 | 0.23 | 0.32 | 0.29 | 0.32 | [10 empty] | 29% | 95% | 82% | [7 empty] | 4 poles | Open | 5 | 4 polesOpen5 | 89.5%
CFs | [9 empty] | Retail | 0.46 | 0.34 | 0.28 | 0.38 | 0.54 | 0.55 | 0.48 | 0.43 | 0.48 | [10 empty] | 28% | 95% | 83% | [7 empty] | 4 poles | Open | 7.5 | 4 polesOpen7.5 | 91.7%
Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | [20 empty] | 27% | 96% | 84% | [7 empty] | 4 poles | Open | 10 | 4 polesOpen10 | 91.7%
Education - College/University | 0.48 | 0.4 | 0.37 | 0.38 | 0.48 | 0.51 | 0.48 | 0.45 | 0.49 | [20 empty] | 26% | 96% | 85% | [7 empty] | 4 poles | Open | 15 | 4 polesOpen15 | 92.4%
Education - Other | 0.12 | 0.09 | 0.07 | 0.09 | 0.18 | 0.19 | 0.18 | 0.13 | 0.15 | [20 empty] | 25% | 97% | 87% | [7 empty] | 4 poles | Open | 20 | 4 polesOpen20 | 93%
Grocery | 0.33 | 0.26 | 0.26 | 0.27 | 0.24 | 0.26 | 0.27 | 0.21 | 0.24 | [20 empty] | 24% | 97% | 88% | [7 empty] | 6 poles | Enclosed | 1 | 6 polesEnclosed1 | 85.5%
Health - Hospital | 0.43 | 0.36 | 0.34 | 0.37 | 0.39 | 0.44 | 0.39 | 0.37 | 0.42 | [20 empty] | 23% | 97% | 89% | [7 empty] | 6 poles | Enclosed | 1.5 | 6 polesEnclosed1.5 | 86.5%
Health - Other | 0.26 | 0.25 | 0.23 | 0.27 | 0.3 | 0.34 | 0.32 | 0.28 | 0.29 | Eff For AC | [19 empty] | 22% | 98% | 90% | [7 empty] | 6 poles | Enclosed | 2 | 6 polesEnclosed2 | 86.5%
Industrial Manufacturing | 0.51 | 0.37 | 0.33 | 0.39 | 0.55 | 0.6 | 0.53 | 0.45 | 0.48 | [Cooling Capacity] | [Cooling Efficiency Default] | [Cooling Efficiency EER Lookup] | [17 empty] | 21% | 98% | 91% | [7 empty] | 6 poles | Enclosed | 3 | 6 polesEnclosed3 | 89.5%
Institutional/Public Service | 0.53 | 0.38 | 0.34 | 0.45 | 0.6 | 0.72 | 0.56 | 0.48 | 0.52 | < 65000 | 13 | 11.3 | [17 empty] | 20% | 98% | 92% | [7 empty] | 6 poles | Enclosed | 5 | 6 polesEnclosed5 | 89.5%
Lodging | 0.72 | 0.73 | 0.71 | 0.77 | 0.78 | 0.83 | 0.83 | 0.73 | 0.78 | ≥ 65000 and < 135000 | 11.4 | 11.2 | [17 empty] | 19% | 98% | 92% | [7 empty] | 6 poles | Enclosed | 7.5 | 6 polesEnclosed7.5 | 91%
Multifamily (Common Areas) | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | ≥ 135000 and < 240000 | 11.2 | 11 | [17 empty] | 18% | 99% | 93% | [7 empty] | 6 poles | Enclosed | 10 | 6 polesEnclosed10 | 91.7%
Office | 0.32 | 0.16 | 0.26 | 0.31 | 0.41 | 0.27 | 0.35 | 0.36 | 0.37 | = 240000 | 10.1 | 10 | [17 empty] | 17% | 99% | 94% | [7 empty] | 6 poles | Enclosed | 15 | 6 polesEnclosed15 | 93%
Restaurant | 0.38 | 0.36 | 0.33 | 0.37 | 0.42 | 0.5 | 0.49 | 0.39 | 0.45 | [20 empty] | 16% | 99% | 95% | [7 empty] | 6 poles | Enclosed | 20 | 6 polesEnclosed20 | 93%
Retail | 0.52 | 0.45 | 0.42 | 0.46 | 0.53 | 0.57 | 0.56 | 0.47 | 0.49 | EFF for HP | [19 empty] | 15% | 99% | 95% | [7 empty] | 6 poles | Open | 1 | 6 polesOpen1 | 82.5%
Warehouse - Other | 0.18 | 0.11 | 0.1 | 0.13 | 0.24 | 0.3 | 0.23 | 0.15 | 0.2 | [Cooling Capacity] | [Cooling Efficiency Default] | [Cooling Efficiency EER Lookup] | [17 empty] | 14% | 99% | 96% | [7 empty] | 6 poles | Open | 1.5 | 6 polesOpen1.5 | 87.5%
Warehouse - Refrigerated | 0.5 | 0.47 | 0.45 | 0.48 | 0.52 | 0.53 | 0.51 | 0.48 | 0.51 | < 65000 | 13 | 11.3 | [17 empty] | 13% | 100% | 97% | [7 empty] | 6 poles | Open | 2 | 6 polesOpen2 | 88.5%
[10 empty] | ≥ 65000 and < 135000 | 11.2 | 11 | [17 empty] | 12% | 100% | 97% | [7 empty] | 6 poles | Open | 3 | 6 polesOpen3 | 89.5%
[10 empty] | ≥ 135000 and < 240000 | 10.7 | 10.6 | [17 empty] | 11% | 100% | 98% | [7 empty] | 6 poles | Open | 5 | 6 polesOpen5 | 89.5%
ROOM AC CEER/EER | [9 empty] | = 240000 | 9.6 | 9.5 | [17 empty] | 10% | 100% | 98% | [7 empty] | 6 poles | Open | 7.5 | 6 polesOpen7.5 | 91%
System Type | Capacity | Concatenate | CEER base | EER base | [25 empty] | 9% | 100% | 98% | [7 empty] | 6 poles | Open | 10 | 6 polesOpen10 | 91%
Room Air Conditioners With Louvered Sides | < 6000 | Room Air Conditioners With Louvered Sides< 6000 | 11 | 11.2 | [5 empty] | Eff for HP | [19 empty] | 8% | 100% | 99% | [7 empty] | 6 poles | Open | 15 | 6 polesOpen15 | 91.7%
Room Air Conditioners With Louvered Sides | ≥ 6000 and < 8000 | Room Air Conditioners With Louvered Sides≥ 6000 and < 8000 | 11 | 11.2 | [5 empty] | [Heating Capacity] | [Heating Efficiency Default] | [18 empty] | 7% | 100% | 99% | [7 empty] | 6 poles | Open | 20 | 6 polesOpen20 | 91.7%
Room Air Conditioners With Louvered Sides | ≥ 8000 and < 11000 | Room Air Conditioners With Louvered Sides≥ 8000 and < 11000 | 10.9 | 11.3 | [5 empty] | < 65000 | 7.7 | [18 empty] | 6% | 100% | 99% | [7 empty] | 8 poles | Enclosed | 1 | 8 polesEnclosed1 | 82%
Room Air Conditioners With Louvered Sides | ≥ 11000 and < 14000 | Room Air Conditioners With Louvered Sides≥ 11000 and < 14000 | 10.9 | 11.3 | [5 empty] | ≥ 65000 and < 135000 | 3.3 | [18 empty] | 5% | 100% | 100% | [7 empty] | 8 poles | Enclosed | 1.5 | 8 polesEnclosed1.5 | 86.5%
Room Air Conditioners With Louvered Sides | ≥ 14000 and < 20000 | Room Air Conditioners With Louvered Sides≥ 14000 and < 20000 | 10.7 | 11.2 | [5 empty] | ≥ 135000 and < 240000 | 3.2 | [18 empty] | 4% | 100% | 100% | [7 empty] | 8 poles | Enclosed | 2 | 8 polesEnclosed2 | 87.5%
Room Air Conditioners With Louvered Sides | ≥ 20000 and < 25000 | Room Air Conditioners With Louvered Sides≥ 20000 and < 25000 | 9.4 | 9.8 | [5 empty] | = 240000 | 3.2 | [18 empty] | 3% | 100% | 100% | [7 empty] | 8 poles | Enclosed | 3 | 8 polesEnclosed3 | 88.5%
Room Air Conditioners With Louvered Sides | ≥ 25000 | Room Air Conditioners With Louvered Sides≥ 25000 | 9 | 9.8 | [25 empty] | 2% | 100% | 100% | [7 empty] | 8 poles | Enclosed | 5 | 8 polesEnclosed5 | 89.5%
Room Air Conditioners Without Louvered Sides | < 6000 | Room Air Conditioners Without Louvered Sides< 6000 | 10 | 10.4 | [25 empty] | 1% | 100% | 100% | [7 empty] | 8 poles | Enclosed | 7.5 | 8 polesEnclosed7.5 | 90.2%
Room Air Conditioners Without Louvered Sides | ≥ 6000 and < 8000 | Room Air Conditioners Without Louvered Sides≥ 6000 and < 8000 | 10 | 10.4 | [25 empty] | 0% | 100% | 100% | [7 empty] | 8 poles | Enclosed | 10 | 8 polesEnclosed10 | 91.7%
Room Air Conditioners Without Louvered Sides | ≥ 8000 and < 11000 | Room Air Conditioners Without Louvered Sides≥ 8000 and < 11000 | 9.6 | 9.8 | [25 empty] | -1% | 100% | 100% | [7 empty] | 8 poles | Enclosed | 15 | 8 polesEnclosed15 | 91.7%
Room Air Conditioners Without Louvered Sides | ≥ 11000 and < 14000 | Room Air Conditioners Without Louvered Sides≥ 11000 and < 14000 | 9.5 | 9.8 | [25 empty] | -2% | 100% | 100% | [7 empty] | 8 poles | Enclosed | 20 | 8 polesEnclosed20 | 92.4%
Room Air Conditioners Without Louvered Sides | ≥ 14000 and < 20000 | Room Air Conditioners Without Louvered Sides≥ 14000 and < 20000 | 9.3 | 9.8 | [25 empty] | -3% | 100% | 100% | [7 empty] | 8 poles | Open | 1 | 8 polesOpen1 | 75.5%
Room Air Conditioners Without Louvered Sides | ≥ 20000 and < 25000 | Room Air Conditioners Without Louvered Sides≥ 20000 and < 25000 | 9.4 | 9.8 | [25 empty] | -4% | 100% | 100% | [7 empty] | 8 poles | Open | 1.5 | 8 polesOpen1.5 | 78.5%
Room Air Conditioners Without Louvered Sides | ≥ 25000 | Room Air Conditioners Without Louvered Sides≥ 25000 | 9.4 | 9.8 | [25 empty] | -5% | 100% | 99% | [7 empty] | 8 poles | Open | 2 | 8 polesOpen2 | 84%
Reverse Cycle Room Air Conditioners with Louvered Sides | < 6000 | Reverse Cycle Room Air Conditioners with Louvered Sides< 6000 | 9.8 | 10.4 | [25 empty] | -6% | 100% | 99% | [7 empty] | 8 poles | Open | 3 | 8 polesOpen3 | 85.5%
Reverse Cycle Room Air Conditioners with Louvered Sides | ≥ 6000 and < 8000 | Reverse Cycle Room Air Conditioners with Louvered Sides≥ 6000 and < 8000 | 9.8 | 10.4 | [25 empty] | -7% | 99% | 99% | [7 empty] | 8 poles | Open | 5 | 8 polesOpen5 | 86.5%
Reverse Cycle Room Air Conditioners with Louvered Sides | ≥ 8000 and < 11000 | Reverse Cycle Room Air Conditioners with Louvered Sides≥ 8000 and < 11000 | 9.8 | 10.4 | [25 empty] | -8% | 99% | 99% | [5 empty] | 8 poles | Open | 7.5 | 8 polesOpen7.5 | 86.5%
Reverse Cycle Room Air Conditioners with Louvered Sides | ≥ 11000 and < 14000 | Reverse Cycle Room Air Conditioners with Louvered Sides≥ 11000 and < 14000 | 9.8 | 10.4 | [25 empty] | -9% | 99% | 98% | [5 empty] | 8 poles | Open | 10 | 8 polesOpen10 | 89.5%
Reverse Cycle Room Air Conditioners with Louvered Sides | ≥ 14000 and < 20000 | Reverse Cycle Room Air Conditioners with Louvered Sides≥ 14000 and < 20000 | 9.8 | 10.4 | [25 empty] | -10% | 99% | 98% | [5 empty] | 8 poles | Open | 15 | 8 polesOpen15 | 89.5%
Reverse Cycle Room Air Conditioners with Louvered Sides | ≥ 20000 and < 25000 | Reverse Cycle Room Air Conditioners with Louvered Sides≥ 20000 and < 25000 | 9.3 | 9.8 | [25 empty] | -11% | 99% | 97% | [5 empty] | 8 poles | Open | 20 | 8 polesOpen20 | 90.2%
Reverse Cycle Room Air Conditioners with Louvered Sides | ≥ 25000 | Reverse Cycle Room Air Conditioners with Louvered Sides≥ 25000 | 9.3 | 9.8 | [25 empty] | -12% | 99% | 97%
Reverse Cycle Room Air Conditioners without Louvered Sides | < 6000 | Reverse Cycle Room Air Conditioners without Louvered Sides< 6000 | 9.3 | 9.8 | [25 empty] | -13% | 99% | 96%
Reverse Cycle Room Air Conditioners without Louvered Sides | ≥ 6000 and < 8000 | Reverse Cycle Room Air Conditioners without Louvered Sides≥ 6000 and < 8000 | 9.3 | 9.8 | [25 empty] | -14% | 98% | 96%
Reverse Cycle Room Air Conditioners without Louvered Sides | ≥ 8000 and < 11000 | Reverse Cycle Room Air Conditioners without Louvered Sides≥ 8000 and < 11000 | 9.3 | 9.8 | [25 empty] | -15% | 98% | 95%
Reverse Cycle Room Air Conditioners without Louvered Sides | ≥ 11000 and < 14000 | Reverse Cycle Room Air Conditioners without Louvered Sides≥ 11000 and < 14000 | 9.3 | 9.8 | [25 empty] | -16% | 98% | 95%
Reverse Cycle Room Air Conditioners without Louvered Sides | ≥ 14000 and < 20000 | Reverse Cycle Room Air Conditioners without Louvered Sides≥ 14000 and < 20000 | 8.7 | 9.2 | [25 empty] | -17% | 98% | 94%
Reverse Cycle Room Air Conditioners without Louvered Sides | ≥ 20000 and < 25000 | Reverse Cycle Room Air Conditioners without Louvered Sides≥ 20000 and < 25000 | 8.7 | 9.2 | [25 empty] | -18% | 98% | 93%
Reverse Cycle Room Air Conditioners without Louvered Sides | ≥ 25000 | Reverse Cycle Room Air Conditioners without Louvered Sides≥ 25000 | 8.7 | 9.2 | [25 empty] | -19% | 98% | 93%
Casement-Only Room Air Conditioners | < 6000 | Casement-Only Room Air Conditioners< 6000 | 9.5 | 10 | [25 empty] | -20% | 97% | 92%
Casement-Only Room Air Conditioners | ≥ 6000 and < 8000 | Casement-Only Room Air Conditioners≥ 6000 and < 8000 | 9.5 | 10 | [25 empty] | -21% | 97% | 91%
Casement-Only Room Air Conditioners | ≥ 8000 and < 11000 | Casement-Only Room Air Conditioners≥ 8000 and < 11000 | 9.5 | 10 | [25 empty] | -22% | 97% | 90%
Casement-Only Room Air Conditioners | ≥ 11000 and < 14000 | Casement-Only Room Air Conditioners≥ 11000 and < 14000 | 9.5 | 10 | [25 empty] | -23% | 97% | 90%
Casement-Only Room Air Conditioners | ≥ 14000 and < 20000 | Casement-Only Room Air Conditioners≥ 14000 and < 20000 | 9.5 | 10 | [25 empty] | -24% | 97% | 89%
Casement-Only Room Air Conditioners | ≥ 20000 and < 25000 | Casement-Only Room Air Conditioners≥ 20000 and < 25000 | 9.5 | 10 | [25 empty] | -25% | 96% | 88%
Casement-Only Room Air Conditioners | ≥ 25000 | Casement-Only Room Air Conditioners≥ 25000 | 9.5 | 10 | [25 empty] | -26% | 96% | 87%
Casement-Slider Room Air Conditioners | < 6000 | Casement-Slider Room Air Conditioners< 6000 | 10.4 | 10.9 | [25 empty] | -27% | 96% | 86%
Casement-Slider Room Air Conditioners | ≥ 6000 and < 8000 | Casement-Slider Room Air Conditioners≥ 6000 and < 8000 | 10.4 | 10.9 | [25 empty] | -28% | 96% | 85%
Casement-Slider Room Air Conditioners | ≥ 8000 and < 11000 | Casement-Slider Room Air Conditioners≥ 8000 and < 11000 | 10.4 | 10.9 | [25 empty] | -29% | 95% | 84%
Casement-Slider Room Air Conditioners | ≥ 11000 and < 14000 | Casement-Slider Room Air Conditioners≥ 11000 and < 14000 | 10.4 | 10.9 | [25 empty] | -30% | 95% | 83%
Casement-Slider Room Air Conditioners | ≥ 14000 and < 20000 | Casement-Slider Room Air Conditioners≥ 14000 and < 20000 | 10.4 | 10.9 | [25 empty] | -31% | 95% | 82%
Casement-Slider Room Air Conditioners | ≥ 20000 and < 25000 | Casement-Slider Room Air Conditioners≥ 20000 and < 25000 | 10.4 | 10.9 | [25 empty] | -32% | 95% | 81%
Casement-Slider Room Air Conditioners | ≥ 25000 | Casement-Slider Room Air Conditioners≥ 25000 | 10.4 | 10.9 | [25 empty] | -33% | 95% | 80%
[30 empty] | -34% | 94% | 78%
COMPUTER ROOM AC SCOP | [29 empty] | -35% | 94% | 77%
System Type | Flow Direction | Concatenate | Capacity | SCOP
Computer Room Air Conditioner Air Cooled | Upflow | Computer Room Air Conditioner Air Cooled Upflow <65,000 BTU/hr | <65,000 BTU/hr | 2.09
Computer Room Air Conditioner Air Cooled | Upflow | Computer Room Air Conditioner Air Cooled Upflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 1.99
Computer Room Air Conditioner Air Cooled | Upflow | Computer Room Air Conditioner Air Cooled Upflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 1.79
Computer Room Air Conditioner Air Cooled | Downflow | Computer Room Air Conditioner Air Cooled Downflow <65,000 BTU/hr | <65,000 BTU/hr | 2.2
Computer Room Air Conditioner Air Cooled | Downflow | Computer Room Air Conditioner Air Cooled Downflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.1
Computer Room Air Conditioner Air Cooled | Downflow | Computer Room Air Conditioner Air Cooled Downflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 1.9
Computer Room Air Conditioner Water Cooled | Upflow | Computer Room Air Conditioner Water Cooled Upflow <65,000 BTU/hr | <65,000 BTU/hr | 2.49
Computer Room Air Conditioner Water Cooled | Upflow | Computer Room Air Conditioner Water Cooled Upflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.39
Computer Room Air Conditioner Water Cooled | Upflow | Computer Room Air Conditioner Water Cooled Upflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.29
Computer Room Air Conditioner Water Cooled | Downflow | Computer Room Air Conditioner Water Cooled Downflow <65,000 BTU/hr | <65,000 BTU/hr | 2.6
Computer Room Air Conditioner Water Cooled | Downflow | Computer Room Air Conditioner Water Cooled Downflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.5
Computer Room Air Conditioner Water Cooled | Downflow | Computer Room Air Conditioner Water Cooled Downflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.4
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Upflow <65,000 BTU/hr | <65,000 BTU/hr | 2.44
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Upflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.34
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Upflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.24
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Downflow <65,000 BTU/hr | <65,000 BTU/hr | 2.55
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Downflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.45
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Water Cooled with Fluid Economizer Downflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.35
Computer Room Air Conditioner Glycol Cooled | Upflow | Computer Room Air Conditioner Glycol Cooled Upflow <65,000 BTU/hr | <65,000 BTU/hr | 2.39
Computer Room Air Conditioner Glycol Cooled | Upflow | Computer Room Air Conditioner Glycol Cooled Upflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.04
Computer Room Air Conditioner Glycol Cooled | Upflow | Computer Room Air Conditioner Glycol Cooled Upflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 1.99
Computer Room Air Conditioner Glycol Cooled | Downflow | Computer Room Air Conditioner Glycol Cooled Downflow <65,000 BTU/hr | <65,000 BTU/hr | 2.5
Computer Room Air Conditioner Glycol Cooled | Downflow | Computer Room Air Conditioner Glycol Cooled Downflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.15
Computer Room Air Conditioner Glycol Cooled | Downflow | Computer Room Air Conditioner Glycol Cooled Downflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.1
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Upflow <65,000 BTU/hr | <65,000 BTU/hr | 2.34
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Upflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 1.99
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Upflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Upflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 1.94
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Downflow <65,000 BTU/hr | <65,000 BTU/hr | 2.45
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Downflow >= 65,000 Btu/hr and <240,000 Btu/hr | >= 65,000 Btu/hr and <240,000 Btu/hr | 2.1
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Downflow | Computer Room Air Conditioner Glycol Cooled with Fluid Economizer Downflow >= 240,000 Btu/hr | >= 240,000 Btu/hr | 2.05
High Volume Low Speed Fan Hours of Use
Location
Allentown | 2459
Binghamton | 1526
Bradford | 1340
Erie | 2124
Harrisburg | 2718
Philadelphia | 2914
Pittsburgh | 2296
Scranton | 2154
Williamsport | 2371
Note on AZ4: Priyam Parikh: Not in TRM

## Calculations (hidden)
-0.21
-0.22
| HVAC Calculations | [21 empty] | -0.23
NC_Cooling kWh Baseline Efficiency
| EFLH_Cool_Default | EFLH_heat_Default | CF_Default | IEER | EER | SEER | COP | HSPF | Cooling kWh Baseline Efficiency | Cooling kWh Proposed Efficiency | Heating kWh Baseline Efficiency | Heating kWh Proposed Efficiency | kW Baseline Efficiency | kW Proposed Efficiency | Existing Cooling kWh | Existing heating kWh | Existing Total kWh | Existing Total kW | Proposed Cooling kWh | Proposed Heating kWh | Proposed Total kWh | Proposed Total kW | [6 empty] | -0.25
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | [8 empty] | -0.26
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | [8 empty] | -0.27
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | [8 empty] | -0.28
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | [8 empty] | -0.29
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | [8 empty] | -0.3
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | [8 empty] | -0.31
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | [8 empty] | -0.32
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | [8 empty] | -0.33
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | [8 empty] | -0.34
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 | [8 empty] | -0.35
HVAC - NC Baseline Savings
| NC_Cooling kWh Baseline Efficiency | NC_Heating kWh baseline Efficiency | NC_kW Baseline Efficiency | NC_Baseline Cooling kWh Consumption | NC_Baseline Heating kWh Consumption | NC_Baseline Total kWh Consumption | NC_Baseline kW Consumption | NC_kWh Savings | NC_kW Savings
| 10.809 | 3.018 | 10.809 | 556.9433 | 1048.8068 | 1605.7501 | 0.27755 | -378.2327 | 0.077546
| 10.809 | 3.018 | 10.809 | 556.9433 | 1048.8068 | 1605.7501 | 0.27755 | -378.2327 | 0.077546
| 10.809 | 3.018 | 10.809 | 556.9433 | 1048.8068 | 1605.7501 | 0.27755 | -378.2327 | 0.077546
| 10.809 | 3.018 | 10.809 | 556.9433 | 1048.8068 | 1605.7501 | 0.27755 | -378.2327 | 0.077546
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
[5 empty] | 0 | 0 |  | #VALUE! | #VALUE!
Lifetime Savings
| Life of Equipment | Early Replacement Savings (kWh) | Early Replacement Savings (kW) | Remaining Useful Life | New Construction Savings (kWh) | New Construction Savings (kW) | Number of Years | Lifetime Savings (kWh) | Lifetime Savings (kW)
| 15 |  |  | 0 | -378.2327 | 0.077546 | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | -378.2327 | 0.077546 | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | -378.2327 | 0.077546 | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | -378.2327 | 0.077546 | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | #VALUE!
Chillers Calculations
| Default Cooling EFLH | Default CF | IPLV | kW/ton | EER | Baseline kWh Eff | Proposed kWh Eff | Baseline kW Eff | Proposed kW Eff | Existing Total kWh | Existing Total kW | Proposed Total kWh | Proposed Total kW
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
HVAC - NC Baseline Savings
| NC_Cooling kWh Baseline Efficiency | NC_Heating kWh baseline Efficiency | NC_Baseline kWh Consumption | NC_Baseline kW Consumption | NC_kWh Savings | NC_kW Savings
Lifetime Savings
| Life of Equipment | Early Replacement Savings (kWh) | Early Replacement Savings (kW) | Remaining Useful Life | New Construction Savings (kWh) | New Construction Savings (kW) | Number of Years | Lifetime Savings (kWh) | Lifetime Savings (kW)
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
| 15 | 0 | 0 | 0 |  |  | 15 | #VALUE! | #VALUE!
#N/A
Geothermal Calculations
Efficiencies Used
| EFLH_Cooling_Default | EFLH_heat_Default | CF_Default | Default Motor Load Factor | Proposed Pump Efficiency_Default | Baseline Pump Efficiency_Default | Assumed Equipment Type | Assumed Electric Resistance Existence | IEER | EER | SEER | COP | HSPF | IEER | EER | SEER | COP | HSPF | Cooling kWh Baseline | Cooling kWh Proposed | Heating kWh Baseline | Heated kWh Proposed | Motor kWh Baseline | Motor kWh Proposed | Cooling kW Baseline | Cooling kW Proposed | Motor kW Baseline | Motor kW Proposed
|  |  |  | 0.75 |  |  | 0 | Yes | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | 0 | 0
|  |  |  | 0.75 |  |  | 0 | Yes | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | 0 | 0
|  |  |  | 0.75 |  |  | 0 | Yes | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | 0 | 0
|  |  |  | 0.75 |  |  | 0 | Yes | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | 0 | 0
|  |  |  | 0.75 |  |  | 0 | Yes | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | 0 | 0
|  |  |  | 0.75 |  |  | 0 | Yes | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | 0 | 0
|  |  |  | 0.75 |  |  | 0 | Yes | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | 0 | 0
|  |  |  | 0.75 |  |  | 0 | Yes | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | 0 | 0
|  |  |  | 0.75 |  |  | 0 | Yes | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | 0 | 0
|  |  |  | 0.75 |  |  | 0 | Yes | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | 0 | 0
Geothermal - NC Baseline Savings
| NC_Cooling kWh Baseline Efficiency | NC_Heating kWh Baseline Efficiency | NC_kW Baseline Efficiency | NC_Motor Efficiency | NC_Pump Efficiency | NC_Baseline Cooling kWh Consumption | NC_Baseline Heating kWh Consumption | NC_Baseline Motor kWh Consumption | NC_Total kWh Consumption | NC_Baseline Cooling kW | NC_Baseline Motor kW | NC_Baseline Total kW | NC_kWh Savings | NC_kW Savings
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | IEER: #VALUE!; EER: #VALUE!; SEER: 0; HSPF: #VALUE!; Efficiencies Used IEER: #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | IEER: #VALUE!; EER: #VALUE!; SEER: 0; HSPF: #VALUE!; Efficiencies Used IEER: #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | IEER: #VALUE!; EER: #VALUE!; SEER: 0; HSPF: #VALUE!; Efficiencies Used IEER: #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | IEER: #VALUE!; EER: #VALUE!; SEER: 0; HSPF: #VALUE!; Efficiencies Used IEER: #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | IEER: #VALUE!; EER: #VALUE!; SEER: 0; HSPF: #VALUE!; Efficiencies Used IEER: #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | IEER: #VALUE!; EER: #VALUE!; SEER: 0; HSPF: #VALUE!; Efficiencies Used IEER: #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | IEER: #VALUE!; EER: #VALUE!; SEER: 0; HSPF: #VALUE!; Efficiencies Used IEER: #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | IEER: #VALUE!; EER: #VALUE!; SEER: 0; HSPF: #VALUE!; Efficiencies Used IEER: #VALUE!
[5 empty] | 0 | #VALUE! | #VALUE! | 0 | IEER: #VALUE!; EER: #VALUE!; SEER: 0; HSPF: #VALUE!; Efficiencies Used IEER: #VALUE!
Lifetime Savings
| Life of Equipment | Early Replacement Savings (kWh) | Early Replacement Savings (kW) | Remaining Useful Life | New Construction Savings (kWh) | New Construction Savings (kW) | Number of Years | Lifetime Savings (kWh) | IEER: Lifetime Savings (kW)
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
Ductless Mini Split Calculations
| Default Cooling EFLH | Default CF | CF_Default | EER | SEER | COP | HSPF | Cooling kWh Baseline Efficiency | IEER: Cooling kWh Proposed Efficiency; EER: Heating kWh Baseline Efficiency; SEER: Heating kWh Proposed Efficiency; COP: kW Baseline Efficiency; HSPF: kW Proposed Efficiency
[9 empty] | 0 |  | 0 |  | 0
[9 empty] | 0 | 0 | 0 |  | 0
[9 empty] | 0 | 0 | 0 |  | 0
[9 empty] | 0 | 0 | 0 |  | 0
[9 empty] | 0 | 0 | 0 |  | 0
[9 empty] | 0 | 0 | 0 |  | 0
[9 empty] | 0 | 0 | 0 |  | 0
[9 empty] | 0 | 0 | 0 |  | 0
[9 empty] | 0 | 0 | 0 |  | 0
[9 empty] | 0 | 0 | 0 |  | 0
Calculations
| Cooling kWh Baseline | Heating kWh Baseline | Total kWh Baseline | kW Baseline | Cooling kWh Proposed | Heating kWh Proposed | Total kWh Proposed | kW Proposed
Fuel Switching Calculations
| Facility Defaults |  | Baseline Efficiency |  |  | Efficiencies Used | Calculations |  | IEER: NC Baseline Savings Calculations
| EFLH_heat_Default | CF_Default | COP | HSPF | AFUE | Heating kWh Baseline Efficiency | Annual kWh Savings | Fuel Consumption Increase | IEER: NC_Heating kWh Baseline Efficiency; EER: NC_Baseline kWh Consumption
|  |  | 1 | NA |  | #REF! |  | #VALUE! | IEER: 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | IEER: 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | IEER: 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | IEER: 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | IEER: 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | IEER: 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | IEER: 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | IEER: 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | IEER: 3.412
|  |  | 1 | NA |  | #REF! |  | #VALUE! | IEER: 3.412
Lifetime Savings
| Life of Equipment | Early Replacement Savings (kWh) | Remaining Useful Life | New Construction Savings (kWh) | Number of Years | Lifetime Savings (kWh)
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
| 20 |  | 0 |  | 20 | #VALUE!
Guest Room Occ Sensor Calculations
Calculations
| Energy Savings Factor | Demand Savings Factor | kWh Savings | kW Savings
Ref Charge Correction Calculations
| Line Item | EFLHc | CAPYc | SEER | IEER | EFLHh | CAPYh | COP | HSPF | RCF | EER | CF | kWh AC | kWh HP | kW | kWh | Incentive
| 1 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
| 2 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
| 3 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
| 4 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
| 5 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
| 6 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
| 7 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
| 8 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
| 9 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
| 10 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
Room Air Conditioning Calculations
| Line Item | EFLHc | CAPYc | Type | Concatenate | CEER base | EER base | CEER ee | EER ee | QTY | CF | kWh | kW | Incentive
| 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
| 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
| 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
| 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
| 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
| 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
| 7 |  | 0 | 0 | 0 | 0 | 0 | 0 | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
| 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
| 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
| 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
Computer Room Air Conditioning Calculations
| Line Item | EFLHc | CAPYc | Type | Concatenate | Flow | CAPYbase | SCOP base | SCOP ee | QTY | CF | kWh | kW | Incentive
| 1 |  | 0 | 0 | Computer Room Air Conditioner 0 0 <65,000 BTU/hr | 0 | <65,000 BTU/hr | #N/A | IEER: 0; EER: 0; COP: 0; HSPF: 0; Efficiencies Used IEER: 0
| 2 |  | 0 | 0 | Computer Room Air Conditioner 0 | 0 |  |  | IEER: 0; EER: 0; COP: 0; Efficiencies Used IEER: 0
| 3 |  | 0 | 0 | Computer Room Air Conditioner 0 | 0 |  |  | IEER: 0; EER: 0; COP: 0; Efficiencies Used IEER: 0
| 4 |  | 0 | 0 | Computer Room Air Conditioner 0 | 0 |  |  | IEER: 0; EER: 0; COP: 0; Efficiencies Used IEER: 0
| 5 |  | 0 | 0 | Computer Room Air Conditioner 0 | 0 |  |  | IEER: 0; EER: 0; COP: 0; Efficiencies Used IEER: 0
| 6 |  | 0 | 0 | Computer Room Air Conditioner 0 | 0 |  |  | IEER: 0; EER: 0; COP: 0; Efficiencies Used IEER: 0
| 7 |  | 0 | 0 | Computer Room Air Conditioner 0 | 0 |  |  | IEER: 0; EER: 0; COP: 0; Efficiencies Used IEER: 0
| 8 |  | 0 | 0 | Computer Room Air Conditioner 0 | 0 |  |  | IEER: 0; EER: 0; COP: 0; Efficiencies Used IEER: 0
| 9 |  | 0 | 0 | Computer Room Air Conditioner 0 | 0 |  |  | IEER: 0; EER: 0; COP: 0; Efficiencies Used IEER: 0
| 10 |  | 0 | 0 | Computer Room Air Conditioner 0 | 0 |  |  | IEER: 0; EER: 0; COP: 0; Efficiencies Used IEER: 0
Computer Room Air Conditioning ECM and VSD Calculations
| Line Item | ηbase fan | ηbase belt | ηbase motor | ηec fan | ηec drive | ηec motor | USDF | CLF | Horesepower | ηcooling | HOU | UF | Fan Power | CF | LF | Quantity | kWh ECM | kW ECM | kWh VSD | kW VSD | Incentive
| 1 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 0.6254 | 0 | 0.95 | 8760 | 83% | 0 |  |  | 0 | 0 | #VALUE! | 0 | #VALUE!
| 2 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 0.6254 | 0 | 0.95 | 8760 | 83% | 0 |  |  | 0 | 0 | #VALUE! | 0 | #VALUE!
| 3 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 0.6254 | 0 | 0.95 | 8760 | 83% | 0 |  |  | 0 | 0 | #VALUE! | 0 | #VALUE!
| 4 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 0.6254 | 0 | 0.95 | 8760 | 83% | 0 |  |  | 0 | 0 | #VALUE! | 0 | #VALUE!
| 5 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 0.6254 | 0 | 0.95 | 8760 | 83% | 0 |  |  | 0 | 0 | #VALUE! | 0 | #VALUE!
| 6 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 0.6254 | 0 | 0.95 | 8760 | 83% | 0 |  |  | 0 | 0 | #VALUE! | 0 | #VALUE!
| 7 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 0.6254 | 0 | 0.95 | 8760 | 83% | 0 |  |  | 0 | 0 | #VALUE! | 0 | #VALUE!
| 8 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 0.6254 | 0 | 0.95 | 8760 | 83% | 0 |  |  | 0 | 0 | #VALUE! | 0 | #VALUE!
| 9 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 0.6254 | 0 | 0.95 | 8760 | 83% | 0 |  |  | 0 | 0 | #VALUE! | 0 | #VALUE!
| 10 | 53.81% | 95% | 91.18% | 65.97% | 99.5% | 88.96% | 0 | 0.6254 | 0 | 0.95 | 8760 | 83% | 0 |  |  | 0 | 0 | #VALUE! | 0 | #VALUE!
| High Volume Low Speed Fans | Fans Removed | Fans Installed | Wconv | WHVLS | Wconv-WHVLS | Hours of Use | CF | IEER: Annual Savings (kWh); EER: Peak Reduction (kW); SEER: Incentive
|  | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 1 | IEER: #N/A; EER: #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 1 | IEER: #N/A; EER: #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 1 | IEER: #N/A; EER: #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 1 | IEER: #N/A; EER: #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 1 | IEER: #N/A; EER: #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 1 | IEER: #N/A; EER: #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 1 | IEER: #N/A; EER: #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 1 | IEER: #N/A; EER: #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 1 | IEER: #N/A; EER: #N/A
|  | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 1 | IEER: #N/A; EER: #N/A
Economizer Calculations
| Facility Defaults | Baseline Efficiency |  |  | Calculations
| Free Cooling Hours (FCHr) | IEER | EER | SEER | Efficiency | kWh Savings | kW Savings
1 | [6 empty] | 0
2 | [6 empty] | 0
3 | [6 empty] | 0
4 | [6 empty] | 0
5 | [6 empty] | 0
6 | [6 empty] | 0
7 | [6 empty] | 0
8 | [6 empty] | 0
9 | [6 empty] | 0
10 | [6 empty] | 0
Insulation Calculations
HVAC Baseline Efficiencies | bar: IEER
| Facility Defaults |  |  |  | Cooling Efficiency |  |  | Heating Efficiency | bar: IEER
| EFLH_cool_Default | CF_Default | CDD | HDD | IEER | EER | SEER | COP | IEER: HSPF
1
2
3
4
5
6
7
8
9
10
|  |  |  | Insulation Baseline Efficiencies |  | Insulation Efficiencies Used | bar: IEER
| HVAC Efficiencies Used |  |  | Ceiling Insulation | Wall Insulation | Ceiling Insulation | Ceiling Insulation | Wall Insulation | IEER: Wall Insulation
| Cooling kWh Baseline Efficiency | Heating kWh Baseline Efficiency | kW Baseline Efficiency | R-Value of Existing Ceiling Insulation | R-Value of Existing Wall Insulation | R-Value of Existing Ceiling Insulation | R-Value of Proposed Ceiling Insulation | R-Value of Existing Wall Insulation | IEER: R-Value of Proposed Wall Insulation
[6 empty] | 0 | 0 | 0 | IEER: 0
[6 empty] | 0 | 0 | 0 | IEER: 0
[6 empty] | 0 | 0 | 0 | IEER: 0
[6 empty] | 0 | 0 | 0 | IEER: 0
[6 empty] | 0 | 0 | 0 | IEER: 0
[6 empty] | 0 | 0 | 0 | IEER: 0
[6 empty] | 0 | 0 | 0 | IEER: 0
[6 empty] | 0 | 0 | 0 | IEER: 0
[6 empty] | 0 | 0 | 0 | IEER: 0
[6 empty] | 0 | 0 | 0 | IEER: 0
Calculations
| Existing Cooling kWh | Existing Heating kWh | Existing kWh | Existing kW | Proposed Cooling kWh | Proposed Heating kWh | Proposed kWh | Proposed kW
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE!
| NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | NC Baseline Savings Calculations | IEER: NC Baseline Savings Calculations; EER: NC Baseline Savings Calculations; SEER: NC Baseline Savings Calculations
| NC_Cooling kWh Baseline Efficiency | NC_Heating kWh Baseline Efficiency | NC_kW Baseline Efficiency | NC_Ceiling R-Value | NC_Wall R-Value | NC_Baseline Cooling kWh Consumption | NC_Baseline Heating kWh Consumption | NC_Baseline Total kWh Consumption | IEER: NC_Baseline kW Consumption; EER: NC_kWh Savings; SEER: NC_kW Savings
[6 empty] | #VALUE! | 0 | #VALUE! | IEER: #VALUE!; EER: #VALUE!; SEER: #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | IEER: #VALUE!; EER: #VALUE!; SEER: #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | IEER: #VALUE!; EER: #VALUE!; SEER: #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | IEER: #VALUE!; EER: #VALUE!; SEER: #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | IEER: #VALUE!; EER: #VALUE!; SEER: #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | IEER: #VALUE!; EER: #VALUE!; SEER: #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | IEER: #VALUE!; EER: #VALUE!; SEER: #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | IEER: #VALUE!; EER: #VALUE!; SEER: #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | IEER: #VALUE!; EER: #VALUE!; SEER: #VALUE!
[6 empty] | #VALUE! | 0 | #VALUE! | IEER: #VALUE!; EER: #VALUE!; SEER: #VALUE!
Lifetime Savings | bar: IEER
| Life of Equipment | Early Replacement Savings (kWh) | Early Replacement Savings (kW) | Remaining Useful Life | New Construction Savings (kWh) | New Construction Savings (kW) | Number of Years | Lifetime Savings (kWh) | IEER: Lifetime Savings (kW)
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!
| 15 |  |  | 0 | #VALUE! | #VALUE! | 15 | #VALUE! | IEER: #VALUE!

## Dropdowns (hidden)
Dropdowns
yBuilding_Type_HVAC | yBuilding Type_Chillers | yBuildingType_GuestRooms | yProject_Type | yEfficiencyKnown | xBuilding_Location | HVAC Equipment Type | Economizer HVAC Equipment Type | Chiller Equipment Type | Geothermal Equipment Type | yGR_EqmtType_Motel | yGR_EqmtType_Hotel | Electric Resistance? | Fuel Switching Equipment Type_Electric | Fuel Switching Equipment Type_NonElectric | PTAC/PTHP Type | yOperating_Schedule | xExpValve | yRefCharge% | yDHPBaseHeatingEquipment Type | yDHPBaseCoolingEquipment Type | yMotorSize | yMotorType | yMotorPoles | y_RACeqmttype | yRAC_options | Capcity Grouping | Capacity Grouping AC | y_Comp_Room_AC | y_Flow | y_ECM_VSD | y_Location of Fan Plug | y_Conv_Fan_Size
Education - College/University | Education - College/University | Hotel | Early Replacement | Nameplate Efficiency Values known | Allentown | Air-Source Air Conditioner | Air-Source Air Conditioner | Air Cooled Chiller | Air-Source Heat Pumps | PTAC with Electric Resistance Heat | PTAC with Electric Resistance Heat | Yes | Air-Source Heat Pumps | Gas Furnace | Standard | 1 Shift, 5 days per week | TXV | 60% | Standard Ductless Heat Pump | Standard Ductless Heat Pump | 1 | Open | 2 poles | Room Air Conditioners With Louvered Sides | Without Louvered Sides | < 65000 | < 6000 | Air Cooled | Upflow | ECM | In Unit | ≥ 16 and < 18
Education - Other | Education - Other | Motel | End of Useful Life or New Construction | Nameplate Efficiency Values NOT known | Binghamton | Air-Source Heat Pumps | Air-Source Heat Pumps | Water Cooled Chiller: Positive Displacement or Reciprocating | Water-Source Heat Pumps | PTAC with Gas Heat | PTAC with Gas Heat | No | Electric Furnace | Oil Furnace | Non Standard | 2 Shift, 5 days per week | Orifice | 59% | Electric Resistance | Central Air Conditioning | 1.5 | Enclosed | 4 poles | Room Air Conditioners Without Louvered Sides | With Louvered Sides | ≥ 65000 and < 135000 | ≥ 6000 and < 8000 | Water Cooled | Downflow | VSD | Underfloor | ≥ 18 and < 20
Grocery | Health - Hospital |  |  |  | Bradford | Water Cooled Air Conditioners | Water Cooled Air Conditioners | Water Cooled Chiller: Centrifugal | Ground Water Source Heat Pumps | PTHP | PTHP |  | Baseboard Heating | Gas/Propane Steam Boiler |  | 3 Shift, 5 days per week |  | 58% | Air-Source Heat Pump | Air-Source Heat Pump | 2 |  | 6 poles | Reverse Cycle Room Air Conditioners with Louvered Sides |  | ≥ 135000 and < 240000 | ≥ 8000 and < 11000 | Water Cooled with Fluid Economizer |  |  | If Unknown | ≥ 20 and < 24
Health - Hospital | Health - Other |  |  |  | Erie | Evaporatively Cooled Air Conditioners | Evaporatively Cooled Air Conditioners |  | Ground Source Heat Pumps |  | Central HW Fan Coil with Electric Resistance Heat |  | PTHP | Gas/Propane Hot Water Boiler |  | 24/7 |  | 57% | Electric Furnace | Room Air Conditoner | 3 |  | 8 poles | Reverse Cycle Room Air Conditioners without Louvered Sides |  | = 240000 | ≥ 11000 and < 14000 | Glycol Cooled |  |  |  | ≥ 24
Health - Other | Industrial Manufacturing |  |  |  | Harrisburg | PTAC |  |  | Other |  | Central HW Fan Coil with Gas Heat |  |  | Oil Steam Boiler |  |  |  | 56% | PTHP | PTAC | 5 |  |  | Casement-Only Room Air Conditioners |  |  | ≥ 14000 and < 20000 | Glycol Cooled with Fluid Economizer
Industrial Manufacturing | Lodging |  |  |  | Philadelphia | PTHP | [7 empty] | Oil Hot Water Boiler |  |  |  | 55% | New Space/No existing heat/Non-electric Heat | PTHP | 7.5 |  |  | Casement-Slider Room Air Conditioners |  |  | ≥ 20000 and < 25000
Institutional/Public Service | Office |  |  |  | Pittsburgh | [12 empty] | 54% |  | New Space/No existing cooling | 10 | [5 empty] | ≥ 25000
Lodging | Retail |  |  |  | Scranton | [12 empty] | 53% |  |  | 15
Multifamily (Common Areas) |  |  |  |  | Williamsport | [12 empty] | 52% |  |  | 20
Office | [17 empty] | 51% |  |  | Other
Restaurant | [17 empty] | 50%
Retail | [17 empty] | 49%
Warehouse - Other | [17 empty] | 48%
Warehouse - Refrigerated | [17 empty] | 47%
46%
45%
44%
43%
42%
41%
40%
39%
38%
37%
List References: Guest Room Occ Sensor, Geothermal | [17 empty] | 36%
Hotel | yGR_EqmtType_Hotel | [16 empty] | 35%
Motel | yGR_EqmtType_Motel | [16 empty] | 34%
End of Useful Life | yGeothermal_EOL_Eqpt | [16 empty] | 33%
Early Replacement | yGeothermal_Retro_Eqpt | [16 empty] | 32%
New Construction | yGeothermal_NC_Eqpt | [16 empty] | 31%
30%
29%
Incentives | [17 empty] | 28%
Custom Lite Incentive | 0.06 | [16 empty] | 27%
Prescriptive Incentive | 0.05 | [16 empty] | 26%
25%
24%
23%
22%
21%
20%
19%
18%
17%
16%
15%
14%
13%
12%
11%
10%
9%
8%
7%
6%
5%
4%
3%
2%
1%
0%
-1%
-2%
-3%
-4%
-5%
-6%
-7%
-8%
-9%
-10%
-11%
-12%
-13%
-14%
-15%
-16%
-17%
-18%
-19%
-20%
-21%
-22%
-23%
-24%
-25%
-26%
-27%
-28%
-29%
-30%
-31%
-32%
-33%
-34%
-35%

## Efficiency Tables (hidden)
Efficiency Tables
yChiller_Type | Fixed or Variable Speed | Chiller Capacity (Tons) | yChiller_MinCapacity | yChiller_MaxCapacity | yIPLV_base | ykWperton_base | yChiller_EER_base
Air Cooled Chiller | Fixed Speed | <150 tons | 0 | 150 | 13.7 |  | 10.1
Air Cooled Chiller | Fixed Speed | >= 150 tons | 150 | 10000 | 14 |  | 10.1
Water Cooled Chiller: Positive Displacement or Reciprocating | Fixed Speed | <75 tons | 0 | 75 | 0.6 | 0.75
Water Cooled Chiller: Positive Displacement or Reciprocating | Fixed Speed | >=75 and <150 tons | 75 | 150 | 0.56 | 0.72
Water Cooled Chiller: Positive Displacement or Reciprocating | Fixed Speed | >=150 and <300 tons | 150 | 300 | 0.54 | 0.66
Water Cooled Chiller: Positive Displacement or Reciprocating | Fixed Speed | >=300 tons | 300 | 10000 | 0.52 | 0.61
Water Cooled Chiller: Centrifugal | Fixed Speed | <300 tons | 0 | 300 | 0.55 | 0.61
Water Cooled Chiller: Centrifugal | Fixed Speed | >=300 and <600 tons | 300 | 600 | 0.52 | 0.56
Water Cooled Chiller: Centrifugal | Fixed Speed | >=600 tons | 600 | 10000 | 0.5 | 0.56
Air Cooled Chiller | Variable Speed | <150 tons | 0 | 150 | 13.7 |  | 10.1
Air Cooled Chiller | Variable Speed | >= 150 tons | 150 | 10000 | 14 |  | 10.1
Water Cooled Chiller: Positive Displacement or Reciprocating | Variable Speed | <75 tons | 0 | 75 | 0.6 | 0.75
Water Cooled Chiller: Positive Displacement or Reciprocating | Variable Speed | >=75 and <150 tons | 75 | 150 | 0.56 | 0.72
Water Cooled Chiller: Positive Displacement or Reciprocating | Variable Speed | >=150 and <300 tons | 150 | 300 | 0.54 | 0.66
Water Cooled Chiller: Positive Displacement or Reciprocating | Variable Speed | >=300 tons | 300 | 10000 | 0.52 | 0.61
Water Cooled Chiller: Centrifugal | Variable Speed | <300 tons | 0 | 300 | 0.55 | 0.61
Water Cooled Chiller: Centrifugal | Variable Speed | >=300 and <600 tons | 300 | 600 | 0.52 | 0.56
Water Cooled Chiller: Centrifugal | Variable Speed | >=600 tons | 600 | 10000 | 0.5 | 0.56
yHVAC_Type | yER_Existence | Installed Rated Cooling Capacity (Btu/hr) | yHVAC_MinCapacity | yHVAC_MaxCapacity | yIEER_base | yEER_base | ySEER_base | yCOP_base | yHSPF_base
Air-Source Air Conditioner | Yes | <65,000 BTU/hr | 0 | 65000 |  | 11.3 | 13
Air-Source Air Conditioner | Yes | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 12.9 | 11.2
Air-Source Air Conditioner | Yes | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 12.4 | 11
Air-Source Air Conditioner | Yes | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 11.6 | 10
Air-Source Air Conditioner | Yes | >= 760,000 Btu/hr | 760000 | 100000000 | 11.2 | 9.7
Air-Source Air Conditioner | No | <65,000 BTU/hr | 0 | 65000 |  | 11.3 | 13
Air-Source Air Conditioner | No | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 11.2 | 11
Air-Source Air Conditioner | No | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 11 | 10.8
Air-Source Air Conditioner | No | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 9.9 | 9.8
Air-Source Air Conditioner | No | >= 760,000 Btu/hr | 760000 | 100000000 | 9.6 | 6.5
Air-Source Heat Pumps | Yes | <65,000 BTU/hr | 0 | 65000 |  | 11.3 | 14 |  | 8.2
Air-Source Heat Pumps | Yes | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 12.2 | 11 |  | 3.3
Air-Source Heat Pumps | Yes | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 11.6 | 10.6 |  | 3.2
Air-Source Heat Pumps | Yes | >= 240,000 Btu/hr | 240000 | 100000000 | 10.6 | 9.5 |  | 3.2
Air-Source Heat Pumps | No | <65,000 BTU/hr | 0 | 65000 |  | 12.1692 | 14 |  | 8.2
Air-Source Heat Pumps | No | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 11 | 10.8 |  | 3.3
Air-Source Heat Pumps | No | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 12.2 | 10.4 |  | 3.2
Air-Source Heat Pumps | No | >= 240,000 Btu/hr | 240000 | 100000000 | 11.6 | 9.3 |  | 3.2
Water Cooled Air Conditioners | Yes | < 65,000 Btu/hr | 0 | 65000 | 12.3 | 12.1
Water Cooled Air Conditioners | Yes | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 13.9 | 12.1
Water Cooled Air Conditioners | Yes | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 13.9 | 12.5
Water Cooled Air Conditioners | Yes | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 13.6 | 12.4
Water Cooled Air Conditioners | Yes | >= 760,000 Btu/hr | 760000 | 100000000 | 13.5 | 12.2
Water Cooled Air Conditioners | No | < 65,000 Btu/hr | 0 | 65000 | 12.3 | 12.1
Water Cooled Air Conditioners | No | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 12.1 | 11.9
Water Cooled Air Conditioners | No | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 12.5 | 12.3
Water Cooled Air Conditioners | No | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 12.4 | 12.2
Water Cooled Air Conditioners | No | >= 760,000 Btu/hr | 760000 | 100000000 | 10.9 | 12
Evaporatively Cooled Air Conditioners | Yes | < 65,000 Btu/hr | 0 | 65000 | 12.3 | 12.1
Evaporatively Cooled Air Conditioners | Yes | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 12.3 | 12.1
Evaporatively Cooled Air Conditioners | Yes | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 12.2 | 12
Evaporatively Cooled Air Conditioners | Yes | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 12.1 | 11.9
Evaporatively Cooled Air Conditioners | Yes | >= 760,000 Btu/hr | 760000 | 100000000 | 11.1 | 11.7
Evaporatively Cooled Air Conditioners | No | < 65,000 Btu/hr | 0 | 65000 | 12.3 | 12.1
Evaporatively Cooled Air Conditioners | No | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 12.3 | 12.1
Evaporatively Cooled Air Conditioners | No | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 12.2 | 12
Evaporatively Cooled Air Conditioners | No | >= 240,000 Btu/hr and < 760,000 Btu/hr | 240000 | 760000 | 12.1 | 11.9
Evaporatively Cooled Air Conditioners | No |  | 760000 | 100000000 | 11.9 | 11.7
PTAC/PTHP | Std/Non-Std | yEER_PT_a | yEER_PT_b | yCOP_PT_a | yCOP_PT_b
PTAC | Non Standard | 10.9 | 0.213 | NA | NA
PTAC | Standard | 14 | 0.3 | NA | NA
PTHP | Non Standard | 10.8 | 0.213 | 2.9 | 0.026
PTHP | Standard | 14 | 0.3 | 3.2 | 0.026
DHP Heating Baseline | yHSPF_DHPbase
Standard Ductless Heat Pump | 8.2
Electric Resistance | 3.412
Air-Source Heat Pump | 8.2
Electric Furnace | 3.241
New Space/No existing heat/Non-electric Heat | 3.412
PTHP - Standard
PTHP - Non Standard
DHP Cooling Baseline | ySEER_DHPbase | yEER_DHPbase
Standard Ductless Heat Pump | 14 | 12.1692
Central Air Conditioning | 14 | 12.1692
Air-Source Heat Pump | 14 | 12.1692
Room Air Conditoner | 11.3 | 9.8223
New Space/No existing cooling | 11.3 | 9.8223
PTAC - Standard |  | 0
PTAC - Non Standard |  | 0
PTHP - Standard |  | 0
PTHP - Non Standard |  | 0
|  | Installed Capacity | Min | Max | COP | HSPF
Air-Source Heat Pumps |  | <65,000 BTU/hr | 0 | 65000 | NA | 7.7
Air-Source Heat Pumps |  | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 3.3
Air-Source Heat Pumps |  | >= 135,000 Btu/hr | 135000 | 100000000 | 3.2
Electric Furnace/Baseboard Heating |  | All Sizes |  |  | 1
|  | All Sizes |  |  | 1
yGeothermal_EqptType | yER_Existence | Installed Rated Cooling Capacity (Btu/hr) | yHVAC_MinCapacity | yHVAC_MaxCapacity | yIEER_base | yEER_base | ySEER_base | yCOP_base | yHSPF_base
Water-Source Heat Pumps | Yes | <17000 BTU/hr | 0 | 17000 |  | 12.2 |  | 4.3 |  | Water to Air: Water Loop
Water-Source Heat Pumps | Yes | >17000 BTU/hr and <65000 BTU/hr | 17000 | 65000 |  | 13 |  | 4.3
Water-Source Heat Pumps | No | <17000 BTU/hr | 0 | 17000 |  | 11 |  | 4.3
Water-Source Heat Pumps | No | >17000 BTU/hr and <65000 BTU/hr | 17000 | 65000 |  | 11.8 |  | 4.2
Ground Water Source Heat Pumps | Yes | <135000 BTU/hr | 0 | 135000 |  | 18 |  | 3.7 |  | Water to Air: Ground Water
Ground Source Heat Pumps | Yes | <135000 BTU/hr | 0 | 135000 |  | 13.4 |  | 3.1
Air-Source Heat Pumps | Yes | <65,000 BTU/hr | 0 | 65000 |  | 11.3 | 13 |  | 7.7 | no brine loop?
Air-Source Heat Pumps | Yes | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 11.2 | 11 |  | 3.3
Air-Source Heat Pumps | Yes | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 10.7 | 10.6 |  | 3.2
Air-Source Heat Pumps | Yes | >= 240,000 Btu/hr | 240000 | 100000000 | 9.6 | 9.5 |  | 3.2
Air-Source Heat Pumps | No | <65,000 BTU/hr | 0 | 65000 |  | 11.3 | 13 |  | 7.7
Air-Source Heat Pumps | No | >= 65,000 Btu/hr and <135,000 Btu/hr | 65000 | 135000 | 11 | 10.8 |  | 3.3
Air-Source Heat Pumps | No | >= 135,000 Btu/hr and < 240,000 Btu/hr | 135000 | 240000 | 10.5 | 10.4 |  | 3.2
Air-Source Heat Pumps | No | >= 240,000 Btu/hr | 240000 | 100000000 | 9.4 | 9.3 |  | 3.2
Equipment Type | yLouver_Existence | Installed Rated Cooling Capacity (Btu/hr) | yHVAC_MinCapacity | yHVAC_MaxCapacity | yCEER_base | yEER_base | yCEER_E*
Room Air Conditioners | With Louvered Sides | < 6,000 BTU/hr | 0 | 6000 | 11 | 11.2 | 12.1
Room Air Conditioners | With Louvered Sides | 6,000 to 7,999 BTU/hr | 6000 | 8000 | 11 | 11.2 | 12
Room Air Conditioners | With Louvered Sides | 8,000 to 10,999 BTU/hr | 8000 | 11000 | 10.9 | 11.3 | 12
Room Air Conditioners | With Louvered Sides | 11,000 to 13,999 BTU/hr | 11000 | 14000 | 10.9 | 11.3 | 11.8
Room Air Conditioners | With Louvered Sides | 14,000 to 19,999 BTU/hr | 14000 | 20000 | 10.7 | 11.2 | 10.3
Room Air Conditioners | With Louvered Sides | 20,000 to 24,999 BTU/hr | 20000 | 25000 | 9.4 | 9.8 | 10.3
Room Air Conditioners | With Louvered Sides | ≥25,000 BTU/hr | 25000 | 100000000 | 9 | 9.8 | 9.9
Room Air Conditioners | Without Louvered Sides | < 6,000 BTU/hr | 0 | 6000 | 10 | 10.4 | 11
Room Air Conditioners | Without Louvered Sides | 6,000 to 7,999 BTU/hr | 6000 | 8000 | 10 | 9.8 | 10.6
Room Air Conditioners | Without Louvered Sides | 8,000 to 10,999 BTU/hr | 8000 | 11000 | 9.6 | 9.8 | 10.5
Room Air Conditioners | Without Louvered Sides | 11,000 to 13,999 BTU/hr | 11000 | 14000 | 9.5 | 9.8 | 10.2
Room Air Conditioners | Without Louvered Sides | 14,000 to 19,999 BTU/hr | 14000 | 20000 | 9.3 | 9.8 | 10.3
Room Air Conditioners | Without Louvered Sides | 20,000 to 24,999 BTU/hr | 20000 | 25000 | 9.4 | 9.8 | 10.3
Room Air Conditioners | Without Louvered Sides | ≥25,000 BTU/hr | 25000 | 100000000 | 9.4 | 9.8 | 10.3
Reverse Cycle Room Air Conditioners | With Louvered Sides | <20,000 BTU/hr | 0 | 20000 | 9.8 | 10.4 | 10.8
Reverse Cycle Room Air Conditioners | With Louvered Sides | >=20,000 BTU/hr | 20000 | 100000000 | 9.3 | 9.8 | 10.2
Reverse Cycle Room Air Conditioners | Without Louvered Sides | <14,000 BTU/hr | 0 | 14000 | 9.3 | 9.8 | 10.2
Reverse Cycle Room Air Conditioners | Without Louvered Sides | >=14,000 BTU/hr | 14000 | 100000000 | 8.7 | 9.2 | 9.6
Casement-Only Room Air Conditioners |  |  | 0 | 100000000 | 9.5 | 10 | 10.5
Casement-Slider Room Air Conditioners |  |  | 0 | 100000000 | 10.4 | 10.9 | 11.4
Equipment Type | yAFUE
Gas Furnace | 95%
Oil Furnace | 85%
Gas/Propane Steam Boiler | 90%
Gas/Propane Hot Water Boiler | 90%
Oil Steam Boiler | 87%
Oil Hot Water Boiler | 87%
Equipment Type | yUpflow/Downflow | Installed Rated Cooling Capacity (Btu/hr) | yHVAC_MinCapacity | yHVAC_MaxCapacity | SCOP
Computer Room Air Conditioner Air Cooled | Upflow | <65,000 BTU/hr | 0 | 65000 | 2.09
Computer Room Air Conditioner Air Cooled | Upflow | >= 65,000 Btu/hr and <240,000 Btu/hr | 65000 | 240000 | 1.99
Computer Room Air Conditioner Air Cooled | Upflow | >= 240,000 Btu/hr | 240000 | 100000000 | 1.79
Computer Room Air Conditioner Air Cooled | Downflow | <65,000 BTU/hr | 0 | 65000 | 2.2
Computer Room Air Conditioner Air Cooled | Downflow | >= 65,000 Btu/hr and <240,000 Btu/hr | 65000 | 240000 | 2.1
Computer Room Air Conditioner Air Cooled | Downflow | >= 240,000 Btu/hr | 240000 | 100000000 | 1.9
Computer Room Air Conditioner Water Cooled | Upflow | <65,000 BTU/hr | 0 | 65000 | 2.49
Computer Room Air Conditioner Water Cooled | Upflow | >= 65,000 Btu/hr and <240,000 Btu/hr | 65000 | 240000 | 2.39
Computer Room Air Conditioner Water Cooled | Upflow | >= 240,000 Btu/hr | 240000 | 100000000 | 2.29
Computer Room Air Conditioner Water Cooled | Downflow | <65,000 BTU/hr | 0 | 65000 | 2.6
Computer Room Air Conditioner Water Cooled | Downflow | >= 65,000 Btu/hr and <240,000 Btu/hr | 65000 | 240000 | 2.5
Computer Room Air Conditioner Water Cooled | Downflow | >= 240,000 Btu/hr | 240000 | 100000000 | 2.4
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Upflow | <65,000 BTU/hr | 0 | 65000 | 2.44
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Upflow | >= 65,000 Btu/hr and <240,000 Btu/hr | 65000 | 240000 | 2.34
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Upflow | >= 240,000 Btu/hr | 240000 | 100000000 | 2.24
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Downflow | <65,000 BTU/hr | 0 | 65000 | 2.44
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Downflow | >= 65,000 Btu/hr and <240,000 Btu/hr | 65000 | 240000 | 2.34
Computer Room Air Conditioner Water Cooled with Fluid Economizer | Downflow | >= 240,000 Btu/hr | 240000 | 100000000 | 2.24
Computer Room Air Conditioner Glycol Cooled | Upflow | <65,000 BTU/hr | 0 | 65000 | 2.39
Computer Room Air Conditioner Glycol Cooled | Upflow | >= 65,000 Btu/hr and <240,000 Btu/hr | 65000 | 240000 | 2.04
Computer Room Air Conditioner Glycol Cooled | Upflow | >= 240,000 Btu/hr | 240000 | 100000000 | 1.99
Computer Room Air Conditioner Glycol Cooled | Downflow | <65,000 BTU/hr | 0 | 65000 | 2.39
Computer Room Air Conditioner Glycol Cooled | Downflow | >= 65,000 Btu/hr and <240,000 Btu/hr | 65000 | 240000 | 2.04
Computer Room Air Conditioner Glycol Cooled | Downflow | >= 240,000 Btu/hr | 240000 | 100000000 | 1.99
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Upflow | <65,000 BTU/hr | 0 | 65000 | 2.34
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Upflow | >= 65,000 Btu/hr and <240,000 Btu/hr | 65000 | 240000 | 1.99
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Upflow | >= 240,000 Btu/hr | 240000 | 100000000 | 1.94
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Downflow | <65,000 BTU/hr | 0 | 65000 | 2.34
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Downflow | >= 65,000 Btu/hr and <240,000 Btu/hr | 65000 | 240000 | 1.99
Computer Room Air Conditioner Glycol Cooled with Fluid Economizer | Downflow | >= 240,000 Btu/hr | 240000 | 100000000 | 1.94
High Volume Low Speed Fans
Fan Size (ft) | Watts (HVLS) | Watts (Conventional) | Wconv-WHVLS
≥ 16 and < 18 | 761 | 4497 | 3736
≥ 18 and < 20 | 850 | 5026 | 4176
≥ 20 and < 24 | 940 | 5555 | 4615
≥ 24 | 1119 | 6613 | 5494
Note on H99: James Domanski: Not in TRM

## Version Log (hidden)
Version Log
Original Author: |  | Alex Nissley | QA/QC Engineer(s): | Jeannie Sikora
Primary Developer: |  | James Domanski | Senior Engineer Approval: | Tom Cosgro
Version | Date | Reason for Change | Change Description | Contact, Department
1 | 2018-09-05 | New format |  | Alex Nissley, Engineering
3 | 2018-11-30 | PPL Branding |  | Tom Cosgro, Engineering
4 | 2021-04-26 | TRM /DSMT Update | Updated for Phase 4 starting 6/1/2021 | James Domanski, Engineering