## Instructions
PPL Drives for Motors Estimator
This calculator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this calculator is deemed acceptable for the PPL Electric Utilities Non-Residential Energy Efficiency Program. However, the assumptions used by the applicant to calculate the annual savings will be reviewed by the Program Team, which is solely responsible for the final determination of the annual energy savings to be used in calculating the incentive amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities. For any questions, or assistance using this Calculator, please call 1-866-432-5501 or email us at pplbusiness@clearesult.com.
Input Instructions
Yellow cells indicate that user input is required. Cells with a * are required.
Grey cells are calculated values.
Worksheet Summary
Methodology
Provides methodology for savings estimations
Project Summary
This provides summary of estimated savings along with some required inputs
Premium Efficiency Motors
This is for constant speed and uniformly loaded motors in new construction and replace on burnout measures. Replacements where old motors and new motors have different horsepowers are considered a custom measure. Motor with variable speeds are considered a custom measure. Systems with multiple motors in a lead-lag setup are also considered custom measures.
VFD Improvements
The protocol is for standard commercial application where the baseline motor is without a VFD control.
ECM Fans
This measure is for the retrofit of existing shaded-pole (SP) or permanent-split capacitor (PSC) evaporator fan motors in an air handling unit to a electronically commutated motor (ECM). This measure only applies to motors of one horsepower or less. Anything greater than 1 HP are governed by NEMA standard. The targeted fan can be for cooling, heating, or both.
VSD Kitchen Fans
This measure is for the installation of variable speed drives (VSD) on commercial kitchen exhaust fans. The VSD must vary the exhaust rate of kitchen ventilation based on the energy and effluent output from the cooking appliances. This involves installing a temperature sensor in the hood exhaust collar and/or an optic sensor on the end of the hood that can sense cooking conditions.
Version Log
The Version Log Worksheet tracks updates and changes made to the workbook.
Glossary of Inputs
Date | Date the estimator is completed.
Project Name | Name of project for reference.
Address | Physical location of project.
Installation Date | Date the project is completed.
Project Cost* | The cost associated with the project. Required for incentive calculation.
Location* | The nearest city to the project location.
Building Type* | The building type for the project. If your building type is not listed, please contact the PPL Program.
Motor ID | The ID of the motor for reference.
Motor Function* | The function of the motor. This is a dropdown list. If your motor function is not listed, please contact the PPL Program.
Number of Units* | The number of units to receive the retrofit. May also be referred to as quantity.
NEMA Design Type* | The NEMA type of motor to be installed. Used to calculate baseline efficiency.
Number of Poles* | Number of poles in the motor.
Motor Enclosure* | The motor enclosure type.
Motor Replacement* | Select if the motor is new construction or a replace on burnout.
Horsepower* | The horsepower of the pre and post motor must match.
Manufacturer* | This is the manufacturer of the equipment to be installed. See specific tab for which piece of equipment.
Model Number* | This is the model number of the equipment to be installed. See individual tab for which piece of equipment.
Efficiency* | In premium motors, this is the efficiency of the new NEMA motor.
Control Type* | In VFD's this is the type of control on the fan/pump. If yours is not listed, or you are unsure of which type you have, contact the PPL Program team.
Baseline Motor Type* | This is the baseline motor type for ECM applications.
Equipment Size* | This is the HP size for the ECM motor application. It must be less than or equal to 1 HP.
Fan Application* | This designates if the fan is for heating, cooling, or both.
Glossary of Outputs
kWh Savings | This is the anticipated kWh savings of the line item or measure. | kWh
kW savings | This is the anticipated peak kW savings of the line item/measure.
Incentive | This is the estimated incentive based on project cost and kWh savings.
Run Hours | This is the prescriptive hours of use based on location and facility type.
Coincidence Factor | This is the prescriptive coincidence factor based on the location and facility type.
Motor Efficiency | This is the NEMA efficiency in the Motors tab based on NEMA inputs.
ESF | This is a Energy Savings Factor based on inputs from the VFD tab.
DSF | This is a Demand Savings Factor based on inputs from the VFD tab.

## Methodology (hidden)
Calculator Methodology
Premium Efficiency Motors
The energy savings is calculated from the 2016 PA TRM with errata. Reference that document for any greater detail than what is provided.
VFD Improvement
The energy savings is calculated from the 2016 PA TRM with errata. Reference that document for any greater detail than what is provided.
ECM Motors
The energy savings is calculated from the 2016 PA TRM with errata. Reference that document for any greater detail than what is provided.
VSD on Kitchen Exhaust Fans
The energy savings is calculated from the 2016 PA TRM with errata. Reference that document for any greater detail than what is provided.

## Project Summary
|  |  |  | Version | 4
|  |  |  | Last Updated | 2021-06-01
Project Summary
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Name
Address
Installation Date
Project Cost*
Location*
Building Type*
Measure | kWh Savings | kW Savings | Uncapped Incentive | Incentive
Premium Efficient Motors | 0 | 0 | 0 | 0
VFDs | 0 | 0 | 0 | 0
ECM Fans | 0 | 0 | 0 | 0
VSD Kitchen Fan | 0 | 0 | 0 | 0
ECM Circulator Pump | 0 | 0 | 0 | 0
High Efficiency Pumps | 0 | 0 | 0 | 0
Total | 0 | 0 | 0 | 0

## Premium Eff Motor
|  |  |  | HIDE | [5 empty] | HIDE | HIDE | HIDE |  |  | HIDE |  | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
Premium Efficiency Motors
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Motor Information | [7 empty] | Baseline Information |  |  |  | New Motor |  |  |  | Calculations | [6 empty] | Total Incentive
Line Item | Motor ID | Motor Function* | Number of Units* | Load Factor | NEMA Design Type* | Number of Poles* | Motor Enclosure* | Motor Replacement* | Horsepower* | Efficiency | Run Hours | CF | Manufacturer | Model Number | Horsepower | Efficiency* | Baseline kWh | Baseline kW | EE kWh | EE kW | kWh Savings | kW Savings | Uncapped Incentive
1 | [9 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | [9 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | [9 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | [9 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | [9 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | [9 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | [9 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | [9 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | [9 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | [9 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0

## VFDs
|  |  |  | HIDE |  |  |  |  | HIDE | HIDE |  |  | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
Variable Frequency Drive (VFD) Improvements
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Motor Information | [5 empty] | Baseline Information |  |  |  | VFD Information |  | Calculations | [6 empty] | Total Incentive
Line Item | Motor ID | Equipment Type | Motor Function* | Load Factor | Horsepower* | Efficiency* | Control Type* | Quantity* | Run Hours | CF | Manufacturer | Model Number | kWhbase | kWhee | kWbase | kWee | kWh Savings | kW Savings | Uncapped Incentive
1 |  |  |  | 0.75 |  |  |  |  | 0 | 0
2 |  |  |  | 0.75 |  |  |  |  | 0 | 0
3 |  |  |  | 0.75 |  |  |  |  | 0 | 0
4 |  |  |  | 0.75 |  |  |  |  | 0 | 0
5 |  |  |  | 0.75 |  |  |  |  | 0 | 0
6 |  |  |  | 0.75 |  |  |  |  | 0 | 0
7 |  |  |  | 0.75 |  |  |  |  | 0 | 0
8 |  |  |  | 0.75 |  |  |  |  | 0 | 0
9 |  |  |  | 0.75 |  |  |  |  | 0 | 0
10 |  |  |  | 0.75 |  |  |  |  | 0 | 0

## ECM Fan
[8 empty] | HIDE |  | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
ECM Circulating Fan
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Efficient Unit |  |  | Baseline Unit | [6 empty] | Proposed Unit |  | Calculations | [14 empty] | Total Incentive
Line Item | Unit ID | Manufacturer | Model | Baseline Motor Type* | Motor HP | Quantity* | Fan Application* | Motor Eff | Ventilation Only Hours | Watts | Equipment Type | Watts | LF | EFLH heat | EFLH cool | IF kWh | IF kW | CFcool | kWh heat | kW heat | kWh cool | kW cool | kWh vent | kW vent | kWh savings | kW savings | Uncapped Incentive
1 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | [9 empty] | 0 | ECM | 0 | 0.9 | 0 | 0 | 0.262 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on Z7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Defaulting to 0 as this parameter is difficult to estimate.

## VSD Kitchen Fan
[6 empty] | HIDE | HIDE |  |  | HIDE
VSD on Kitchen Exhaust Fan
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Line Item | Motor Information |  |  |  |  | Calculations |  |  |  |  | Total Incentive
| Unit ID | Manufacturer | Model | Horsepower* | Quantity* | Run Hours | CF | kWh Savings | kW Savings | Uncapped Incentive
1 | [5 empty] | 4423 | 0.55 | 0 | 0 | 0
2 | [5 empty] | 4423 | 0.55 | 0 | 0 | 0
3 | [5 empty] | 4423 | 0.55 | 0 | 0 | 0
4 | [5 empty] | 4423 | 0.55 | 0 | 0 | 0
5 | [5 empty] | 4423 | 0.55 | 0 | 0 | 0
6 | [5 empty] | 4423 | 0.55 | 0 | 0 | 0
7 | [5 empty] | 4423 | 0.55 | 0 | 0 | 0
8 | [5 empty] | 4423 | 0.55 | 0 | 0 | 0
9 | [5 empty] | 4423 | 0.55 | 0 | 0 | 0
10 | [5 empty] | 4423 | 0.55 | 0 | 0 | 0

## ECM Circulator Pump
[8 empty] | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
ECM Circulating Pump
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Line Item | Efficient Unit | [7 empty] | Baseline Unit | Calculations | [12 empty] | Total Incentive
| Unit ID | Manufacturer | Model | Motor HP | Quantity* | Pump Application* | Pump Control Type | Watts | Watts | LF | EFLH heat | HOUdhw-base | HOUdhw-ee | CFbase | CFee | kWh heating | kW heating | kWh dhw | kW dhw | kWh savings | kW savings | Uncapped Incentive | Capped Incentive
1 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 | 0
2 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 | 0
3 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 | 0
4 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 | 0
5 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 | 0
6 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 | 0
7 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 | 0
8 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 | 0
9 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 | 0
10 | [7 empty] | 0 | 0 | 0.9 | 0 |  |  |  |  | 0 | 0

## High Efficiency Pumps
[6 empty] | HIDE |  |  | HIDE | HIDE |  |  |  | HIDE | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
High Efficiency Pumps
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Line Item | Pump/Motor Information | [12 empty] | Calculations | [7 empty] | Total Incentive
| Motor ID | Pump Function | Pump Type | Pump Speed | Quantity | Load Factor | Horsepower | Efficiency | Run Hours | CF | Manufacturer | Model Number | PEIee | PEIbase | Baseline kWh | Baseline kW | EE kWh | EE kW | kWh Savings | kW Savings | Uncapped Incentive | Capped Incentive
1 | [5 empty] | 0.79 |  |  | 0 | 0 |  |  |  | #N/A
2 | [5 empty] | 0.79 |  |  | 0 | 0 |  |  |  | #N/A
3 | [5 empty] | 0.79 |  |  | 0 | 0 |  |  |  | #N/A
4 | [5 empty] | 0.79 |  |  | 0 | 0 |  |  |  | #N/A
5 | [5 empty] | 0.79 |  |  | 0 | 0 |  |  |  | #N/A
6 | [5 empty] | 0.79 |  |  | 0 | 0 |  |  |  | #N/A
7 | [5 empty] | 0.79 |  |  | 0 | 0 |  |  |  | #N/A
8 | [5 empty] | 0.79 |  |  | 0 | 0 |  |  |  | #N/A
9 | [5 empty] | 0.79 |  |  | 0 | 0 |  |  |  | #N/A
10 | [5 empty] | 0.79 |  |  | 0 | 0 |  |  |  | #N/A

## Lookup Table (hidden)
Table 1: Location |  | Table 2: Facility Type |  | Table 3: Motor Replace |  | Table 4: Nema Type |  | Table 5: Motor Function | Load Factor |  | Table 6: Motor Enclosure |  | Table 7: Horsepower |  | Table 8: Poles
Allentown |  | Education - College / University |  | New Construction |  | Type A |  | Supply Fan | 0.76 |  | Open |  | 1 |  | 2
Binghamton |  | Education - Other |  | Replace on Burnout |  | Type B |  | Cooling Tower Fan | 0.76 |  | Enclosed |  | 1.5 |  | 4
Bradford |  | Grocery |  | Early Replacement |  | Type C |  | Chilled Water Pump | 0.79 |  |  |  | 2 |  | 6
Erie |  | Health - Hospital | [5 empty] | Heating Hot Water Pump | 0.79 |  |  |  | 3 |  | 8
Harrisburg |  | Health - Other | [5 empty] | Condenser Water Pump | 0.79 |  |  |  | 5
Philadelphia |  | Industrial Manufacturing | [10 empty] | 7.5
Pittsburgh |  | Institutional / Public Service | [10 empty] | 10
Scranton |  | Lodging | [10 empty] | 15
Williamsburg |  | Multifamily (Common Areas) | [10 empty] | 20
|  | Office | [10 empty] | 25
|  | Restaurant | [10 empty] | 30
|  | Retail | [10 empty] | 40
|  | Warehouse - Other | [10 empty] | 50
|  | Warehouse - Refrigerated | [10 empty] | 60
75
100
125
150
200
250
300
350
400
450
500
Calculation 1: Calculating Baseline Efficiency for Premium Motors
Line Item | NC? | Nema Type | Poles | Open | Horsepower | Table Lookup | 2 close | 2 open | 4 close | 4 open | 6 close | 6 open | 8 close | 8 open | 2 Pole | 4 Pole | 6 Pole | 8 Pole | Efficiency
1 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
2 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
3 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
4 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
5 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
6 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
7 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
8 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
9 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
10 | Yes | 0 | 0 | 0 | 0 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
Table 9: Type A/B | [9 empty] | Table 10: Type C Motors
| 2 Poles |  | 4 Poles |  | 6 Poles |  | 8 Poles |  |  |  | 4 Poles |  | 6 Poles |  | 8 Poles
HP | Close | Open | Close | Open | Close | Open | Close | Open |  | HP | Close | Open | Close | Open | Close | Open
1 | 77% | 77% | 85.5% | 85.5% | 82.5% | 82% | 75.5% | 75.5% |  | 1 | 0.855 | 0.855 | 0.825 | 0.825 | 0.755 | 0.755
1.5 | 84% | 84% | 86.5% | 86.5% | 87.5% | 86.5% | 78.5% | 77% |  | 1.5 | 0.865 | 0.865 | 0.875 | 0.865 | 0.785 | 0.77
2 | 85.5% | 85.5% | 86.5% | 86.5% | 88.5% | 87.5% | 84% | 86.5% |  | 2 | 0.865 | 0.865 | 0.885 | 0.875 | 0.84 | 0.865
3 | 86.5% | 85.5% | 89.5% | 89.5% | 89.5% | 88.5% | 85.5% | 87.5% |  | 3 | 0.895 | 0.895 | 0.895 | 0.885 | 0.855 | 0.875
5 | 88.5% | 86.5% | 89.5% | 89.5% | 89.5% | 89.5% | 86.5% | 88.5% |  | 5 | 0.895 | 0.895 | 0.895 | 0.895 | 0.865 | 0.885
7.5 | 89.5% | 88.5% | 91.7% | 91% | 91% | 90.2% | 86.5% | 89.5% |  | 7.5 | 0.917 | 0.91 | 0.91 | 0.902 | 0.865 | 0.895
10 | 90.2% | 89.5% | 91.7% | 91.7% | 91% | 91.7% | 89.5% | 90.2% |  | 10 | 0.917 | 0.917 | 0.91 | 0.917 | 0.895 | 0.902
15 | 91% | 90.2% | 92.4% | 93% | 91.7% | 91.7% | 89.5% | 90.2% |  | 15 | 0.924 | 0.93 | 0.917 | 0.917 | 0.895 | 0.902
20 | 91% | 91% | 93% | 93% | 91.7% | 92.4% | 90.2% | 91% |  | 20 | 0.93 | 0.93 | 0.917 | 0.924 | 0.902 | 0.91
25 | 91.7% | 91.7% | 93.6% | 93.6% | 93% | 93% | 90.2% | 91% |  | 25 | 0.936 | 0.936 | 0.93 | 0.93 | 0.902 | 0.91
30 | 91.7% | 91.7% | 93.6% | 94.1% | 93% | 93.6% | 91.7% | 91.7% |  | 30 | 0.936 | 0.941 | 0.93 | 0.936 | 0.917 | 0.917
40 | 92.4% | 92.4% | 94.1% | 94.1% | 94.1% | 94.1% | 91.7% | 91.7% |  | 40 | 0.941 | 0.941 | 0.941 | 0.941 | 0.917 | 0.917
50 | 93% | 93% | 94.5% | 94.5% | 94.1% | 94.1% | 92.4% | 92.4% |  | 50 | 0.945 | 0.945 | 0.941 | 0.941 | 0.924 | 0.924
60 | 93.6% | 93.6% | 95% | 95% | 94.5% | 94.5% | 92.4% | 93% |  | 60 | 0.95 | 0.95 | 0.945 | 0.945 | 0.924 | 0.93
75 | 93.6% | 93.6% | 95.4% | 95% | 94.5% | 94.5% | 93.6% | 94.1% |  | 75 | 0.954 | 0.95 | 0.945 | 0.945 | 0.936 | 0.941
100 | 94.1% | 93.6% | 95.4% | 95.4% | 95% | 95% | 93.6% | 94.1% |  | 100 | 0.954 | 0.954 | 0.95 | 0.95 | 0.936 | 0.941
125 | 95% | 94.1% | 95.4% | 95.4% | 95% | 95% | 94.1% | 94.1% |  | 125 | 0.954 | 0.954 | 0.95 | 0.95 | 0.941 | 0.941
150 | 95% | 94.1% | 95.8% | 95.8% | 95.8% | 95.4% | 94.1% | 94.1% |  | 150 | 0.958 | 0.958 | 0.958 | 0.954 | 0.941 | 0.941
200 | 95.4% | 95% | 96.2% | 95.8% | 95.8% | 95.4% | 94.5% | 94.1% |  | 200 | 0.962 | 0.958 | 0.958 | 0.954 | 0.945 | 0.941
250 | 95.8% | 95% | 96.2% | 95.8% | 95.8% | 95.8% | 95% | 95%
300 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A
350 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A
400 | 95.8% | 95.8% | 96.2% | 95.8% | N/A | N/A | N/A | N/A
450 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A
500 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A
Table 11: Run Hours | [9 empty] | Table 12: Coincidence Factor
City | Type | Concatenate | Chilled Water Pump | Cooling Tower Fan | Condenser Water Pump | Heating Hot Water Pump | Supply Fan |  |  | City | Type | Concatenate | Chilled Water Pump | Cooling Tower Fan | Condenser Water Pump | Heating Hot Water Pump | Supply Fan
Allentown | Education - College / University | Allentown Education - College / University | 4007 | 4006 | 3527 | 4548 | 6042 |  |  | Allentown | Education - College / University | Allentown Education - College / University | 0.41 | 0.41 | 0.41 | 0.01 | 0.43
Allentown | Education - Other | Allentown Education - Other | 2721 | 2742 | 2448 | 3651 | 4380 |  |  | Allentown | Education - Other | Allentown Education - Other | 0.1 | 0.11 | 0.11 | 0 | 0.12
Allentown | Grocery | Allentown Grocery | #N/A | #N/A | #N/A | #N/A | 6708 |  |  | Allentown | Grocery | Allentown Grocery | #N/A | #N/A | #N/A | #N/A | 0.24
Allentown | Health - Hospital | Allentown Health - Hospital | 5588 | 5587 | 3950 | 8760 | 8760 |  |  | Allentown | Health - Hospital | Allentown Health - Hospital | 0.46 | 0.45 | 0.45 | 0.09 | 0.43
Allentown | Health - Other | Allentown Health - Other | 3892 | 3894 | 3675 | 5934 | 8760 |  |  | Allentown | Health - Other | Allentown Health - Other | 0.24 | 0.24 | 0.24 | 0 | 0.24
Allentown | Industrial Manufacturing | Allentown Industrial Manufacturing | 1735 | 1735 | 1735 | 1258 | 3831 |  |  | Allentown | Industrial Manufacturing | Allentown Industrial Manufacturing | 0.53 | 0.53 | 0.53 | 0 | 0.48
Allentown | Institutional / Public Service | Allentown Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 5188 |  |  | Allentown | Institutional / Public Service | Allentown Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 0.53
Allentown | Lodging | Allentown Lodging | 5845 | 5844 | 5544 | 6469 | 8760 |  |  | Allentown | Lodging | Allentown Lodging | 0.61 | 0.61 | 0.61 | 0 | 0.64
Allentown | Office | Allentown Office | 1789 | 1789 | 1781 | 3214 | 4195 |  |  | Allentown | Office | Allentown Office | 0.29 | 0.29 | 0.29 | 0 | 0.3
Allentown | Restaurant | Allentown Restaurant | #N/A | #N/A | #N/A | #N/A | 6282 |  |  | Allentown | Restaurant | Allentown Restaurant | #N/A | #N/A | #N/A | #N/A | 0.38
Allentown | Retail | Allentown Retail | 2957 | 2957 | 2889 | 2676 | 5137 |  |  | Allentown | Retail | Allentown Retail | 0.46 | 0.46 | 0.46 | 0 | 0.5
Allentown | Warehouse - Other | Allentown Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5037 |  |  | Allentown | Warehouse - Other | Allentown Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.18
Allentown | Warehouse - Refrigerated | Allentown Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Allentown | Warehouse - Refrigerated | Allentown Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.5
Binghamton | Education - College / University | Binghamton Education - College / University | 3436 | 3435 | 2938 | 5271 | 6054 |  |  | Binghamton | Education - College / University | Binghamton Education - College / University | 0.27 | 0.26 | 0.26 | 0.01 | 0.3
Binghamton | Education - Other | Binghamton Education - Other | 1849 | 1851 | 1733 | 4251 | 4583 |  |  | Binghamton | Education - Other | Binghamton Education - Other | 0.08 | 0.08 | 0.08 | 0 | 0.08
Binghamton | Grocery | Binghamton Grocery | #N/A | #N/A | #N/A | #N/A | 6764 |  |  | Binghamton | Grocery | Binghamton Grocery | #N/A | #N/A | #N/A | #N/A | 0.21
Binghamton | Health - Hospital | Binghamton Health - Hospital | 4801 | 4798 | 3546 | 8760 | 8760 |  |  | Binghamton | Health - Hospital | Binghamton Health - Hospital | 0.38 | 0.37 | 0.37 | 0.09 | 0.24
Binghamton | Health - Other | Binghamton Health - Other | 3093 | 3093 | 3100 | 6627 | 8760 |  |  | Binghamton | Health - Other | Binghamton Health - Other | 0.2 | 0.2 | 0.2 | 0 | 0.21
Binghamton | Industrial Manufacturing | Binghamton Industrial Manufacturing | 1306 | 1306 | 1305 | 1684 | 3981 |  |  | Binghamton | Industrial Manufacturing | Binghamton Industrial Manufacturing | 0.4 | 0.4 | 0.4 | 0 | 0.34
Binghamton | Institutional / Public Service | Binghamton Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 5223 |  |  | Binghamton | Institutional / Public Service | Binghamton Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 0.38
Binghamton | Lodging | Binghamton Lodging | 5042 | 5039 | 4591 | 7072 | 8760 |  |  | Binghamton | Lodging | Binghamton Lodging | 0.58 | 0.58 | 0.58 | 0 | 0.64
Binghamton | Office | Binghamton Office | 1402 | 1402 | 1389 | 3876 | 4473 |  |  | Binghamton | Office | Binghamton Office | 0.25 | 0.25 | 0.25 | 0 | 0.26
Binghamton | Restaurant | Binghamton Restaurant | #N/A | #N/A | #N/A | #N/A | 2680 |  |  | Binghamton | Restaurant | Binghamton Restaurant | #N/A | #N/A | #N/A | #N/A | 0.19
Binghamton | Retail | Binghamton Retail | 2416 | 2416 | 2381 | 3183 | 5188 |  |  | Binghamton | Retail | Binghamton Retail | 0.33 | 0.33 | 0.33 | 0 | 0.4
Binghamton | Warehouse - Other | Binghamton Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5189 |  |  | Binghamton | Warehouse - Other | Binghamton Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.11
Binghamton | Warehouse - Refrigerated | Binghamton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Binghamton | Warehouse - Refrigerated | Binghamton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.46
Bradford | Education - College / University | Bradford Education - College / University | 3096 | 3096 | 2466 | 5900 | 6126 |  |  | Bradford | Education - College / University | Bradford Education - College / University | 0.23 | 0.23 | 0.2 | 0.01 | 0.24
Bradford | Education - Other | Bradford Education - Other | 1631 | 1634 | 1529 | 4722 | 4718 |  |  | Bradford | Education - Other | Bradford Education - Other | 0.07 | 0.07 | 0.07 | 0 | 0.07
Bradford | Grocery | Bradford Grocery | #N/A | #N/A | #N/A | #N/A | 6810 |  |  | Bradford | Grocery | Bradford Grocery | #N/A | #N/A | #N/A | #N/A | 0.19
Bradford | Health - Hospital | Bradford Health - Hospital | 4167 | 4165 | 3293 | 8760 | 8760 |  |  | Bradford | Health - Hospital | Bradford Health - Hospital | 0.31 | 0.31 | 0.29 | 0.09 | 0.29
Bradford | Health - Other | Bradford Health - Other | 2592 | 2593 | 2585 | 7170 | 8760 |  |  | Bradford | Health - Other | Bradford Health - Other | 0.16 | 0.16 | 0.16 | 0 | 0.17
Bradford | Industrial Manufacturing | Bradford Industrial Manufacturing | 1086 | 1086 | 1084 | 1944 | 4080 |  |  | Bradford | Industrial Manufacturing | Bradford Industrial Manufacturing | 0.32 | 0.32 | 0.32 | 0 | 0.28
Bradford | Institutional / Public Service | Bradford Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 5248 |  |  | Bradford | Institutional / Public Service | Bradford Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 0.34
Bradford | Lodging | Bradford Lodging | 4444 | 4442 | 3939 | 7587 | 8760 |  |  | Bradford | Lodging | Bradford Lodging | 0.53 | 0.53 | 0.53 | 0 | 0.6
Bradford | Office | Bradford Office | 1189 | 1189 | 1177 | 4446 | 4699 |  |  | Bradford | Office | Bradford Office | 0.2 | 0.2 | 0.2 | 0 | 0.21
Bradford | Restaurant | Bradford Restaurant | #N/A | #N/A | #N/A | #N/A | 6487 |  |  | Bradford | Restaurant | Bradford Restaurant | #N/A | #N/A | #N/A | #N/A | 0.28
Bradford | Retail | Bradford Retail | 2012 | 2012 | 1986 | 3568 | 5234 |  |  | Bradford | Retail | Bradford Retail | 0.28 | 0.28 | 0.28 | 0 | 0.36
Bradford | Warehouse - Other | Bradford Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5259 |  |  | Bradford | Warehouse - Other | Bradford Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.1
Bradford | Warehouse - Refrigerated | Bradford Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Bradford | Warehouse - Refrigerated | Bradford Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.43
Erie | Education - College / University | Erie Education - College / University | 3641 | 3641 | 3063 | 5036 | 6139 |  |  | Erie | Education - College / University | Erie Education - College / University | 0.3 | 0.3 | 0.3 | 0.01 | 0.32
Erie | Education - Other | Erie Education - Other | 2175 | 2178 | 2039 | 4080 | 4572 |  |  | Erie | Education - Other | Erie Education - Other | 0.09 | 0.09 | 0.09 | 0 | 0.09
Erie | Grocery | Erie Grocery | #N/A | #N/A | #N/A | #N/A | 6738 |  |  | Erie | Grocery | Erie Grocery | #N/A | #N/A | #N/A | #N/A | 0.22
Erie | Health - Hospital | Erie Health - Hospital | 5109 | 5107 | 3698 | 8760 | 8760 |  |  | Erie | Health - Hospital | Erie Health - Hospital | 0.42 | 0.41 | 0.41 | 0.09 | 0.39
Erie | Health - Other | Erie Health - Other | 3456 | 3457 | 3394 | 6280 | 8760 |  |  | Erie | Health - Other | Erie Health - Other | 0.22 | 0.22 | 0.22 | 0 | 0.23
Erie | Industrial Manufacturing | Erie Industrial Manufacturing | 1448 | 1448 | 1445 | 1555 | 3977 |  |  | Erie | Industrial Manufacturing | Erie Industrial Manufacturing | 0.43 | 0.43 | 0.43 | 0 | 0.38
Erie | Institutional / Public Service | Erie Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 5217 |  |  | Erie | Institutional / Public Service | Erie Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 0.45
Erie | Lodging | Erie Lodging | 5198 | 5197 | 4766 | 6829 | 8760 |  |  | Erie | Lodging | Erie Lodging | 0.6 | 0.61 | 0.61 | 0 | 0.65
Erie | Office | Erie Office | 1585 | 1585 | 1569 | 3611 | 4441 |  |  | Erie | Office | Erie Office | 0.27 | 0.27 | 0.27 | 0 | 0.28
Erie | Restaurant | Erie Restaurant | #N/A | #N/A | #N/A | #N/A | 6365 |  |  | Erie | Restaurant | Erie Restaurant | #N/A | #N/A | #N/A | #N/A | 0.37
Erie | Retail | Erie Retail | 2653 | 2653 | 2616 | 2960 | 5158 |  |  | Erie | Retail | Erie Retail | 0.38 | 0.38 | 0.38 | 0 | 0.44
Erie | Warehouse - Other | Erie Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5222 |  |  | Erie | Warehouse - Other | Erie Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.13
Erie | Warehouse - Refrigerated | Erie Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Erie | Warehouse - Refrigerated | Erie Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.48
Harrisburg | Education - College / University | Harrisburg Education - College / University | 4057 | 4057 | 3602 | 4250 | 5860 |  |  | Harrisburg | Education - College / University | Harrisburg Education - College / University | 0.42 | 0.42 | 0.42 | 0 | 0.44
Harrisburg | Education - Other | Harrisburg Education - Other | 2730 | 2744 | 2539 | 3492 | 4313 |  |  | Harrisburg | Education - Other | Harrisburg Education - Other | 0.18 | 0.18 | 0.18 | 0 | 0.17
Harrisburg | Grocery | Harrisburg Grocery | #N/A | #N/A | #N/A | #N/A | 6692 |  |  | Harrisburg | Grocery | Harrisburg Grocery | #N/A | #N/A | #N/A | #N/A | 0.24
Harrisburg | Health - Hospital | Harrisburg Health - Hospital | 5717 | 5714 | 3687 | 8760 | 8760 |  |  | Harrisburg | Health - Hospital | Harrisburg Health - Hospital | 0.5 | 0.49 | 0.49 | 0.09 | 0.45
Harrisburg | Health - Other | Harrisburg Health - Other | 4104 | 4106 | 3725 | 5823 | 8760 |  |  | Harrisburg | Health - Other | Harrisburg Health - Other | 0.28 | 0.28 | 0.28 | 0 | 0.29
Harrisburg | Industrial Manufacturing | Harrisburg Industrial Manufacturing | 1742 | 1742 | 1737 | 1184 | 3769 |  |  | Harrisburg | Industrial Manufacturing | Harrisburg Industrial Manufacturing | 0.53 | 0.54 | 0.54 | 0 | 0.53
Harrisburg | Institutional / Public Service | Harrisburg Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 5172 |  |  | Harrisburg | Institutional / Public Service | Harrisburg Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 0.6
Harrisburg | Lodging | Harrisburg Lodging | 6045 | 6043 | 5569 | 6155 | 8760 |  |  | Harrisburg | Lodging | Harrisburg Lodging | 0.66 | 0.67 | 0.67 | 0 | 0.71
Harrisburg | Office | Harrisburg Office | 1804 | 1804 | 1792 | 3014 | 4087 |  |  | Harrisburg | Office | Harrisburg Office | 0.35 | 0.35 | 0.35 | 0 | 0.37
Harrisburg | Restaurant | Harrisburg Restaurant | #N/A | #N/A | #N/A | #N/A | 6252 |  |  | Harrisburg | Restaurant | Harrisburg Restaurant | #N/A | #N/A | #N/A | #N/A | 0.42
Harrisburg | Retail | Harrisburg Retail | 3085 | 3085 | 3025 | 2561 | 5108 |  |  | Harrisburg | Retail | Harrisburg Retail | 0.53 | 0.53 | 0.53 | 0 | 0.53
Harrisburg | Warehouse - Other | Harrisburg Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 4980 |  |  | Harrisburg | Warehouse - Other | Harrisburg Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.24
Harrisburg | Warehouse - Refrigerated | Harrisburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Harrisburg | Warehouse - Refrigerated | Harrisburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.52
Philadelphia | Education - College / University | Philadelphia Education - College / University | 4311 | 4309 | 4030 | 4014 | 5966 |  |  | Philadelphia | Education - College / University | Philadelphia Education - College / University | 0.45 | 0.45 | 0.45 | 0 | 0.47
Philadelphia | Education - Other | Philadelphia Education - Other | 3505 | 3517 | 3346 | 3341 | 4384 |  |  | Philadelphia | Education - Other | Philadelphia Education - Other | 0.18 | 0.18 | 0.18 | 0 | 0.18
Philadelphia | Grocery | Philadelphia Grocery | #N/A | #N/A | #N/A | #N/A | 6669 |  |  | Philadelphia | Grocery | Philadelphia Grocery | #N/A | #N/A | #N/A | #N/A | 0.26
Philadelphia | Health - Hospital | Philadelphia Health - Hospital | 6086 | 6084 | 4168 | 8760 | 8760 |  |  | Philadelphia | Health - Hospital | Philadelphia Health - Hospital | 0.54 | 0.54 | 0.54 | 0.09 | 0.51
Philadelphia | Health - Other | Philadelphia Health - Other | 4535 | 4537 | 4304 | 5477 | 8760 |  |  | Philadelphia | Health - Other | Philadelphia Health - Other | 0.3 | 0.3 | 0.3 | 0 | 0.31
Philadelphia | Industrial Manufacturing | Philadelphia Industrial Manufacturing | 1891 | 1891 | 1889 | 1028 | 3838 |  |  | Philadelphia | Industrial Manufacturing | Philadelphia Industrial Manufacturing | 0.58 | 0.59 | 0.59 | 0 | 0.57
Philadelphia | Institutional / Public Service | Philadelphia Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 5186 |  |  | Philadelphia | Institutional / Public Service | Philadelphia Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 0.72
Philadelphia | Lodging | Philadelphia Lodging | 6161 | 6159 | 5886 | 6077 | 8760 |  |  | Philadelphia | Lodging | Philadelphia Lodging | 0.67 | 0.68 | 0.68 | 0 | 0.71
Philadelphia | Office | Philadelphia Office | 2036 | 2036 | 2027 | 2690 | 4063 |  |  | Philadelphia | Office | Philadelphia Office | 0.36 | 0.36 | 0.36 | 0 | 0.39
Philadelphia | Restaurant | Philadelphia Restaurant | #N/A | #N/A | #N/A | #N/A | 6226 |  |  | Philadelphia | Restaurant | Philadelphia Restaurant | #N/A | #N/A | #N/A | #N/A | 0.5
Philadelphia | Retail | Philadelphia Retail | 3225 | 3226 | 3185 | 2398 | 5092 |  |  | Philadelphia | Retail | Philadelphia Retail | 0.54 | 0.54 | 0.54 | 0 | 0.56
Philadelphia | Warehouse - Other | Philadelphia Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5168 |  |  | Philadelphia | Warehouse - Other | Philadelphia Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.3
Philadelphia | Warehouse - Refrigerated | Philadelphia Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Philadelphia | Warehouse - Refrigerated | Philadelphia Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.53
Pittsburgh | Education - College / University | Pittsburgh Education - College / University | 3916 | 3914 | 3749 | 4572 | 5982 |  |  | Pittsburgh | Education - College / University | Pittsburgh Education - College / University | 0.4 | 0.4 | 0.4 | 0.01 | 0.42
Pittsburgh | Education - Other | Pittsburgh Education - Other | 2676 | 2685 | 2409 | 3705 | 4415 |  |  | Pittsburgh | Education - Other | Pittsburgh Education - Other | 0.17 | 0.17 | 0.17 | 0 | 0.18
Pittsburgh | Grocery | Pittsburgh Grocery | #N/A | #N/A | #N/A | #N/A | 6718 |  |  | Pittsburgh | Grocery | Pittsburgh Grocery | #N/A | #N/A | #N/A | #N/A | 0.29
Pittsburgh | Health - Hospital | Pittsburgh Health - Hospital | 5593 | 5591 | 4093 | 8760 | 8760 |  |  | Pittsburgh | Health - Hospital | Pittsburgh Health - Hospital | 0.48 | 0.47 | 0.47 | 0.09 | 0.45
Pittsburgh | Health - Other | Pittsburgh Health - Other | 3900 | 3902 | 3571 | 5991 | 8760 |  |  | Pittsburgh | Health - Other | Pittsburgh Health - Other | 0.28 | 0.28 | 0.28 | 0 | 0.29
Pittsburgh | Industrial Manufacturing | Pittsburgh Industrial Manufacturing | 1606 | 1606 | 1602 | 1287 | 3869 |  |  | Pittsburgh | Industrial Manufacturing | Pittsburgh Industrial Manufacturing | 0.54 | 0.54 | 0.54 | 0 | 0.5
Pittsburgh | Institutional / Public Service | Pittsburgh Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 5201 |  |  | Pittsburgh | Institutional / Public Service | Pittsburgh Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 0.56
Pittsburgh | Lodging | Pittsburgh Lodging | 5686 | 5683 | 5239 | 6574 | 8760 |  |  | Pittsburgh | Lodging | Pittsburgh Lodging | 0.69 | 0.7 | 0.7 | 0 | 0.73
Pittsburgh | Office | Pittsburgh Office | 1739 | 1739 | 1730 | 3246 | 4240 |  |  | Pittsburgh | Office | Pittsburgh Office | 0.33 | 0.33 | 0.33 | 0 | 0.35
Pittsburgh | Restaurant | Pittsburgh Restaurant | #N/A | #N/A | #N/A | #N/A | 6300 |  |  | Pittsburgh | Restaurant | Pittsburgh Restaurant | #N/A | #N/A | #N/A | #N/A | 0.49
Pittsburgh | Retail | Pittsburgh Retail | 2795 | 2795 | 2757 | 2908 | 5146 |  |  | Pittsburgh | Retail | Pittsburgh Retail | 0.47 | 0.47 | 0.47 | 0 | 0.54
Pittsburgh | Warehouse - Other | Pittsburgh Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5110 |  |  | Pittsburgh | Warehouse - Other | Pittsburgh Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.23
Pittsburgh | Warehouse - Refrigerated | Pittsburgh Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Pittsburgh | Warehouse - Refrigerated | Pittsburgh Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.51
Scranton | Education - College / University | Scranton Education - College / University | 3828 | 3827 | 3500 | 4638 | 5876 |  |  | Scranton | Education - College / University | Scranton Education - College / University | 0.33 | 0.33 | 0.33 | 0.01 | 0.38
Scranton | Education - Other | Scranton Education - Other | 2310 | 2313 | 2164 | 3830 | 4490 |  |  | Scranton | Education - Other | Scranton Education - Other | 0.12 | 0.12 | 0.12 | 0 | 0.12
Scranton | Grocery | Scranton Grocery | #N/A | #N/A | #N/A | #N/A | 6725 |  |  | Scranton | Grocery | Scranton Grocery | #N/A | #N/A | #N/A | #N/A | 0.21
Scranton | Health - Hospital | Scranton Health - Hospital | 5266 | 5263 | 3713 | 8760 | 8760 |  |  | Scranton | Health - Hospital | Scranton Health - Hospital | 0.44 | 0.44 | 0.44 | 0.09 | 0.4
Scranton | Health - Other | Scranton Health - Other | 3710 | 3711 | 3687 | 6223 | 8760 |  |  | Scranton | Health - Other | Scranton Health - Other | 0.23 | 0.23 | 0.23 | 0 | 0.25
Scranton | Industrial Manufacturing | Scranton Industrial Manufacturing | 1558 | 1558 | 1558 | 1393 | 3902 |  |  | Scranton | Industrial Manufacturing | Scranton Industrial Manufacturing | 0.48 | 0.48 | 0.48 | 0 | 0.43
Scranton | Institutional / Public Service | Scranton Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 5207 |  |  | Scranton | Institutional / Public Service | Scranton Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 0.47
Scranton | Lodging | Scranton Lodging | 5655 | 5652 | 5353 | 6628 | 8760 |  |  | Scranton | Lodging | Scranton Lodging | 0.59 | 0.59 | 0.59 | 0 | 0.65
Scranton | Office | Scranton Office | 1638 | 1638 | 1631 | 3336 | 4228 |  |  | Scranton | Office | Scranton Office | 0.29 | 0.29 | 0.29 | 0 | 0.32
Scranton | Restaurant | Scranton Restaurant | #N/A | #N/A | #N/A | #N/A | 6315 |  |  | Scranton | Restaurant | Scranton Restaurant | #N/A | #N/A | #N/A | #N/A | 0.39
Scranton | Retail | Scranton Retail | 2735 | 2736 | 2702 | 2841 | 5149 |  |  | Scranton | Retail | Scranton Retail | 0.42 | 0.42 | 0.42 | 0 | 0.45
Scranton | Warehouse - Other | Scranton Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5188 |  |  | Scranton | Warehouse - Other | Scranton Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.15
Scranton | Warehouse - Refrigerated | Scranton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Scranton | Warehouse - Refrigerated | Scranton Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.48
Williamsburg | Education - College / University | Williamsburg Education - College / University | 3872 | 3871 | 3489 | 4487 | 5905 |  |  | Williamsburg | Education - College / University | Williamsburg Education - College / University | 0.4 | 0.39 | 0.39 | 0.01 | 0.44
Williamsburg | Education - Other | Williamsburg Education - Other | 2573 | 2604 | 2423 | 3658 | 4377 |  |  | Williamsburg | Education - Other | Williamsburg Education - Other | 0.16 | 0.17 | 0.17 | 0 | 0.15
Williamsburg | Grocery | Williamsburg Grocery | #N/A | #N/A | #N/A | #N/A | 6710 |  |  | Williamsburg | Grocery | Williamsburg Grocery | #N/A | #N/A | #N/A | #N/A | 0.24
Williamsburg | Health - Hospital | Williamsburg Health - Hospital | 5628 | 5626 | 3670 | 8760 | 8760 |  |  | Williamsburg | Health - Hospital | Williamsburg Health - Hospital | 0.47 | 0.46 | 0.46 | 0.09 | 0.41
Williamsburg | Health - Other | Williamsburg Health - Other | 3818 | 3819 | 3722 | 6045 | 8760 |  |  | Williamsburg | Health - Other | Williamsburg Health - Other | 0.26 | 0.26 | 0.26 | 0 | 0.28
Williamsburg | Industrial Manufacturing | Williamsburg Industrial Manufacturing | 1633 | 1633 | 1632 | 1277 | 3829 |  |  | Williamsburg | Industrial Manufacturing | Williamsburg Industrial Manufacturing | 0.5 | 0.5 | 0.5 | 0 | 0.46
Williamsburg | Institutional / Public Service | Williamsburg Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 5184 |  |  | Williamsburg | Institutional / Public Service | Williamsburg Institutional / Public Service | #N/A | #N/A | #N/A | #N/A | 0.52
Williamsburg | Lodging | Williamsburg Lodging | 5776 | 5773 | 5328 | 6387 | 8760 |  |  | Williamsburg | Lodging | Williamsburg Lodging | 0.66 | 0.66 | 0.66 | 0 | 0.71
Williamsburg | Office | Williamsburg Office | 1711 | 1711 | 1702 | 3169 | 4139 |  |  | Williamsburg | Office | Williamsburg Office | 0.32 | 0.32 | 0.32 | 0 | 0.34
Williamsburg | Restaurant | Williamsburg Restaurant | #N/A | #N/A | #N/A | #N/A | 6286 |  |  | Williamsburg | Restaurant | Williamsburg Restaurant | #N/A | #N/A | #N/A | #N/A | 0.45
Williamsburg | Retail | Williamsburg Retail | 2898 | 2898 | 2847 | 2660 | 5134 |  |  | Williamsburg | Retail | Williamsburg Retail | 0.47 | 0.47 | 0.47 | 0 | 0.49
Williamsburg | Warehouse - Other | Williamsburg Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 5028 |  |  | Williamsburg | Warehouse - Other | Williamsburg Warehouse - Other | #N/A | #N/A | #N/A | #N/A | 0.2
Williamsburg | Warehouse - Refrigerated | Williamsburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 4041 |  |  | Williamsburg | Warehouse - Refrigerated | Williamsburg Warehouse - Refrigerated | #N/A | #N/A | #N/A | #N/A | 0.51
Calculation 2: Run Hours/CF Motors | [8 empty] | Default Load Profiles for HVAC Fans and Pumps
Line Item | Location | Type | Concatenate | Motor Type | Column | Run Hours | CF |  | Equipment Type | Flow Fraction (%)
1 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
2 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | HVAC Fan | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.3 | 0.2 | 0.15 | 0.05
3 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | HVAC Pump | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.3 | 0.2 | 0.1 | 0.05 | 0
4 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | Supply/Return and Cooling Tower Fan Power Part Load Ratios
5 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | Control Type | Flow Fraction (%) 0: Flow Fraction (%)
6 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
7 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | Constant Volume | [11 empty] | 1 | bar: Flow Fraction (%) 0 to Flow Fraction (%) 100
8 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | Two-Speed | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 0.95
9 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | Air Foil/Backward Incline | 0.56 | 0.53 | 0.53 | 0.57 | 0.64 | 0.72 | 0.8 | 0.89 | 0.96 | 1.02 | 1.05 | 0.8965
10 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | Air Foil/Backward Incline with Inlet Guide Vanes | 0.47 | 0.53 | 0.56 | 0.57 | 0.59 | 0.6 | 0.62 | 0.67 | 0.74 | 0.85 | 1 | 0.7105
[9 empty] | Forward Curved | 0.2 | 0.22 | 0.26 | 0.3 | 0.37 | 0.45 | 0.54 | 0.65 | 0.77 | 0.91 | 1.06 | 0.6915
Table 13: Vlookup Column |  |  | Table 14: HVAC VFD Controls | [5 empty] | Forward Curved with Inlet Guide Vanes | 0.2 | 0.21 | 0.22 | 0.23 | 0.26 | 0.31 | 0.39 | 0.49 | 0.63 | 0.81 | 1.04 | 0.5555
Type | Number |  | Type | ESF | DSF |  |  |  | Variable Frequency Drive | 0.05 | 0.05 | 0.05 | 0.08 | 0.13 | 0.2 | 0.3 | 0.43 | 0.6 | 0.8 | 1.03 | 0.5005
Chilled Water Pump | 2 |  | Constant Volume | 0.534 | 0.347 |  |  |  | HVAC Pump Power Part Load Ratios
Cooling Tower Fan | 3 |  | Air Foil/Back Incline | 0.354 | 0.26 |  |  |  | Control Type | Flow Fraction (%) 0: Flow Fraction (%)
Condenser Water Pump | 4 |  | Air Foil/Back Incline w/Inlet Guide Vanes | 0.227 | 0.13 |  |  |  |  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Heating Hot Water Pump | 5 |  | Forward Curved | 0.179 | 0.136 |  |  |  | Constant Volume | [11 empty] | 1 | bar: Flow Fraction (%) 0 to Flow Fraction (%) 100
Supply Fan | 6 |  | Forward Curve w/ Inlet Guide Vanes | 0.092 | 0.029 |  |  |  | Throttle Valve | 0.55 | 0.61 | 0.67 | 0.73 | 0.78 | 0.82 | 0.87 | 0.9 | 0.94 | 0.97 | 1 | 0.862
|  |  | Chilled Water Pump | 0.411 | 0.299 |  |  |  | Variable Frequency Drive | 0.27 | 0.19 | 0.14 | 0.13 | 0.15 | 0.21 | 0.3 | 0.43 | 0.6 | 0.79 | 1.03 | 0.339
|  |  | Hot Water Pump | 0.424 | 0
Calculation 3: Run hours/CF VFD
Line Item | Location | Type | Concatenate | Motor Type | Column | Run Hours | CF
1 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
2 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
3 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
4 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
5 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
6 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
7 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
8 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
9 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
10 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
Table 15: EFLH Heat | [9 empty] | Flow Fraction (%) 10: Table 16: EFLH Cool
Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport |  | Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Education - College / University | 719 | 984 | 1078 | 857 | 552 | 464 | 651 | 824 | 655 |  | Education - College / University | 640 | 440 | 369 | 478 | 657 | 734 | 594 | 533 | 595
Education - Other | 636 | 910 | 1018 | 666 | 741 | 646 | 884 | 925 | 655 |  | Education - Other | 267 | 163 | 139 | 185 | 310 | 345 | 273 | 217 | 239
Grocery | 733 | 1068 | 1068 | 534 | 1269 | 1217 | 564 | 1737 | 1419 |  | Grocery | 654 | 542 | 542 | 636 | 453 | 536 | 638 | 434 | 442
Health - Hospital | 147 | 81 | 71 | 95 | 361 | 345 | 418 | 106 | 154 |  | Health - Hospital | 1030 | 977 | 977 | 1038 | 892 | 1059 | 788 | 1022 | 1013
Health - Other | 944 | 1432 | 1630 | 1304 | 854 | 805 | 1023 | 1193 | 958 |  | Health - Other | 477 | 397 | 350 | 481 | 540 | 684 | 511 | 467 | 476
Industrial Manufacturing | 406 | 500 | 568 | 473 | 374 | 339 | 400 | 441 | 346 |  | Industrial Manufacturing | 570 | 361 | 309 | 411 | 616 | 682 | 530 | 445 | 478
Institutional / Public Service | 1178 | 1489 | 1719 | 1437 | 1098 | 1121 | 1163 | 1401 | 1066 |  | Institutional / Public Service | 753 | 516 | 455 | 607 | 820 | 1087 | 706 | 629 | 685
Lodging | 2371 | 3219 | 3846 | 3077 | 2159 | 2017 | 2411 | 2591 | 2403 |  | Lodging | 1386 | 1205 | 1084 | 1392 | 1523 | 1732 | 1478 | 1348 | 1384
Multifamily (Common Areas) | 277 | 320 | 354 | 322 | 263 | 259 | 264 | 281 | 278 |  | Multifamily (Common Areas) | 1395 | 654 | 577 | 769 | 1482 | 1647 | 1176 | 991 | 1052
Office | 321 | 159 | 527 | 422 | 330 | 281 | 344 | 329 | 340 |  | Office | 458 | 213 | 323 | 412 | 565 | 704 | 721 | 500 | 466
Restaurant | 1151 | 1865 | 2109 | 1687 | 1040 | 993 | 1340 | 1501 | 1241 |  | Restaurant | 550 | 429 | 374 | 513 | 590 | 791 | 632 | 522 | 594
Retail | 809 | 1085 | 1221 | 980 | 648 | 632 | 781 | 855 | 675 |  | Retail | 735 | 535 | 464 | 620 | 742 | 911 | 816 | 603 | 648
Warehouse - Other | 847 | 1108 | 1258 | 1114 | 843 | 900 | 978 | 1008 | 800 |  | Warehouse - Other | 174 | 97 | 86 | 114 | 235 | 346 | 192 | 130 | 178
Warehouse - Refrigerated | 363 | 613 | 668 | 534 | 307 | 222 | 409 | 439 | 328 |  | Warehouse - Refrigerated | 3130 | 3048 | 3010 | 3080 | 3163 | 3200 | 3116 | 3094 | 3135
Table 17: CFs ECM | [9 empty] | Flow Fraction (%) 10: Table 18: Fan Application; Flow Fraction (%) 30: Motor Type; Flow Fraction (%) 40: Assumed Efficiency
Space and/or Building Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Flow Fraction (%) 10: Heating Only; Flow Fraction (%) 30: SP; Flow Fraction (%) 40: 0.4
Education - College / University | 0.48 | 0.4 | 0.37 | 0.38 | 0.48 | 0.51 | 0.48 | 0.45 | 0.49 | Flow Fraction (%) 10: Cooling Only; Flow Fraction (%) 30: PSC; Flow Fraction (%) 40: 0.5
Education - Other | 0.12 | 0.09 | 0.07 | 0.09 | 0.18 | 0.19 | 0.18 | 0.13 | 0.15 | Flow Fraction (%) 10: Ventilation Only; Flow Fraction (%) 30: ECM; Flow Fraction (%) 40: 0.7
Grocery | 0.33 | 0.26 | 0.26 | 0.27 | 0.24 | 0.26 | 0.27 | 0.21 | 0.24 | Flow Fraction (%) 10: Heating & Cooling
Health - Hospital | 0.43 | 0.36 | 0.34 | 0.37 | 0.39 | 0.44 | 0.39 | 0.37 | 0.42 | Flow Fraction (%) 10: Heating & Ventilation
Health - Other | 0.26 | 0.25 | 0.23 | 0.27 | 0.3 | 0.34 | 0.32 | 0.28 | 0.29 | Flow Fraction (%) 10: Cooling & Ventilation
Industrial Manufacturing | 0.51 | 0.37 | 0.33 | 0.39 | 0.55 | 0.6 | 0.53 | 0.45 | 0.48 | Flow Fraction (%) 10: Heating & Cooling & Ventilation
Institutional / Public Service | 0.53 | 0.38 | 0.34 | 0.45 | 0.6 | 0.72 | 0.56 | 0.48 | 0.52
Lodging | 0.72 | 0.73 | 0.71 | 0.77 | 0.78 | 0.83 | 0.83 | 0.73 | 0.78
Multifamily (Common Areas) | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48
Office | 0.32 | 0.16 | 0.26 | 0.31 | 0.41 | 0.27 | 0.35 | 0.36 | 0.37
Restaurant | 0.38 | 0.36 | 0.33 | 0.37 | 0.42 | 0.5 | 0.49 | 0.39 | 0.45
Retail | 0.52 | 0.45 | 0.42 | 0.46 | 0.53 | 0.57 | 0.56 | 0.47 | 0.49
Warehouse - Other | 0.18 | 0.11 | 0.1 | 0.13 | 0.24 | 0.3 | 0.23 | 0.15 | 0.2
Warehouse - Refrigerated | 0.5 | 0.47 | 0.45 | 0.48 | 0.52 | 0.53 | 0.51 | 0.48 | 0.51
Table 18: Pump Application
Heating Circulation
Domestic Hot Water
Calculation: Run Hours/CF High Efficiency Pumps | [8 empty] | Pump Type | Flow Fraction (%) 0: PEIbase
Line Item | Location | Type | Concatenate | Motor Type | Column | Run Hours | CF |  |  | Flow Fraction (%) 0: Constant Speed; Flow Fraction (%) 10: Variable Speed
1 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | ESCC, 1800 RPM | Flow Fraction (%) 0: 1; Flow Fraction (%) 10: 0.49
2 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | ESCC, 3600 RPM | Flow Fraction (%) 0: 0.96; Flow Fraction (%) 10: 0.51
3 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | ESFM, 1800 RPM | Flow Fraction (%) 0: 0.98; Flow Fraction (%) 10: 0.49
4 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | ESFM, 3600 RPM | Flow Fraction (%) 0: 0.99; Flow Fraction (%) 10: 0.51
5 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | IL | Flow Fraction (%) 0: 0.99; Flow Fraction (%) 10: 0.5
6 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | RSV | Flow Fraction (%) 0: 0.98; Flow Fraction (%) 10: 0.5
7 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A |  | ST | Flow Fraction (%) 0: 0.96; Flow Fraction (%) 10: 0.6
8 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
9 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A
10 | 0 | 0 | 0 0 | 0 | #N/A | #N/A | #N/A

## Data Export (hidden)
Measure Type | Measure Code | Quantity | Per Unit Incentive | Non PPL Incentive Amount Received | Total PPL Incentive | Manufacturer | Model # | Nozzle Size | Compressor Control Type | Motor Rated Horsepower (HP) | Motor Type | ηmotor | Annual Run Hours of Motor (RHRS) | PSIG - Orifice Diameter | HVAC Fan/Pump Control Type | Total kW Savings | Total kWh savings | Facility schedule | Pressure | Space Type | Pump Type | Baseline Watts | Energy Efficient Watts

## Version Log (hidden)
Version Log
Original Author: |  | Tom Cosgro | QA/QC Engineer(s):
Primary Developer: |  | Jeremy Selwyn | Senior Engineer Approval:
Version | Date | Reason for Change | Change Description | Contact, Department
1 | 2016-04-20 | Document created | Adapted the TRM Motor & Drives tool for use in the PPL Program | Jeremy Selwyn, Engineering
1.1 | 2017-01-16 | Unprotect input fields | ECM Circ Fan and VSD Kitchen have protected user inputs | Jeannie Sikora, Engineering
2 | 2017-03-28 | TRM Errata | Correction to Energy Interactive Factor within kWh equation, Change to HP option set and wattage lookup values | Mary Clayton, Core Engineering
3 | 2018-07-16 | Update format | Update format of calculator to match other PPL Calculator | Ryan Novosedliak, Engineering
3 | 2018-11-30 | PPl branding |  | Tom Cosgro
4 | 2021-06-01 | Phase IV Update | Update to 2021 TRM for Phase IV | Michael Stevenson

## Supply Fans (hidden)
Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
Education - College / University | CF | 0.43 | 0.3 | 0.24 | 0.32 | 0.44 | 0.47 | 0.42 | 0.38 | 0.44 | Education - College / University | Run Hours | 6042 | 6054 | 6126 | 6139 | 5860 | 5966 | 5982 | 5876 | 5905 | Education - College / University | CF | 0.43 | 0.3 | 0.24 | 0.32 | 0.44 | 0.47 | 0.42 | 0.38 | 0.44
Education - College / University | Run Hours | 6042 | 6054 | 6126 | 6139 | 5860 | 5966 | 5982 | 5876 | 5905 | Education - Other | Run Hours | 4380 | 4583 | 4718 | 4572 | 4313 | 4384 | 4415 | 4490 | 4377 | Education - Other | CF | 0.12 | 0.08 | 0.07 | 0.09 | 0.17 | 0.18 | 0.18 | 0.12 | 0.15
Education - Other | CF | 0.12 | 0.08 | 0.07 | 0.09 | 0.17 | 0.18 | 0.18 | 0.12 | 0.15 | Grocery | Run Hours | 6708 | 6764 | 6810 | 6738 | 6692 | 6669 | 6718 | 6725 | 6710 | Grocery | CF | 0.24 | 0.21 | 0.19 | 0.22 | 0.24 | 0.26 | 0.29 | 0.21 | 0.24
Education - Other | Run Hours | 4380 | 4583 | 4718 | 4572 | 4313 | 4384 | 4415 | 4490 | 4377 | Health - Hospital | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health - Hospital | CF | 0.43 | 0.24 | 0.29 | 0.39 | 0.45 | 0.51 | 0.45 | 0.4 | 0.41
Grocery | CF | 0.24 | 0.21 | 0.19 | 0.22 | 0.24 | 0.26 | 0.29 | 0.21 | 0.24 | Health - Other | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health - Other | CF | 0.24 | 0.21 | 0.17 | 0.23 | 0.29 | 0.31 | 0.29 | 0.25 | 0.28
Grocery | Run Hours | 6708 | 6764 | 6810 | 6738 | 6692 | 6669 | 6718 | 6725 | 6710 | Industrial Manufacturing | Run Hours | 3831 | 3981 | 4080 | 3977 | 3769 | 3838 | 3869 | 3902 | 3829 | Industrial Manufacturing | CF | 0.48 | 0.34 | 0.28 | 0.38 | 0.53 | 0.57 | 0.5 | 0.43 | 0.46
Health - Hospital | CF | 0.43 | 0.24 | 0.29 | 0.39 | 0.45 | 0.51 | 0.45 | 0.4 | 0.41 | Institutional / Public Service | Run Hours | 5188 | 5223 | 5248 | 5217 | 5172 | 5186 | 5201 | 5207 | 5184 | Institutional / Public Service | CF | 0.53 | 0.38 | 0.34 | 0.45 | 0.6 | 0.72 | 0.56 | 0.47 | 0.52
Health - Hospital | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Lodging | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Lodging | CF | 0.64 | 0.64 | 0.6 | 0.65 | 0.71 | 0.71 | 0.73 | 0.65 | 0.71
Health - Other | CF | 0.24 | 0.21 | 0.17 | 0.23 | 0.29 | 0.31 | 0.29 | 0.25 | 0.28 | Office | Run Hours | 4195 | 4473 | 4699 | 4441 | 4087 | 4063 | 4240 | 4228 | 4139 | Office | CF | 0.3 | 0.26 | 0.21 | 0.28 | 0.37 | 0.39 | 0.35 | 0.32 | 0.34
Health - Other | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Restaurant | Run Hours | 6282 | 2680 | 6487 | 6365 | 6252 | 6226 | 6300 | 6315 | 6286 | Restaurant | CF | 0.38 | 0.19 | 0.28 | 0.37 | 0.42 | 0.5 | 0.49 | 0.39 | 0.45
Industrial Manufacturing | CF | 0.48 | 0.34 | 0.28 | 0.38 | 0.53 | 0.57 | 0.5 | 0.43 | 0.46 | Retail | Run Hours | 5137 | 5188 | 5234 | 5158 | 5108 | 5092 | 5146 | 5149 | 5134 | Retail | CF | 0.5 | 0.4 | 0.36 | 0.44 | 0.53 | 0.56 | 0.54 | 0.45 | 0.49
Industrial Manufacturing | Run Hours | 3831 | 3981 | 4080 | 3977 | 3769 | 3838 | 3869 | 3902 | 3829 | Warehouse - Other | Run Hours | 5037 | 5189 | 5259 | 5222 | 4980 | 5168 | 5110 | 5188 | 5028 | Warehouse - Other | CF | 0.18 | 0.11 | 0.1 | 0.13 | 0.24 | 0.3 | 0.23 | 0.15 | 0.2
Institutional / Public Service | CF | 0.53 | 0.38 | 0.34 | 0.45 | 0.6 | 0.72 | 0.56 | 0.47 | 0.52 | Warehouse - Refrigerated | Run Hours | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | Warehouse - Refrigerated | CF | 0.5 | 0.46 | 0.43 | 0.48 | 0.52 | 0.53 | 0.51 | 0.48 | 0.51
Institutional / Public Service | Run Hours | 5188 | 5223 | 5248 | 5217 | 5172 | 5186 | 5201 | 5207 | 5184
Lodging | CF | 0.64 | 0.64 | 0.6 | 0.65 | 0.71 | 0.71 | 0.73 | 0.65 | 0.71
Lodging | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
Office | CF | 0.3 | 0.26 | 0.21 | 0.28 | 0.37 | 0.39 | 0.35 | 0.32 | 0.34
Office | Run Hours | 4195 | 4473 | 4699 | 4441 | 4087 | 4063 | 4240 | 4228 | 4139
Restaurant | CF | 0.38 | 0.19 | 0.28 | 0.37 | 0.42 | 0.5 | 0.49 | 0.39 | 0.45
Restaurant | Run Hours | 6282 | 2680 | 6487 | 6365 | 6252 | 6226 | 6300 | 6315 | 6286
Retail | CF | 0.5 | 0.4 | 0.36 | 0.44 | 0.53 | 0.56 | 0.54 | 0.45 | 0.49
Retail | Run Hours | 5137 | 5188 | 5234 | 5158 | 5108 | 5092 | 5146 | 5149 | 5134
Warehouse - Other | CF | 0.18 | 0.11 | 0.1 | 0.13 | 0.24 | 0.3 | 0.23 | 0.15 | 0.2
Warehouse - Other | Run Hours | 5037 | 5189 | 5259 | 5222 | 4980 | 5168 | 5110 | 5188 | 5028
Warehouse - Refrigerated | CF | 0.5 | 0.46 | 0.43 | 0.48 | 0.52 | 0.53 | 0.51 | 0.48 | 0.51
Warehouse - Refrigerated | Run Hours | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041 | 4041

## Chilled Water Pumps (hidden)
Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
Education – College / University | CF | 0.41 | 0.27 | 0.23 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.4 | Education - College / University | Run Hours | 4007 | 3436 | 3096 | 3641 | 4057 | 4311 | 3916 | 3828 | 3872 | Education - College / University | CF | 0.41 | 0.27 | 0.23 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.4
Education – College / University | Run Hours | 4007 | 3436 | 3096 | 3641 | 4057 | 4311 | 3916 | 3828 | 3872 | Education - Other | Run Hours | 2721 | 1849 | 1631 | 2175 | 2730 | 3505 | 2676 | 2310 | 2573 | Education - Other | CF | 0.1 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.16
Education - Other | CF | 0.1 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.16 | Health - Hospital | Run Hours | 5588 | 4801 | 4167 | 5109 | 5717 | 6086 | 5593 | 5266 | 5628 | Health - Hospital | CF | 0.46 | 0.38 | 0.31 | 0.42 | 0.5 | 0.54 | 0.48 | 0.44 | 0.47
Education - Other | Run Hours | 2721 | 1849 | 1631 | 2175 | 2730 | 3505 | 2676 | 2310 | 2573 | Health - Other | Run Hours | 3892 | 3093 | 2592 | 3456 | 4104 | 4535 | 3900 | 3710 | 3818 | Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26
Health - Hospital | CF | 0.46 | 0.38 | 0.31 | 0.42 | 0.5 | 0.54 | 0.48 | 0.44 | 0.47 | Industrial Manufacturing | Run Hours | 1735 | 1306 | 1086 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633 | Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.53 | 0.58 | 0.54 | 0.48 | 0.5
Health - Hospital | Run Hours | 5588 | 4801 | 4167 | 5109 | 5717 | 6086 | 5593 | 5266 | 5628 | Lodging | Run Hours | 5845 | 5042 | 4444 | 5198 | 6045 | 6161 | 5686 | 5655 | 5776 | Lodging | CF | 0.61 | 0.58 | 0.53 | 0.6 | 0.66 | 0.67 | 0.69 | 0.59 | 0.66
Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26 | Office | Run Hours | 1789 | 1402 | 1189 | 1585 | 1804 | 2036 | 1739 | 1638 | 1711 | Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Health - Other | Run Hours | 3892 | 3093 | 2592 | 3456 | 4104 | 4535 | 3900 | 3710 | 3818 | Retail | Run Hours | 2957 | 2416 | 2012 | 2653 | 3085 | 3225 | 2795 | 2735 | 2898 | Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.53 | 0.58 | 0.54 | 0.48 | 0.5
Industrial Manufacturing | Run Hours | 1735 | 1306 | 1086 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633
Lodging | CF | 0.61 | 0.58 | 0.53 | 0.6 | 0.66 | 0.67 | 0.69 | 0.59 | 0.66
Lodging | Run Hours | 5845 | 5042 | 4444 | 5198 | 6045 | 6161 | 5686 | 5655 | 5776
Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Office | Run Hours | 1789 | 1402 | 1189 | 1585 | 1804 | 2036 | 1739 | 1638 | 1711
Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Retail | Run Hours | 2957 | 2416 | 2012 | 2653 | 3085 | 3225 | 2795 | 2735 | 2898

## Cooling Tower Fan (hidden)
Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
Education – College / University | CF | 0.41 | 0.26 | 0.23 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.39 | Education - College / University | Run Hours | 4006 | 3435 | 3096 | 3641 | 4057 | 4309 | 3914 | 3827 | 3871 | Education - College / University | CF | 0.41 | 0.26 | 0.23 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.39
Education – College / University | Run Hours | 4006 | 3435 | 3096 | 3641 | 4057 | 4309 | 3914 | 3827 | 3871 | Education - Other | Run Hours | 2742 | 1851 | 1634 | 2178 | 2744 | 3517 | 2685 | 2313 | 2604 | Education - Other | CF | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17
Education - Other | CF | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17 | Health - Hospital | Run Hours | 5587 | 4798 | 4165 | 5107 | 5714 | 6084 | 5591 | 5263 | 5626 | Health - Hospital | CF | 0.45 | 0.37 | 0.31 | 0.41 | 0.49 | 0.54 | 0.47 | 0.44 | 0.46
Education - Other | Run Hours | 2742 | 1851 | 1634 | 2178 | 2744 | 3517 | 2685 | 2313 | 2604 | Health - Other | Run Hours | 3894 | 3093 | 2593 | 3457 | 4106 | 4537 | 3902 | 3711 | 3819 | Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26
Health - Hospital | CF | 0.45 | 0.37 | 0.31 | 0.41 | 0.49 | 0.54 | 0.47 | 0.44 | 0.46 | Industrial Manufacturing | Run Hours | 1735 | 1306 | 1086 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633 | Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.54 | 0.59 | 0.54 | 0.48 | 0.5
Health - Hospital | Run Hours | 5587 | 4798 | 4165 | 5107 | 5714 | 6084 | 5591 | 5263 | 5626 | Lodging | Run Hours | 5844 | 5039 | 4442 | 5197 | 6043 | 6159 | 5683 | 5652 | 5773 | Lodging | CF | 0.61 | 0.58 | 0.53 | 0.61 | 0.67 | 0.68 | 0.7 | 0.59 | 0.66
Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26 | Office | Run Hours | 1789 | 1402 | 1189 | 1585 | 1804 | 2036 | 1739 | 1638 | 1711 | Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Health - Other | Run Hours | 3894 | 3093 | 2593 | 3457 | 4106 | 4537 | 3902 | 3711 | 3819 | Retail | Run Hours | 2957 | 2416 | 2012 | 2653 | 3085 | 3226 | 2795 | 2736 | 2898 | Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.54 | 0.59 | 0.54 | 0.48 | 0.5
Industrial Manufacturing | Run Hours | 1735 | 1306 | 1086 | 1448 | 1742 | 1891 | 1606 | 1558 | 1633
Lodging | CF | 0.61 | 0.58 | 0.53 | 0.61 | 0.67 | 0.68 | 0.7 | 0.59 | 0.66
Lodging | Run Hours | 5844 | 5039 | 4442 | 5197 | 6043 | 6159 | 5683 | 5652 | 5773
Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Office | Run Hours | 1789 | 1402 | 1189 | 1585 | 1804 | 2036 | 1739 | 1638 | 1711
Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Retail | Run Hours | 2957 | 2416 | 2012 | 2653 | 3085 | 3226 | 2795 | 2736 | 2898

## Heating Hot Water Pumps (hidden)
Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
Education – College / University | CF | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0.01 | 0.01 | 0.01 | Education - College / University | Run Hours | 4548 | 5271 | 5900 | 5036 | 4250 | 4014 | 4572 | 4638 | 4487 | Education - College / University | CF | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0.01 | 0.01 | 0.01
Education – College / University | Run Hours | 4548 | 5271 | 5900 | 5036 | 4250 | 4014 | 4572 | 4638 | 4487 | Education - Other | Run Hours | 3651 | 4251 | 4722 | 4080 | 3492 | 3341 | 3705 | 3830 | 3658 | Education - Other | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Education - Other | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Health - Hospital | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Health - Hospital | CF | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
Education - Other | Run Hours | 3651 | 4251 | 4722 | 4080 | 3492 | 3341 | 3705 | 3830 | 3658 | Health - Other | Run Hours | 5934 | 6627 | 7170 | 6280 | 5823 | 5477 | 5991 | 6223 | 6045 | Health - Other | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health - Hospital | CF | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | Industrial Manufacturing | Run Hours | 1258 | 1684 | 1944 | 1555 | 1184 | 1028 | 1287 | 1393 | 1277 | Industrial Manufacturing | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health - Hospital | Run Hours | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | Lodging | Run Hours | 6469 | 7072 | 7587 | 6829 | 6155 | 6077 | 6574 | 6628 | 6387 | Lodging | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health - Other | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Office | Run Hours | 3214 | 3876 | 4446 | 3611 | 3014 | 2690 | 3246 | 3336 | 3169 | Office | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health - Other | Run Hours | 5934 | 6627 | 7170 | 6280 | 5823 | 5477 | 5991 | 6223 | 6045 | Retail | Run Hours | 2676 | 3183 | 3568 | 2960 | 2561 | 2398 | 2908 | 2841 | 2660 | Retail | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Industrial Manufacturing | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Industrial Manufacturing | Run Hours | 1258 | 1684 | 1944 | 1555 | 1184 | 1028 | 1287 | 1393 | 1277
Lodging | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lodging | Run Hours | 6469 | 7072 | 7587 | 6829 | 6155 | 6077 | 6574 | 6628 | 6387
Office | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office | Run Hours | 3214 | 3876 | 4446 | 3611 | 3014 | 2690 | 3246 | 3336 | 3169
Retail | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail | Run Hours | 2676 | 3183 | 3568 | 2960 | 2561 | 2398 | 2908 | 2841 | 2660

## Condenser Water Pumps (hidden)
Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg | Facility Type | Parameter | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsburg
Education - College / University | CF | 0.41 | 0.26 | 0.2 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.39 | Education - College / University | Run Hours | 3527 | 2938 | 2466 | 3063 | 3602 | 4030 | 3749 | 3500 | 3489 | Education - College / University | CF | 0.41 | 0.26 | 0.2 | 0.3 | 0.42 | 0.45 | 0.4 | 0.33 | 0.39
Education - College / University | Run Hours | 3527 | 2938 | 2466 | 3063 | 3602 | 4030 | 3749 | 3500 | 3489 | Education - Other | Run Hours | 2448 | 1733 | 1529 | 2039 | 2539 | 3346 | 2409 | 2164 | 2423 | Education - Other | CF | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17
Education - Other | CF | 0.11 | 0.08 | 0.07 | 0.09 | 0.18 | 0.18 | 0.17 | 0.12 | 0.17 | Health - Hospital | Run Hours | 3950 | 3546 | 3293 | 3698 | 3687 | 4168 | 4093 | 3713 | 3670 | Health - Hospital | CF | 0.45 | 0.37 | 0.29 | 0.41 | 0.49 | 0.54 | 0.47 | 0.44 | 0.46
Education - Other | Run Hours | 2448 | 1733 | 1529 | 2039 | 2539 | 3346 | 2409 | 2164 | 2423 | Health - Other | Run Hours | 3675 | 3100 | 2585 | 3394 | 3725 | 4304 | 3571 | 3687 | 3722 | Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26
Health - Hospital | CF | 0.45 | 0.37 | 0.29 | 0.41 | 0.49 | 0.54 | 0.47 | 0.44 | 0.46 | Industrial Manufacturing | Run Hours | 1735 | 1305 | 1084 | 1445 | 1737 | 1889 | 1602 | 1558 | 1632 | Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.54 | 0.59 | 0.54 | 0.48 | 0.5
Health - Hospital | Run Hours | 3950 | 3546 | 3293 | 3698 | 3687 | 4168 | 4093 | 3713 | 3670 | Lodging | Run Hours | 5544 | 4591 | 3939 | 4766 | 5569 | 5886 | 5239 | 5353 | 5328 | Lodging | CF | 0.61 | 0.58 | 0.53 | 0.61 | 0.67 | 0.68 | 0.7 | 0.59 | 0.66
Health - Other | CF | 0.24 | 0.2 | 0.16 | 0.22 | 0.28 | 0.3 | 0.28 | 0.23 | 0.26 | Office | Run Hours | 1781 | 1389 | 1177 | 1569 | 1792 | 2027 | 1730 | 1631 | 1702 | Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Health - Other | Run Hours | 3675 | 3100 | 2585 | 3394 | 3725 | 4304 | 3571 | 3687 | 3722 | Retail | Run Hours | 2889 | 2381 | 1986 | 2616 | 3025 | 3185 | 2757 | 2702 | 2847 | Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Industrial Manufacturing | CF | 0.53 | 0.4 | 0.32 | 0.43 | 0.54 | 0.59 | 0.54 | 0.48 | 0.5
Industrial Manufacturing | Run Hours | 1735 | 1305 | 1084 | 1445 | 1737 | 1889 | 1602 | 1558 | 1632
Lodging | CF | 0.61 | 0.58 | 0.53 | 0.61 | 0.67 | 0.68 | 0.7 | 0.59 | 0.66
Lodging | Run Hours | 5544 | 4591 | 3939 | 4766 | 5569 | 5886 | 5239 | 5353 | 5328
Office | CF | 0.29 | 0.25 | 0.2 | 0.27 | 0.35 | 0.36 | 0.33 | 0.29 | 0.32
Office | Run Hours | 1781 | 1389 | 1177 | 1569 | 1792 | 2027 | 1730 | 1631 | 1702
Retail | CF | 0.46 | 0.33 | 0.28 | 0.38 | 0.53 | 0.54 | 0.47 | 0.42 | 0.47
Retail | Run Hours | 2889 | 2381 | 1986 | 2616 | 3025 | 3185 | 2757 | 2702 | 2847