## Instructions
PPL Calculator for Commercial Refrigeration Measures
Note: This calculator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this calculator is deemed acceptable for the PPL Electric Utilities Non-Residential Energy Efficiency Program. However, the assumptions used by the applicant to calculate the annual savings will be reviewed by the Program Team, which is solely responsible for the final determination of the annual energy savings to be used in calculating the incentive amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities. For any questions, or assistance using this Calculator, please call 1-866-432-5501 or email us at pplbusiness@clearesult.com.
Input Instructions
Yellow cells indicate that user input is required. Cells with a * are required.
Grey cells are calculated values.
Worksheet Summary
Methodology
Provides methodology for savings estimations.
Project Summary
This provides summary of estimated savings along with some required inputs.
3.5.1 High Efficiency Refrigeration/Freezer Cases
This protocol estimates savings for installing high efficiency refrigeration and freezer cases that exceed federal efficiency standards. Eligible refrigerators and freezers are self-contained with vertical-closed transparent or solid doors. The measurement of energy and demand savings is based on algorithms with volume as the key variable.
3.5.2/3.5.3 High Efficiency Evaporative Fan Motors for Refrigerated Cases
This protocol covers energy and demand savings associated with the replacement of existing shaded-pole evaporator fan motors or Permanent Split Capacitor (PSC) motors in reach-in refrigerated display cases with an Electronically Commutated (ECM).
3.5.4 Evaporator Fan Controllers
This measure is for the installation of evaporator fan controls in medium-temperature walk-in coolers with no pre-existing controls.
3.5.5 Floating Head Pressure Controls
This protocol documents the energy savings attributed to FHPCs applied to a single-compressor refrigeration system in commercial applications. The baseline case is a refrigeration system without FHPC whereas the efficient case is a refrigeration system with FHPC.
3.5.6 Anti Sweat Heater Controls
Anti-sweat heater (ASH) controls sense the humidity in the store outside of reach-in, glass door refrigerated cases and turn off anti-sweat heaters during periods of low humidity.
3.5.7 Evaporator Coil Defrost Control
This measure is targeted to non-residential customers whose equipment uses electric defrost controls on small commercial walk-in freezer systems.
3.5.8 Variable Speed Refrigeration Compressor
This measure, VSD control for refrigeration systems and its eligibility targets applies to retrofit construction in the commercial and industrial building sectors; it is most applicable to grocery stores or food processing applications with refrigeration systems. This protocol is for a VSD control system replacing a slide valve control system.
3.5.9 Strip Curtains for Walk In Freezers and Coolers
This protocol documents the energy savings attributed to strip curtains applied on walk-in cooler and freezer doors in commercial applications.
3.5.10 Night Covers for Display Cases
This measure documents the energy savings associated with the installation of night covers on existing open-type refrigerated display cases, where covers are deployed during the facility’s unoccupied hours in order to reduce refrigeration energy consumption.
3.5.11 Auto Closer (Walk Ins Only)
This protocol documents the energy savings attributed to installation of auto closers in walk-in coolers and freezers. The auto-closer must be able to firmly close the door when it is within one inch of full closure. The walk-in door perimeter must be ≥ 16 ft.
3.5.12 Door Gaskets for Walk In and Reach In Coolers and Freezers
The following protocol for the measurement of energy and demand savings is applicable to commercial refrigeration and applies to the replacement of worn-out gaskets with new better-fitting gaskets. Applicable gaskets include those located on the doors of walk-in and/or reach-in coolers and freezers.
3.5.13 Special Doors with Low or Anti Sweat Heat for Low Temp Case
For this measure, a no-heat/low-heat clear glass door must be installed on an upright display case. It is limited to door heights of 57 inches or more. Doors must have either heat reflective treated glass, be gas filled, or both. This measure applies to low temperature cases only—those with a case temperature below 0°F. Doors must have 3 or more panes. Total door rail, glass, and frame heater amperage (@ 120 volt) cannot exceed 0.39 amps per door for low temperature display cases. Rebate is based on the door width (not including case frame).
3.5.14 Suction Pipe Insulation For Walk In Coolers and Freezers
This measure applies to the installation of insulation on existing bare suction lines (the larger diameter lines that run from the evaporator to the compressor) that are located outside of the refrigerated space for walk-in coolers and freezers. Insulation impedes heat transfer from the ambient air to the suction lines, thereby reducing undesirable system superheat.
3.5.15 Refrigerated Display Cases with Doors Replacing Open Cases
The eligible equipment is a new case with no sweat doors that meets federal standard requirements. If a lighting retrofit is included with the new case, it must consume the same amount of energy or less than the old lighting.
3.5.16 Adding Doors to Existing Refrigerated Display Cases
This measure considers adding doors to existing vertical open display cases. The baseline equipment is an existing vertical display case of medium temperature with no doors. The display cases should be medium temperature (typically for dairy, meats, or beverages) as opposed to low temperature (typically for frozen food and ice cream).
Version Log
The Version Log Worksheet tracks updates and changes made to the workbook.
Glossary of Inputs
Date | Date the estimator is completed.
Project Name | Name of project for reference.
Address | Physical location of project.
Installation Date | Date the project is completed.
Project Cost* | The cost associated with the project. Required for incentive calculation.
Location* | The nearest city to the project location.
Building Type* | The building type for the project. If your building type is not listed, please contact the PPL Program.
Unit Id | The ID of the unit for reference.
Manufacturer | The manufacturer of the installed unit.
Model Number | The model number of the installed unit.
Project Type* | The type of project be completed, either retrofit or new construction.
Case Type* | This identifies the case type in the individual measure.
Volume Category* | The volume grouping that the unit goes too.
Nameplate Volume* | The actual volume of the unit.
Door Type* | The type of door on the unit.
Quantity* | The quantity for the specific measures.
Cooling Type* | The cooling type used on the unit.
Existing Motor Type* | The kind of motor used before the change.
Motor Wattage* | The wattage of the motor.
Compressor Voltage* | The voltage of the compressor from the nameplate.
Compressor Amperage* | The amperage of the compressor from the nameplate.
Fan Voltage* | The voltage of the fan from the nameplate.
Fan Amperage* | The amperage of the fan from the nameplate.
Unit Type* | The type of the unit in the specific measure.
Tons* | The tonnage of the unit in the measure.
Strip Thickness >0.06 Inches* | Verification of the strip thickness.
Pre Existing Curtains* | Identification of pre existing conditions.
Area of Strip Curtains per Case (ft2)* | The area in sq. ft that the strip curtains will be installed in.
Temperature* | The operating temperature for the measure.
Width of Opening* | The width of the opening for the measure.
Operating Temp <0oF* | The verification of the operating temperature being less than 0 degrees.
BTUh/door* | The rated Btuh/door from the nameplate.
EER Rating* | The rated EER rating.
Glossary of Outputs
kWh Savings | This is the anticipated kWh savings of the line item or measure. | kWh
kW savings | This is the anticipated peak kW savings of the line item/measure.
Incentive | This is the estimated incentive based on project cost and kWh savings.
Run Hours | This is the prescriptive hours of use based on location and facility type.
Coincidence Factor | This is the prescriptive coincidence factor based on the location and facility type.
ESF | This is a Energy Savings Factor based on inputs from the VFD tab.
DSF | This is a Demand Savings Factor based on inputs from the VFD tab.

## Methodology Part 1 (hidden)
Savings Methodologies
High Efficiency Refrigeration/Freezer Cases | High-Efficiency Evaporator Fan Motors For Walk reach-In Refrigerated Cases | High-Efficiency Evaporator Fan Motors For Walk-In Refrigerated Cases | Evaporator Fan Controllers
Eligibility: To be eligible, refrigerators and freezers must be self-contained and have vertically-closed glass or solid doors . Methodology: The energy savings are obtained through the following equations - | Eligibility: This measure applies only to the replacement of functioning equipment. Methodology: The energy savings are obtained through the following equations - | Eligibility: This measure applies only to the replacement of functioning equipment. Methodology: The energy savings are obtained through the following equations - | Methodology: The energy savings are obtained through the following equations -
Floating Head Pressure Controls | Anti-Sweat Door Heater Controls | Evaporator Coil Defrost Controls | Variable Speed Refrigeration Compressor
Eligibility: To qualify for this measure, the FHPC must be installed in on a signelsingle-compressor refrigeration system in a commercial application. To qualify for this measure, a balanced-port or electronic expansion valve that is sized to meet the refrigeration load at 70ºF condensing temperature must be installed. This measure applies to FHPCs on a single-compressor (≥ 1 hp) refrigeration system in commercial applications. To be eligible, FHPCs must be programmed to have a minimum saturated condensing temperature of ≤ 70ºF. To qualify for this measure, aA balanced-port or electronic expansion valve that is sized to meet the refrigeration load at 70ºF condensing temperature must be installed. Alternately, a device which supplements the refrigeration to each evaporator, which is attached to a condenser that is reducing head pressure, can be installed. Methodology: The energy savings are obtained through the following equations - | Eligibility: To be eligible, ASH controls must be retrofit on reach-in glass door refrigerators with uncontrolled anti-sweat heaters. Methodology: The energy savings are obtained through the following equations - | Eligibility: To be eligible, an existing small commercial walk-in cooler or freezer without defrost controls must be retrofit with defrost controls. Methodology: The energy savings are obtained through the following equations - | Eligibility: To be eligible, a VSD control system must replace an existing slide valve control system on a refrigeration compressor. Methodology: The energy savings are obtained through the following equations -

## Methodology Part 2 (hidden)
Savings Methodologies
Strip Curtains for Walk-In Freezers amd Coolers | Night Covers For Display Cases | Auto Closers For Walk-In Cooler/Freezer Doors | Door Gaskets For Walk-In And Reach-In Coolers And Freezers
Eligibility: This measure applies when strip curtains are added to walk-in cooler and freezer door openings which previously had either no strip curtain or an ineffective strip curtain. Strip curtains must be installed in a grocery, convenience store, or restaurant and the curtain must be at least 0.06 inches thick. Special low temperature strip curtains must be used on low temperature applications. Methodology: The energy savings are obtained through the following equations - | Methodology: The energy savings are obtained through the following equations - | Eligibility: An auto-closer should be applied to the main insulated opaque door(s) of a walk-in cooler or freezer. This measure applies only to the new installation of an auto-closer on a door not previously equipped with an auto-closer and assumes the doors have strip curtains. The auto-closer must be able to firmly close a door that is within one inch of full closure. Door perimeter must measure ≥16 ft. Methodology: The energy savings are obtained through the following equations - | Methodology: The energy savings are obtained through the following equations -
Special Doors With Low Or No Anti-Sweat Heat For Low Temperature Cases | Suction Pipe Insulation For Walk-In Coolers And Freezers | Refrigerated Display Cases With Zero Heat Doors Replacing Open Cases | Adding Doors to Existing Refrigerated Display Cases
Eligibility: To be eligible, a no-heat/low-heat clear glass door, no less than 57 inches in height, must be installed on an upright display case in a new or retrofit application. New doors must have either heat reflective treated glass, be gas filled, or both. This measure applies to low temperature (<0°F) cases only. To be eligible, doors must have at least 3 panes of glass. Total door rail, glass, and frame heater amperage (@ 120 volt) cannot exceed 0.39 amps per door. Methodology: The energy savings are obtained through the following equations - | Eligibility: To be eligible, the suction pipe insulation must:  Installed in a grocery or restaurant walk-in cooler or freezer  Insulate bare refrigeration suction lines 1-5/8 inches in diameter or less on existing equipment only  For medium temperature lines, be 3/4 inch-thick, flexible, closed-cell, nitrite rubber or an equivalent insulation  For low temperature lines, be 1-inch-thick flexible, closed-cell, nitrite rubber or an equivalent insulation  Be protected from the weather, if outdoors (i.e. with medium-gauge aluminum jacket) Methodology: The energy savings are obtained through the following equations - | Eligibility: This applies only to the replacement of open, vertical display cases with new closed display cases having no antisweat heater controls (zero energy doors). Horizontal cases are not eligible and should be submitted as custom. If a lighting retrofit is included with the new case, it must consume the same amount of energy or less than the old lighting. Upgrades to lighting or other system components should be submitted separately. Methodology: The energy savings are obtained through the following equations - | Eligibility: The eligible retrofit equipment is either no sweat doors or doors with anti-sweat heaters. If a lighting retrofit is included with the new doors, it must consume the same amount of energy or less energy than the old lighting. Upgrades to lighting or other system components should be processed separately. Horizontal cases are not eligible and should be processed as custom. Methodology: The energy savings are obtained through the following equations -

## Project Summary
[5 empty] | Version | 4
[5 empty] | Last Updated | 2021-06-01
Project Summary
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Date
Project Name
Address
Installation Date
Project Cost* | 10000
Location* | Bradford
Building Type* | Grocery
Measure | kWh Savings | kW Savings | Total Uncapped Incentive | Incentive
High Efficiency Refrigeration/Freezer Cases | 2419.59 | 0.28 | 104.37 | 104.37
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 8773.23 | 1.0017 | 375.8 | 375.8
Evaporator Fan Controllers | 6880.98 | 0 | 137.62 | 137.62
Floating Head Pressure Controls | 57414.82 | 0 | 1148.3 | 1148.3
Anti Sweat Heater Controls | 13043 | 1.404 | 541.66 | 541.66
Evaporator Coil Defrost Control | 390.53 | 0.8019 | 168.19 | 168.19
Variable Speed Refrigeration Compressor | 18656 | 2.42 | 857.12 | 857.12
Strip Curtains for Walk In Freezers and Coolers | 1271 | 0.1603 | 57.48 | 57.48
Night Covers for Display Cases | 131.4 | 0 | 2.63 | 2.63
Auto Closer (Walk Ins Only) | 2734 | 0.951 | 244.88 | 244.88
Door Gaskets for Walk In and Reach In Coolers and Freezers | 1042 | 0.136 | 48.04 | 48.04
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 4179.21 | 0.4771 | 179.01 | 179.01
Suction Pipe Insulation For Walk In Coolers and Freezers | 110.3 | 0.021 | 6.41 | 6.41
Refrigerated Display Cases with Doors Replacing Open Cases | 1215.2 | 0.1388 | 52.07 | 52.07
Adding Doors to Existing Refrigerated Display Cases | 3130.63 | 0.3574 | 134.1 | 134.1
Air Cooled Refrigerated Condenser | 1296 | 0.1429 | 54.5 | 54.5
Refrigeration Economizers | 5230.54 | 0 | 104.63 | 104.63
Total | 127918.43 | 8.2921 | 4216.81 | 4216.81

## High Eff Ref Freeze
Last Updated: [Date], See Version Log | [10 empty] | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
High Efficiency Refrigeration/Freezer Cases
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [8 empty] | Calculations | [5 empty] | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Case Type* | Volume Category* | Nameplate Volume* | Door Type* | Quantity* | Baseline Eff | ECM Savings | Days/Year | Hrs/Day | kWh Savings | kW Savings
| 1 |  |  |  | Retrofit | Freezer | V < 15 | 13 | Solid | 1 | 4.24 | 3.63 | 365 | 24 | 222.65 | 0.03 | 10.45 | 10.45
| 2 |  |  |  | Retrofit | Freezer | 15 ≤ V < 30 | 15 | Solid | 1 | 4.68 | 4.048 | 365 | 24 | 230.68 | 0.03 | 10.61 | 10.61
| 3 |  |  |  | Retrofit | Freezer | 30 ≤ V < 50 | 45 | Solid | 1 | 11.28 | 10.122 | 365 | 24 | 422.67 | 0.05 | 18.45 | 18.45
| 4 |  |  |  | Retrofit | Freezer | 50 ≤ V | 55 | Solid | 1 | 13.48 | 12.255 | 365 | 24 | 447.13 | 0.05 | 18.94 | 18.94
| 5 |  |  |  | Retrofit | Refrigeration | V < 15 | 13 | Solid | 1 | 2.01 | 1.256 | 365 | 24 | 275.21 | 0.03 | 11.5 | 11.5
| 6 |  |  |  | Retrofit | Refrigeration | 15 ≤ V < 30 | 15 | Solid | 1 | 2.11 | 1.3 | 365 | 24 | 295.65 | 0.03 | 11.91 | 11.91
| 7 |  |  |  | Retrofit | Refrigeration | 30 ≤ V < 50 | 40 | Solid | 1 | 3.36 | 2.69 | 365 | 24 | 244.55 | 0.03 | 10.89 | 10.89
| 8 |  |  |  | Retrofit | Refrigeration | 50 ≤ V | 50 | Solid | 1 | 3.86 | 3.09 | 365 | 24 | 281.05 | 0.03 | 11.62 | 11.62
| 9 | [9 empty] | 0 | 0 | 365 | 24 | 0 | 0 | 0 | 0
| 10 | [9 empty] | 0 | 0 | 365 | 24 | 0 | 0 | 0 | 0

## Evap Fan Motors
Last Updated: [Date], See Version Log | [14 empty] | HIDE
High Efficiency Evaporative Fan Motors for Refrigerated Cases
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [10 empty] | Savings |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Case Type* | Cooling Type* | Existing Motor Type* | Efficient Motor Type* | Baseline Motor Wattage* HP | Efficient Motor Wattage* HP | Quantity* | Savings kWh | Savings kW
| 1 |  | Penguin | Macaroni | Retrofit | Walk In | Freezer | SP | ECM | 0.25 | 0.25 | 1 | 602.6 | 0.0688 | 25.81 | 25.81
| 2 |  |  |  | Retrofit | Reach In | Refrigeration | SP | ECM | 0.33 | 0.25 | 1 | 1530.87 | 0.1748 | 65.58 | 65.58
| 3 |  |  |  | Retrofit | Walk In | Freezer | PSC | PMS | 0.05 | 0.05 | 1 | 779.29 | 0.089 | 33.39 | 33.39
| 4 |  |  |  | Retrofit | Reach In | Refrigeration | PSC | PMS | 0.15 | 0.15 | 1 | 2015.98 | 0.2301 | 86.34 | 86.34
| 5 |  |  |  | Retrofit | Reach In | Refrigeration | PSC | ECM | 0.15 | 0.15 | 1 | 1955.7 | 0.2233 | 83.77 | 83.77
| 6 |  |  |  | Retrofit | Walk In | Freezer | SP | ECM | 0.15 | 0.15 | 1 | 361.56 | 0.0413 | 15.49 | 15.49
| 7 |  |  |  | Retrofit | Reach In | Refrigeration | SP | PMS | 0.15 | 0.15 | 1 | 353.4 | 0.0403 | 15.13 | 15.13
| 8 |  |  |  | Retrofit | Reach In | Freezer | SP | PMS | 0.15 | 0.15 | 1 | 450.71 | 0.0515 | 19.31 | 19.31
| 9 |  |  |  | Retrofit | Reach In | Freezer | SP | ECM | 0.15 | 0.15 | 1 | 361.56 | 0.0413 | 15.49 | 15.49
| 10 |  |  |  | Retrofit | Walk In | Freezer | SP | ECM | 0.15 | 0.15 | 1 | 361.56 | 0.0413 | 15.49 | 15.49

## Fan Control
Last Updated: [Date], See Version Log | [12 empty] | HIDE
Evaporator Fan Controllers
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [8 empty] | Savings |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Cooling Type* | Namplate Rated Horsepower* | Fan Control Type* | Motor Type* | Quantity* | kWh Savings | kW Savings
| 1 |  |  |  | Retrofit | Freezer | 0.25 | Unknown | SP | 1 | 2699.98 | 0 | 54 | 54
| 2 |  |  |  |  | Refrigeration | 0.25 | Unknown | SP | 1 | 2117 | 0 | 42.34 | 42.34
| 3 |  |  |  |  | Freezer | 0.25 | Unknown | ECM | 1 | 1157 | 0 | 23.14 | 23.14
| 4 |  |  |  |  | Refrigeration | 0.25 | Unknown | ECM | 1 | 907 | 0 | 18.14 | 18.14
| 5 |  |  |  |  | Freezer |  | Unknown | SP |  | 0 | 0 | 0 | 0
| 6 |  |  |  |  | Freezer |  | Unknown | SP |  | 0 | 0 | 0 | 0
| 7 |  |  |  |  | Freezer |  | Unknown | SP |  | 0 | 0 | 0 | 0
| 8 |  |  |  |  | Freezer |  | Unknown | SP |  | 0 | 0 | 0 | 0
| 9 |  |  |  |  | Freezer |  | Unknown | SP |  | 0 | 0 | 0 | 0
| 10 |  |  |  |  | Freezer |  | Unknown | SP |  | 0 | 0 | 0 | 0

## Float Control
Last Updated: [Date], See Version Log | [8 empty] | HIDE | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
Floating Head Pressure Controls
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [6 empty] | Calculations | [6 empty] | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Unit Type* | Tons* | Quantity* | City | Column Number | kWh/HP | COP | HP/Tons | kWh Savings | kW Savings
| 1 |  |  |  | Retrofit | Condesing Unit - Refrigerator | 10 | 1 | Bradford | 2 | 765 | 2.51 | 4.715 | 14370.42 | 0 | 287.41 | 287.41
| 2 |  |  |  | Retrofit | Condesing Unit - Freezer | 10 | 1 | Bradford | 3 | 860 | 1.3 | 4.715 | 31191.54 | 0 | 623.83 | 623.83
| 3 |  |  |  | Retrofit | Remote Condeser - Refrigerator | 10 | 1 | Bradford | 4 | 511 | 2.5 | 4.715 | 9637.46 | 0 | 192.75 | 192.75
| 4 |  |  |  | Retrofit | Remote Condeser - Freezer | 1 | 1 | Bradford | 5 | 686 | 1.46 | 4.715 | 2215.4 | 0 | 44.31 | 44.31
| 5 | [7 empty] | Bradford | 0 | 0 | 0 | 4.715 | 0 | 0 | 0 | 0
| 6 | [7 empty] | Bradford | 0 | 0 | 0 | 4.715 | 0 | 0 | 0 | 0
| 7 | [7 empty] | Bradford | 0 | 0 | 0 | 4.715 | 0 | 0 | 0 | 0
| 8 | [7 empty] | Bradford | 0 | 0 | 0 | 4.715 | 0 | 0 | 0 | 0
| 9 | [7 empty] | Bradford | 0 | 0 | 0 | 4.715 | 0 | 0 | 0 | 0
| 10 | [7 empty] | Bradford | 0 | 0 | 0 | 4.715 | 0 | 0 | 0 | 0

## Anti Sweat
Last Updated: [Date], See Version Log | [8 empty] | HIDE | HIDE |  |  | HIDE
Anti Sweat Heater Controls
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [6 empty] | Calculations |  |  |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Case Type* | Control Type* | Number of Doors* | kWh/door | kW/door | kWh Savings | kW Savings
| 1 |  | Good | 1234 | Retrofit | Refrigeration | Micropulse | 16 | 682 | 0.073 | 10912 | 1.168 | 451.84 | 451.84
| 2 |  |  |  | Retrofit | Freezer | On/Off | 1 | 543 | 0.062 | 543 | 0.062 | 23.26 | 23.26
| 3 |  |  |  | Retrofit | Freezer | Unknown | 1 | 770 | 0.086 | 770 | 0.086 | 32.6 | 32.6
| 4 |  |  |  | Retrofit | Freezer | Micropulse | 1 | 818 | 0.088 | 818 | 0.088 | 33.96 | 33.96
| 5 | [5 empty] | On/Off |  | 0 | 0 | 0 | 0 | 0 | 0
| 6 | [5 empty] | On/Off |  | 0 | 0 | 0 | 0 | 0 | 0
| 7 | [5 empty] | On/Off |  | 0 | 0 | 0 | 0 | 0 | 0
| 8 | [5 empty] | On/Off |  | 0 | 0 | 0 | 0 | 0 | 0
| 9 | [5 empty] | On/Off |  | 0 | 0 | 0 | 0 | 0 | 0
| 10 | [5 empty] | On/Off |  | 0 | 0 | 0 | 0 | 0 | 0

## Coil Defrost
Last Updated: [Date], See Version Log | [7 empty] | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
Evaporator Coil Defrost Control
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [5 empty] | Calculations | [5 empty] | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Case Type* | Number of Fans* | kW DE | SVG | BF | HOU | kWh Savings | kW Savings
| 1 |  | junk | 5678 | Retrofit | Freezer | 1 | 0.9 | 0.3 | 1.67 | 487 | 219.59 | 0.4509 | 94.57 | 94.57
| 2 |  |  |  | Retrofit | Refrigeration | 1 | 0.9 | 0.3 | 1.3 | 487 | 170.94 | 0.351 | 73.62 | 73.62
| 3 | [6 empty] | 0.9 | 0.3 | 0 | 487 | 0 | 0 | 0 | 0
| 4 | [6 empty] | 0.9 | 0.3 | 0 | 487 | 0 | 0 | 0 | 0
| 5 | [6 empty] | 0.9 | 0.3 | 0 | 487 | 0 | 0 | 0 | 0
| 6 | [6 empty] | 0.9 | 0.3 | 0 | 487 | 0 | 0 | 0 | 0
| 7 | [6 empty] | 0.9 | 0.3 | 0 | 487 | 0 | 0 | 0 | 0
| 8 | [6 empty] | 0.9 | 0.3 | 0 | 487 | 0 | 0 | 0 | 0
| 9 | [6 empty] | 0.9 | 0.3 | 0 | 487 | 0 | 0 | 0 | 0
| 10 | [6 empty] | 0.9 | 0.3 | 0 | 487 | 0 | 0 | 0 | 0

## VS Ref Comp
Last Updated: [Date], See Version Log | [7 empty] | HIDE | HIDE |  |  | HIDE
Variable Speed Refrigeration Compressor
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [5 empty] | Calculations |  |  |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Tons* | Quantity* | ES value | DS value | kWh Savings | kW Savings
| 1 |  |  |  | Retrofit | 1 | 1 | 1696 | 0.22 | 1696 | 0.22 | 77.92 | 77.92
| 2 |  |  |  | Retrofit | 10 | 1 | 1696 | 0.22 | 16960 | 2.2 | 779.2 | 779.2
| 3 | [6 empty] | 1696 | 0.22 | 0 | 0 | 0 | 0
| 4 | [6 empty] | 1696 | 0.22 | 0 | 0 | 0 | 0
| 5 | [6 empty] | 1696 | 0.22 | 0 | 0 | 0 | 0
| 6 | [6 empty] | 1696 | 0.22 | 0 | 0 | 0 | 0
| 7 | [6 empty] | 1696 | 0.22 | 0 | 0 | 0 | 0
| 8 | [6 empty] | 1696 | 0.22 | 0 | 0 | 0 | 0
| 9 | [6 empty] | 1696 | 0.22 | 0 | 0 | 0 | 0
| 10 | [6 empty] | 1696 | 0.22 | 0 | 0 | 0 | 0

## Strip Curtains
Last Updated: [Date], See Version Log | [9 empty] | HIDE
Strip Curtains for Walk In Freezers and Coolers
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [5 empty] | Calculations |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Facility and Type* | Quantity* | kWh Savings | kW Savings
| 1 |  | whatever | 109238 | Retrofit | Supermarket - Cooler | 1 | 123 | 0.016 | 5.66 | 5.66
| 2 |  |  |  | Retrofit | Supermarket - Freezer | 1 | 535 | 0.0659 | 23.88 | 23.88
| 3 |  |  |  | Retrofit | Convenience Store - Cooler | 1 | 19 | 0.0025 | 0.88 | 0.88
| 4 |  |  |  | Retrofit | Convenience Store - Freezer | 1 | 31 | 0.0038 | 1.38 | 1.38
| 5 |  |  |  | Retrofit | Restaurant - Cooler | 1 | 24 | 0.0031 | 1.1 | 1.1
| 6 |  |  |  | Retrofit | Restaurant - Freezer | 1 | 129 | 0.0158 | 5.74 | 5.74
| 7 |  |  |  | Retrofit | Warehouse - Refrigerated | 1 | 410 | 0.0532 | 18.84 | 18.84
| 8 | [6 empty] | 0 | 0 | 0 | 0
| 9 | [6 empty] | 0 | 0 | 0 | 0
| 10 | [6 empty] | 0 | 0 | 0 | 0

## Night Covers
Last Updated: [Date], See Version Log | [8 empty] | HIDE | HIDE |  |  | HIDE
Night Covers for Display Cases
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [6 empty] | Calculations |  |  |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Temperature* | Width of Opening* | Number of Units* | SF | HOU | kWh Savings | kW Savings
| 1 |  | test | test | Retrofit | Low Temperature (-35F to -5F) | 1 | 1 | 0.03 | 2190 | 65.7 | 0 | 1.31 | 1.31
| 2 |  |  |  | Retrofit | Medium Temperature (0F to 30F) | 1 | 1 | 0.02 | 2190 | 43.8 | 0 | 0.88 | 0.88
| 3 |  |  |  | Retrofit | High Temperature (35F - 55F) | 1 | 1 | 0.01 | 2190 | 21.9 | 0 | 0.44 | 0.44
| 4 | [7 empty] | 0 | 2190 | 0 | 0 | 0 | 0
| 5 | [7 empty] | 0 | 2190 | 0 | 0 | 0 | 0
| 6 | [7 empty] | 0 | 2190 | 0 | 0 | 0 | 0
| 7 | [7 empty] | 0 | 2190 | 0 | 0 | 0 | 0
| 8 | [7 empty] | 0 | 2190 | 0 | 0 | 0 | 0
| 9 | [7 empty] | 0 | 2190 | 0 | 0 | 0 | 0
| 10 | [7 empty] | 0 | 2190 | 0 | 0 | 0 | 0

## Auto Closer
Last Updated: [Date], See Version Log | [7 empty] | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
Auto Closer (Walk Ins Only)
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [5 empty] | Calculations | [5 empty] | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Case Type* | Quantity* | kWh Cooler | kWh Freezer | kW Cooler | kW Freezer | kWh Savings | kW Savings
| 1 |  | test model | test number | Retrofit | Freezer | 1 | 737 | 1997 | 0.463 | 0.488 | 1997 | 0.488 | 137.54 | 137.54
| 2 |  |  |  | Retrofit | Refrigeration | 1 | 737 | 1997 | 0.463 | 0.488 | 737 | 0.463 | 107.34 | 107.34
| 3 | [6 empty] | 737 | 1997 | 0.463 | 0.488 | 0 | 0 | 0 | 0
| 4 | [6 empty] | 737 | 1997 | 0.463 | 0.488 | 0 | 0 | 0 | 0
| 5 | [6 empty] | 737 | 1997 | 0.463 | 0.488 | 0 | 0 | 0 | 0
| 6 | [6 empty] | 737 | 1997 | 0.463 | 0.488 | 0 | 0 | 0 | 0
| 7 | [6 empty] | 737 | 1997 | 0.463 | 0.488 | 0 | 0 | 0 | 0
| 8 | [6 empty] | 737 | 1997 | 0.463 | 0.488 | 0 | 0 | 0 | 0
| 9 | [6 empty] | 737 | 1997 | 0.463 | 0.488 | 0 | 0 | 0 | 0
| 10 | [6 empty] | 737 | 1997 | 0.463 | 0.488 | 0 | 0 | 0 | 0

## Door Gaskets
Last Updated: [Date], See Version Log | [10 empty] | HIDE
Door Gaskets for Walk In and Reach In Coolers and Freezers
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [6 empty] | Calculations |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Case Type* | Door Type* | Quantity* | kWh Savings | kW Savings
| 1 |  |  |  | Retrofit | Freezer | Reach-In | 1 | 243 | 0.032 | 11.26 | 11.26
| 2 |  |  |  | Retrofit | Refrigeration | Walk-In | 1 | 204 | 0.027 | 9.48 | 9.48
| 3 |  |  |  | Retrofit | Refrigeration | Reach-In | 1 | 248 | 0.032 | 11.36 | 11.36
| 4 |  |  |  | Retrofit | Freezer | Walk-In | 1 | 347 | 0.045 | 15.94 | 15.94
| 5 |  |  |  | Retrofit |  |  | 1 | 0 | 0 | 0 | 0
| 6 |  |  |  | Retrofit |  |  | 1 | 0 | 0 | 0 | 0
| 7 |  |  |  | Retrofit |  |  | 1 | 0 | 0 | 0 | 0
| 8 |  |  |  | Retrofit |  |  | 1 | 0 | 0 | 0 | 0
| 9 | [7 empty] | 0 | 0 | 0 | 0
| 10 | [7 empty] | 0 | 0 | 0 | 0

## Special Doors
Last Updated: [Date], See Version Log | [9 empty] | HIDE | HIDE | HIDE |  |  | HIDE
Special Doors with Low or Anti Sweat Heat for Low Temp Case
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [7 empty] | Calculations |  |  |  |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Case Type* | Existing Door Heater Watts* | Replacement Door Heater Watts* | Quantity* | COP | Hours of Use | kW/w | kWh Savings | kW Savings
| 1 |  | test model | test number | Retrofit | Freezer | 150 | 5 | 1 | 1.25 | 8760 | 0.001 | 2286.36 | 0.261 | 97.93 | 97.93
| 2 |  |  |  | Retrofit | Refrigeration | 150 | 5 | 1 | 2.04 | 8760 | 0.001 | 1892.85 | 0.2161 | 81.08 | 81.08
| 3 | [8 empty] | 0 | 0 | 0.001 | 0 | 0 | 0 | 0
| 4 | [8 empty] | 0 | 0 | 0.001 | 0 | 0 | 0 | 0
| 5 | [8 empty] | 0 | 0 | 0.001 | 0 | 0 | 0 | 0
| 6 | [8 empty] | 0 | 0 | 0.001 | 0 | 0 | 0 | 0
| 7 | [8 empty] | 0 | 0 | 0.001 | 0 | 0 | 0 | 0
| 8 | [8 empty] | 0 | 0 | 0.001 | 0 | 0 | 0 | 0
| 9 | [8 empty] | 0 | 0 | 0.001 | 0 | 0 | 0 | 0
| 10 | [8 empty] | 0 | 0 | 0.001 | 0 | 0 | 0 | 0

## Pipe Insulation
Last Updated: [Date], See Version Log | [8 empty] | HIDE | HIDE |  |  | HIDE
Suction Pipe Insulation For Walk In Coolers and Freezers
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [6 empty] | Calculations |  |  |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Cooler Type* | Length* | Quantity* | ESF | DSF | kWh Savings | kW Savings
| 1 |  | test mfg | test model | Retrofit | Medium Temperature - Walk In Cooler | 1 | 1 | 24.8 | 0.005 | 24.8 | 0.005 | 1.5 | 1.5
| 2 |  |  |  | Retrofit | Low Temperature Walk In Freezer | 1 | 1 | 85.5 | 0.016 | 85.5 | 0.016 | 4.91 | 4.91
| 3 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 9 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 10 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0

## Door Replace Open
Last Updated: [Date], See Version Log | [7 empty] | HIDE | HIDE |  |  | HIDE
Refrigerated Display Cases with Doors Replacing Open Cases
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [5 empty] | Calculations |  |  |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Case Width* | Quantity* | ESF | DSF | kWh Savings | kW Savings
| 1 |  | test mfg | test model | Retrofit | 1 | 1 | 404.4 | 0.046164 | 404.4 | 0.0462 | 17.33 | 17.33
| 2 |  |  |  | Retrofit | 2 | 1 | 405.4 | 0.046279 | 810.8 | 0.0926 | 34.74 | 34.74
| 3 | [6 empty] | 406.4 | 0.046393 | 0 | 0 | 0 | 0
| 4 | [6 empty] | 407.4 | 0.046507 | 0 | 0 | 0 | 0
| 5 | [6 empty] | 408.4 | 0.046621 | 0 | 0 | 0 | 0
| 6 | [6 empty] | 409.4 | 0.046735 | 0 | 0 | 0 | 0
| 7 | [6 empty] | 410.4 | 0.046849 | 0 | 0 | 0 | 0
| 8 | [6 empty] | 411.4 | 0.046963 | 0 | 0 | 0 | 0
| 9 | [6 empty] | 412.4 | 0.047078 | 0 | 0 | 0 | 0
| 10 | [6 empty] | 413.4 | 0.047192 | 0 | 0 | 0 | 0

## Adding Doors
Last Updated: [Date], See Version Log | [8 empty] | HIDE | HIDE | HIDE |  |  | HIDE
Adding Doors to Existing Refrigerated Display Cases
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [6 empty] | Calculations |  |  |  |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Door Type* | Case Width* | Quantity* | ESF | Days | (kWh/day)/ft | kWh Savings | kW Savings
| 1 |  | test mfg | test model | Retrofit | Doors with Anti Sweat Heaters | 5 | 1 | 0.87 | 365.25 | 1.76 | 2796.35 | 0.3192 | 119.77 | 119.77
| 2 |  |  |  | Retrofit | No Sweat Doors | 1 | 1 | 0.52 | 365.25 | 1.76 | 334.28 | 0.0382 | 14.33 | 14.33
| 3 | [7 empty] | 0 | 365.25 | 1.76 | 0 | 0 | 0 | 0
| 4 | [7 empty] | 0 | 365.25 | 1.76 | 0 | 0 | 0 | 0
| 5 | [7 empty] | 0 | 365.25 | 1.76 | 0 | 0 | 0 | 0
| 6 | [7 empty] | 0 | 365.25 | 1.76 | 0 | 0 | 0 | 0
| 7 | [7 empty] | 0 | 365.25 | 1.76 | 0 | 0 | 0 | 0
| 8 | [7 empty] | 0 | 365.25 | 1.76 | 0 | 0 | 0 | 0
| 9 | [7 empty] | 0 | 365.25 | 1.76 | 0 | 0 | 0 | 0
| 10 | [7 empty] | 0 | 365.25 | 1.76 | 0 | 0 | 0 | 0

## Air Cooled Ref Condenser
Last Updated: [Date], See Version Log | [7 empty] | HIDE |  |  | HIDE
Air-Cooled Refrigeration Condenser
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [5 empty] | Calculations |  |  | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Tons* | Quantity* | City | kWh Savings | kW Savings
| 1 |  | test mfg | test model | Retrofit | 1 | 1 | Bradford | 1296 | 0.1429 | 54.5 | 54.5
| 2 | [6 empty] | Bradford | 0 | 0 | 0 | 0
| 3 | [6 empty] | Bradford | 0 | 0 | 0 | 0
| 4 | [6 empty] | Bradford | 0 | 0 | 0 | 0
| 5 | [6 empty] | Bradford | 0 | 0 | 0 | 0
| 6 | [6 empty] | Bradford | 0 | 0 | 0 | 0
| 7 | [6 empty] | Bradford | 0 | 0 | 0 | 0
| 8 | [6 empty] | Bradford | 0 | 0 | 0 | 0
| 9 | [6 empty] | Bradford | 0 | 0 | 0 | 0
| 10 | [6 empty] | Bradford | 0 | 0 | 0 | 0

## Refrigeration Economizer
Last Updated: [Date], See Version Log | [10 empty] | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE | HIDE |  |  | HIDE
Refrigeration Economizers
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| Line Item | User Inputs | [8 empty] | Calculations | [12 empty] | Total Uncapped Incentive | Total Incentive
|  | Unit ID | Manufacturer | Model Number | Project Type* | Nameplate HP* | Condenser Type* | Number of Fans* | Fan Control Installed* | Quantity* | City | kWh cond | kW evap | kW circ | kW econ | BF | DC comp | DC econ | Hours | kWh Savings w/Fan Control | kWh Savings wo/Fan Control | kWh Savings | kW Savings
| 1 |  |  |  | Retrofit | 1 | Discus/Unknown | 1 | YES | 1 | Bradford | 1092 | 0.123 | 0.035 | 0.227 | 1.29 | 50% | 63% | 2721 | 857.3138 | 702.8698 | 857.31 | 0 | 17.15 | 17.15
| 2 |  |  |  | Retrofit | 1 | Scroll | 1 | YES | 1 | Bradford | 1153 | 0.123 | 0.035 | 0.227 | 1.29 | 50% | 63% | 2721 | 918.3138 | 763.8698 | 918.31 | 0 | 18.37 | 18.37
| 3 |  |  |  | Retrofit | 1 | Hermetic / Semi-Hermetic | 1 | YES | 1 | Bradford | 1306 | 0.123 | 0.035 | 0.227 | 1.29 | 50% | 63% | 2721 | 1071.3138 | 916.8698 | 1071.31 | 0 | 21.43 | 21.43
| 4 |  |  |  | Retrofit | 1 | Discus/Unknown | 1 | NO | 1 | Bradford | 1092 | 0.123 | 0.035 | 0.227 | 1.29 | 50% | 63% | 2721 | 857.3138 | 702.8698 | 702.87 | 0 | 14.06 | 14.06
| 5 |  |  |  | Retrofit | 1 | Scroll | 1 | NO | 1 | Bradford | 1153 | 0.123 | 0.035 | 0.227 | 1.29 | 50% | 63% | 2721 | 918.3138 | 763.8698 | 763.87 | 0 | 15.28 | 15.28
| 6 |  |  |  | Retrofit | 1 | Hermetic / Semi-Hermetic | 1 | NO | 1 | Bradford | 1306 | 0.123 | 0.035 | 0.227 | 1.29 | 50% | 63% | 2721 | 1071.3138 | 916.8698 | 916.87 | 0 | 18.34 | 18.34
| 7 | [9 empty] | Bradford | 0 | 0.123 | 0.035 | 0.227 | 1.29 | 50% | 63% | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8 | [9 empty] | Bradford | 0 | 0.123 | 0.035 | 0.227 | 1.29 | 50% | 63% | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | [9 empty] | Bradford | 0 | 0.123 | 0.035 | 0.227 | 1.29 | 50% | 63% | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10 | [9 empty] | Bradford | 0 | 0.123 | 0.035 | 0.227 | 1.29 | 50% | 63% | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Data Export (hidden)
| Line Item | Measure Quantity | Measure Code Measure Description | Incentive | Project End Date | Total Energy Savings (kWh) | Total Energy Savings (kW) | Estimator Version Number | Make/Manufacturer | Model Number | Building Type | Energy Star | Number of Doors | Refrigeration Type | Baseline Motor HP | Existing Motor Type | Efficient Motor HP | Efficient Motor Watts | Efficient Motor Type | Control Type | Condesing Unit Type | Refrigeration Tonnage | Compressor HP | COP | Door Type | Case Volume | Pre Existing Curtains | Area SQFT | Width ft | Gasket Size | EER | Case Rating | Height in (Door Height) | Case Type | Baseline Wattage | Efficient Wattage | Case Temperature | Case Opening Width | Linear ft of insulation | Not Included | Compressor Volts | Compressor Amps | Fan Volts | Fan Amps | Operating Tem <0 | BTU /Door | Number of Fans
High Efficiency Refrigeration/Freezer Cases | 1 | 1 | HEFrzCase | 10.45 | 0 | 222.65 | 0.03 | 4 | 0 | 0 | Grocery |  |  | Freezer | [10 empty] | Solid | 13 | [7 empty] | Freezer
High Efficiency Refrigeration/Freezer Cases | 2 | 1 | HEFrzCase | 10.61 | 0 | 230.68 |  | 4 | 0 | 0 | Grocery |  |  | Freezer | [10 empty] | Solid | 15 | [7 empty] | Freezer
High Efficiency Refrigeration/Freezer Cases | 3 | 1 | HEFrzCase | 18.45 | 0 | 422.67 |  | 4 | 0 | 0 | Grocery |  |  | Freezer | [10 empty] | Solid | 45 | [7 empty] | Freezer
High Efficiency Refrigeration/Freezer Cases | 4 | 1 | HEFrzCase | 18.94 | 0 | 447.13 |  | 4 | 0 | 0 | Grocery |  |  | Freezer | [10 empty] | Solid | 55 | [7 empty] | Freezer
High Efficiency Refrigeration/Freezer Cases | 5 | 1 | HECoolCase | 11.5 | 0 | 275.21 |  | 4 | 0 | 0 | Grocery |  |  | Refrigeration | [10 empty] | Solid | 13 | [7 empty] | Refrigeration
High Efficiency Refrigeration/Freezer Cases | 6 | 1 | HECoolCase | 11.91 | 0 | 295.65 |  | 4 | 0 | 0 | Grocery |  |  | Refrigeration | [10 empty] | Solid | 15 | [7 empty] | Refrigeration
High Efficiency Refrigeration/Freezer Cases | 7 | 1 | HECoolCase | 10.89 | 0 | 244.55 |  | 4 | 0 | 0 | Grocery |  |  | Refrigeration | [10 empty] | Solid | 40 | [7 empty] | Refrigeration
High Efficiency Refrigeration/Freezer Cases | 8 | 1 | HECoolCase | 11.62 | 0 | 281.05 |  | 4 | 0 | 0 | Grocery |  |  | Refrigeration | [10 empty] | Solid | 50 | [7 empty] | Refrigeration
High Efficiency Refrigeration/Freezer Cases | 9
High Efficiency Refrigeration/Freezer Cases | 10
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 11 | 0 | HEEvapFanMotor | 25.81 | 0 | 602.6 | 0.0688 | 4 | Penguin | Macaroni | Grocery |  |  | Freezer | 0.25 | SP | 0.25 | 186.5 | ECM | [14 empty] | Walk In
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 12 | 0 | HEEvapFanRICoolCase3 | 65.58 | 0 | 1530.87 | 0.1748 | 4 | 0 | 0 | Grocery |  |  | Refrigeration | 0.33 | SP | 0.25 | 246.18 | ECM | [14 empty] | Reach In
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 13 | 0 | HEEvapFanMotor | 33.39 | 0 | 779.29 | 0.089 | 4 | 0 | 0 | Grocery |  |  | Freezer | 0.05 | PSC | 0.05 | 37.3 | PMS | [14 empty] | Walk In
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 14 | 0 | HEEvapFanRICoolCase6 | 86.34 | 0 | 2015.98 | 0.2301 | 4 | 0 | 0 | Grocery |  |  | Refrigeration | 0.15 | PSC | 0.15 | 111.9 | PMS | [14 empty] | Reach In
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 15 | 0 | HEEvapFanRICoolCase6 | 83.77 | 0 | 1955.7 | 0.2233 | 4 | 0 | 0 | Grocery |  |  | Refrigeration | 0.15 | PSC | 0.15 | 111.9 | ECM | [14 empty] | Reach In
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 16 | 0 | HEEvapFanMotor | 15.49 | 0 | 361.56 | 0.0413 | 4 | 0 | 0 | Grocery |  |  | Freezer | 0.15 | SP | 0.15 | 111.9 | ECM | [14 empty] | Walk In
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 17 | 0 | HEEvapFanRICoolCase3 | 15.13 | 0 | 353.4 | 0.0403 | 4 | 0 | 0 | Grocery |  |  | Refrigeration | 0.15 | SP | 0.15 | 111.9 | PMS | [14 empty] | Reach In
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 18 | 0 | HEEvapFanRIFrzCase3 | 19.31 | 0 | 450.71 | 0.0515 | 4 | 0 | 0 | Grocery |  |  | Freezer | 0.15 | SP | 0.15 | 111.9 | PMS | [14 empty] | Reach In
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 19 | 0 | HEEvapFanRIFrzCase3 | 15.49 | 0 | 361.56 | 0.0413 | 4 | 0 | 0 | Grocery |  |  | Freezer | 0.15 | SP | 0.15 | 111.9 | ECM | [14 empty] | Reach In
High Efficiency Evaporative Fan Motors for Refrigerated Cases | 20 | 0 | HEEvapFanMotor | 15.49 | 0 | 361.56 | 0.0413 | 4 | 0 | 0 | Grocery |  |  | Freezer | 0.15 | SP | 0.15 | 111.9 | ECM | [14 empty] | Walk In
Evaporator Fan Controllers | 21 | 1 | EvapFanCntrl | 54 | 0 | 2699.98 | 0 | 4 | 0 | 0 | Grocery |  |  | Freezer | 0.25 | SP |  |  |  | Unknown
Evaporator Fan Controllers | 22 | 1 | EvapFanCntrl | 42.34 | 0 | 2117 | 0 | 4 | 0 | 0 | Grocery |  |  | Refrigeration | 0.25 | SP |  |  |  | Unknown
Evaporator Fan Controllers | 23 | 1 | EvapFanCntrl | 23.14 | 0 | 1157 | 0 | 4 | 0 | 0 | Grocery |  |  | Freezer | 0.25 | ECM |  |  |  | Unknown
Evaporator Fan Controllers | 24 | 1 | EvapFanCntrl | 18.14 | 0 | 907 | 0 | 4 | 0 | 0 | Grocery |  |  | Refrigeration | 0.25 | ECM |  |  |  | Unknown
Evaporator Fan Controllers | 25
Evaporator Fan Controllers | 26
Evaporator Fan Controllers | 27
Evaporator Fan Controllers | 28
Evaporator Fan Controllers | 29
Evaporator Fan Controllers | 30
Floating Head Pressure Controls | 31 | 1 | FloatHeadPresCntrlTon | 287.41 | 0 | 14370.42 | 0 | 4 | 0 | 0 | Grocery | [9 empty] | Condesing Unit - Refrigerator | 10
Floating Head Pressure Controls | 32 | 1 | FloatHeadPresCntrlTon | 623.83 | 0 |  |  | 4 |  |  | Grocery | [9 empty] | Condesing Unit - Freezer | 10
Floating Head Pressure Controls | 33 | 1 | FloatHeadPresCntrlTon | 192.75 | 0 |  |  | 4 |  |  | Grocery | [9 empty] | Remote Condeser - Refrigerator | 10
Floating Head Pressure Controls | 34 | 1 | FloatHeadPresCntrlTon | 44.31 | 0 |  |  | 4 |  |  | Grocery | [9 empty] | Remote Condeser - Freezer | 1
Floating Head Pressure Controls | 35
Floating Head Pressure Controls | 36
Floating Head Pressure Controls | 37
Floating Head Pressure Controls | 38
Floating Head Pressure Controls | 39
Floating Head Pressure Controls | 40
Anti Sweat Heater Controls | 41 | 16 | ASHTRCntrlUnknownCool | 451.84 | 0 | 10912 | 1.168 | 4 | Good | 1234 | Grocery |  | 16 | Refrigeration | [5 empty] | Micropulse
Anti Sweat Heater Controls | 42 | 1 | ASHTRCntrlUnknownCool | 23.26 | 0 | 543 | 0.062 | 4 | 0 | 0 | Grocery |  | 1 | Freezer | [5 empty] | On/Off
Anti Sweat Heater Controls | 43 | 1 | ASHTRCntrlUnknownCool | 32.6 | 0 | 770 | 0.086 | 4 | 0 | 0 | Grocery |  | 1 | Freezer | [5 empty] | Unknown
Anti Sweat Heater Controls | 44 | 1 | ASHTRCntrlUnknownCool | 33.96 | 0 | 818 | 0.088 | 4 | 0 | 0 | Grocery |  | 1 | Freezer | [5 empty] | Micropulse
Anti Sweat Heater Controls | 45
Anti Sweat Heater Controls | 46
Anti Sweat Heater Controls | 47
Anti Sweat Heater Controls | 48
Anti Sweat Heater Controls | 49
Anti Sweat Heater Controls | 50
Evaporator Coil Defrost Control | 51 | 1 | EvapCoilDefCntrlFreez | 94.57 | 0 | 219.59 |  | 4 | junk | 5678 | Grocery |  |  | Freezer | [19 empty] | Freezer
Evaporator Coil Defrost Control | 52 | 1 | EvapCoilDefCntrlFreez | 73.62 | 0 | 170.94 |  | 4 | 0 | 0 | Grocery |  |  | Refrigeration | [19 empty] | Refrigeration
Evaporator Coil Defrost Control | 53
Evaporator Coil Defrost Control | 54
Evaporator Coil Defrost Control | 55
Evaporator Coil Defrost Control | 56
Evaporator Coil Defrost Control | 57
Evaporator Coil Defrost Control | 58
Evaporator Coil Defrost Control | 59
Evaporator Coil Defrost Control | 60
Variable Speed Refrigeration Compressor | 61 | 1 | VSRefComTon | 77.92 | 0 | 1696 | 0.22 | 4 | 0 | 0 | Grocery | [10 empty] | 1
Variable Speed Refrigeration Compressor | 62 | 1 | VSRefComTon | 779.2 | 0 | 16960 | 2.2 | 4 | 0 | 0 | Grocery | [10 empty] | 10
Variable Speed Refrigeration Compressor | 63
Variable Speed Refrigeration Compressor | 64
Variable Speed Refrigeration Compressor | 65
Variable Speed Refrigeration Compressor | 66
Variable Speed Refrigeration Compressor | 67
Variable Speed Refrigeration Compressor | 68
Variable Speed Refrigeration Compressor | 69
Variable Speed Refrigeration Compressor | 70
Strip Curtains for Walk In Freezers and Coolers | 71 | 1 | StripCurtain | 5.66 | 0 | 123 | 0.016 | 4 | whatever | 109238 | Grocery
Strip Curtains for Walk In Freezers and Coolers | 72 | 1 | StripCurtain | 23.88 | 0 | 535 | 0.0659 | 4 | 0 | 0 | Grocery
Strip Curtains for Walk In Freezers and Coolers | 73 | 1 | StripCurtain | 0.88 | 0 | 19 | 0.0025 | 4 | 0 | 0 | Grocery
Strip Curtains for Walk In Freezers and Coolers | 74 | 1 | StripCurtain | 1.38 | 0 | 31 | 0.0038 | 4 | 0 | 0 | Grocery
Strip Curtains for Walk In Freezers and Coolers | 75 | 1 | StripCurtain | 1.1 | 0 | 24 | 0.0031 | 4 | 0 | 0 | Grocery
Strip Curtains for Walk In Freezers and Coolers | 76 | 1 | StripCurtain | 5.74 | 0 | 129 | 0.0158 | 4 | 0 | 0 | Grocery
Strip Curtains for Walk In Freezers and Coolers | 77 | 1 | StripCurtain | 18.84 | 0 | 410 | 0.0532 | 4 | 0 | 0 | Grocery
Strip Curtains for Walk In Freezers and Coolers | 78
Strip Curtains for Walk In Freezers and Coolers | 79
Strip Curtains for Walk In Freezers and Coolers | 80
Night Covers for Display Cases | 81 | 1 | NightCover | 1.31 | 0 | 65.7 | 0 | 4 | test | test | Grocery | [25 empty] | Low Temperature (-35F to -5F) | 1
Night Covers for Display Cases | 82 | 1 | NightCover | 0.88 | 0 | 43.8 | 0 | 4 | 0 | 0 | Grocery | [25 empty] | Medium Temperature (0F to 30F) | 1
Night Covers for Display Cases | 83 | 1 | NightCover | 0.44 | 0 | 21.9 | 0 | 4 | 0 | 0 | Grocery | [25 empty] | High Temperature (35F - 55F) | 1
Night Covers for Display Cases | 84
Night Covers for Display Cases | 85
Night Covers for Display Cases | 86
Night Covers for Display Cases | 87
Night Covers for Display Cases | 88
Night Covers for Display Cases | 89
Night Covers for Display Cases | 90
Auto Closer (Walk Ins Only) | 91 | 1 | DoorCloseWIFreez | 137.54 | 0 | 1997 | 0.488 | 4 | test model | test number | Grocery | [22 empty] | Freezer
Auto Closer (Walk Ins Only) | 92 | 1 | DoorCloseWICooler | 107.34 | 0 | 737 | 0.463 | 4 | 0 | 0 | Grocery | [22 empty] | Refrigeration
Auto Closer (Walk Ins Only) | 93
Auto Closer (Walk Ins Only) | 94
Auto Closer (Walk Ins Only) | 95
Auto Closer (Walk Ins Only) | 96
Auto Closer (Walk Ins Only) | 97
Auto Closer (Walk Ins Only) | 98
Auto Closer (Walk Ins Only) | 99
Auto Closer (Walk Ins Only) | 100
Door Gaskets for Walk In and Reach In Coolers and Freezers | 101 | 1 | DoorGasketRICool | 11.26 | 0 | 243 | 0.032 | 4 | 0 | 0 | Grocery |  |  | Freezer | [10 empty] | Reach-In |  |  |  |  | Reach-In
Door Gaskets for Walk In and Reach In Coolers and Freezers | 102 | 1 | DoorGasketRIFrz | 9.48 | 0 | 204 | 0.027 | 4 | 0 | 0 | Grocery |  |  | Refrigeration | [10 empty] | Walk-In |  |  |  |  | Walk-In
Door Gaskets for Walk In and Reach In Coolers and Freezers | 103 | 1 | DoorGasketWICool | 11.36 | 0 | 248 | 0.032 | 4 | 0 | 0 | Grocery |  |  | Refrigeration | [10 empty] | Reach-In |  |  |  |  | Reach-In
Door Gaskets for Walk In and Reach In Coolers and Freezers | 104 | 1 | DoorGasketWIFrz | 15.94 | 0 | 347 | 0.045 | 4 | 0 | 0 | Grocery |  |  | Freezer | [10 empty] | Walk-In |  |  |  |  | Walk-In
Door Gaskets for Walk In and Reach In Coolers and Freezers | 105 | 1 | DoorGasketSuperCool | 0 | 0 | 0 | 0 | 4 | 0 | 0 | Grocery |  |  | 0 | [10 empty] | 0 |  |  |  |  | 0
Door Gaskets for Walk In and Reach In Coolers and Freezers | 106 | 1 | DoorGasketSuperCool | 0 | 0 | 0 | 0 | 4 | 0 | 0 | Grocery |  |  | 0 | [10 empty] | 0 |  |  |  |  | 0
Door Gaskets for Walk In and Reach In Coolers and Freezers | 107 | 1 | DoorGasketSuperCool | 0 | 0 | 0 | 0 | 4 | 0 | 0 | Grocery |  |  | 0 | [10 empty] | 0 |  |  |  |  | 0
Door Gaskets for Walk In and Reach In Coolers and Freezers | 108 | 1 | DoorGasketSuperCool | 0 | 0 | 0 | 0 | 4 | 0 | 0 | Grocery |  |  | 0 | [10 empty] | 0 |  |  |  |  | 0
Door Gaskets for Walk In and Reach In Coolers and Freezers | 109
Door Gaskets for Walk In and Reach In Coolers and Freezers | 110
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 111 | 1 | SpecDoors | 97.93 | 0 | 2286.36 | 0.261 | 4 | test model | test number | Grocery |  | 1 | Freezer | [15 empty] | 0 | 5 |  |  |  | 150 | 5 | Freezer
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 112 | 1 | SpecDoors | 81.08 | 0 | 1892.85 | 0.2161 | 4 | 0 | 0 | Grocery |  | 1 | Refrigeration | [15 empty] | 0 | 5 |  |  |  | 150 | 5 | Refrigeration
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 113
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 114
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 115
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 116
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 117
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 118
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 119
Special Doors with Low or Anti Sweat Heat for Low Temp Case | 120
Suction Pipe Insulation For Walk In Coolers and Freezers | 121 | 1 | SucPipeInsulMedTemp | 1.5 | 0 | 24.8 | 0.005 | 4 | test mfg | test model | Grocery | [18 empty] | 0 | 0 |  |  | Medium Temperature - Walk In Cooler |  |  |  |  | 1
Suction Pipe Insulation For Walk In Coolers and Freezers | 122 | 1 | SucPipeInsulLowTemp | 4.91 | 0 | 85.5 | 0.016 | 4 | 0 | 0 | Grocery | [18 empty] | 0 | 0 |  |  | Low Temperature Walk In Freezer |  |  |  |  | 1
Suction Pipe Insulation For Walk In Coolers and Freezers | 123
Suction Pipe Insulation For Walk In Coolers and Freezers | 124
Suction Pipe Insulation For Walk In Coolers and Freezers | 125
Suction Pipe Insulation For Walk In Coolers and Freezers | 126
Suction Pipe Insulation For Walk In Coolers and Freezers | 127
Suction Pipe Insulation For Walk In Coolers and Freezers | 128
Suction Pipe Insulation For Walk In Coolers and Freezers | 129
Suction Pipe Insulation For Walk In Coolers and Freezers | 130
Refrigerated Display Cases with Doors Replacing Open Cases | 131 | 1 | CaseDoor | 17.33 | 0 | 404.4 | 0.0462 | 4 | test mfg | test model | Grocery | [17 empty] | 1 | [8 empty] | 1
Refrigerated Display Cases with Doors Replacing Open Cases | 132 | 1 | CaseDoor | 34.74 | 0 | 810.8 | 0.0926 | 4 | 0 | 0 | Grocery | [17 empty] | 2 | [8 empty] | 2
Refrigerated Display Cases with Doors Replacing Open Cases | 133
Refrigerated Display Cases with Doors Replacing Open Cases | 134
Refrigerated Display Cases with Doors Replacing Open Cases | 135
Refrigerated Display Cases with Doors Replacing Open Cases | 136
Refrigerated Display Cases with Doors Replacing Open Cases | 137
Refrigerated Display Cases with Doors Replacing Open Cases | 138
Refrigerated Display Cases with Doors Replacing Open Cases | 139
Refrigerated Display Cases with Doors Replacing Open Cases | 140
Adding Doors to Existing Refrigerated Display Cases | 141 | 1 | CaseDoor | 119.77 | 0 | 2796.35 | 0.3192 | 4 | test mfg | test model | Grocery | [13 empty] | Doors with Anti Sweat Heaters |  |  |  | 5
Adding Doors to Existing Refrigerated Display Cases | 142 | 1 | CaseDoor | 14.33 | 0 | 334.28 | 0.0382 | 4 | 0 | 0 | Grocery | [13 empty] | No Sweat Doors |  |  |  | 1
Adding Doors to Existing Refrigerated Display Cases | 143
Adding Doors to Existing Refrigerated Display Cases | 144
Adding Doors to Existing Refrigerated Display Cases | 145
Adding Doors to Existing Refrigerated Display Cases | 146
Adding Doors to Existing Refrigerated Display Cases | 147
Adding Doors to Existing Refrigerated Display Cases | 148
Adding Doors to Existing Refrigerated Display Cases | 149
Adding Doors to Existing Refrigerated Display Cases | 150
Air-Cooled Refrigeration Condenser | 151 | 1 | 0 | 54.5 | 0 | 1296 | 0.1429 | 4 | test mfg | test model | Grocery | [10 empty] | 1
Air-Cooled Refrigeration Condenser | 152
Air-Cooled Refrigeration Condenser | 153
Air-Cooled Refrigeration Condenser | 154
Air-Cooled Refrigeration Condenser | 155
Air-Cooled Refrigeration Condenser | 156
Air-Cooled Refrigeration Condenser | 157
Air-Cooled Refrigeration Condenser | 158
Air-Cooled Refrigeration Condenser | 159
Air-Cooled Refrigeration Condenser | 160
Refrigeration Economizers | 161 | 1 | 0 | 17.15 | 0 | 857.31 | 0 | 4 | 0 | 0 | Grocery |  |  |  | 1 | [5 empty] | Discus/Unknown
Refrigeration Economizers | 162 | 1 | NightCover | 18.37 | 0 | 918.31 | 0 | 4 | 0 | 0 | Grocery |  |  |  | 1 | [5 empty] | Scroll
Refrigeration Economizers | 163 | 1 | StripCurtain | 21.43 | 0 | 1071.31 | 0 | 4 | 0 | 0 | Grocery |  |  |  | 1 | [5 empty] | Hermetic / Semi-Hermetic
Refrigeration Economizers | 164 | 1 | StripCurtain | 14.06 | 0 | 702.87 | 0 | 4 | 0 | 0 | Grocery |  |  |  | 1 | [5 empty] | Discus/Unknown
Refrigeration Economizers | 165 | 1 | StripCurtain | 15.28 | 0 | 763.87 | 0 | 4 | 0 | 0 | Grocery |  |  |  | 1 | [5 empty] | Scroll
Refrigeration Economizers | 166 | 1 | StripCurtain | 18.34 | 0 | 916.87 | 0 | 4 | 0 | 0 | Grocery |  |  |  | 1 | [5 empty] | Hermetic / Semi-Hermetic
Refrigeration Economizers | 167
Refrigeration Economizers | 168
Refrigeration Economizers | 169
Refrigeration Economizers | 170
Note on AO1: James Domanski: None of these to the right are included data dictionary terms

## Look Up Tables (hidden)
| Table 1: Volume Category |  | Table 2: Case Type |  | Table 3: Door Type |  | Calculation 1: Baseline kWh 3.5.1 | [6 empty] | Calculation 2: kWh EE 3.5.1 | [17 empty] | Refrigeration | Evap Fan Motors | HEEvapFanMotor | High efficiency evaporator fan motors for walk in or reach in cases | HEEvapFanMotor
| V < 15 |  | Freezer |  | Solid |  |  |  | Glass Door |  | Solid Door |  |  |  |  | Glass Door |  |  |  | Glass Door |  |  |  | Solid Door |  |  |  | Solid Door |  |  |  | Refrigeration | Evap Fan Motors | HEEvapFanRICoolCase2 | High-Efficiency Evaporator Fans-Reach in Cooler, SP 16W-36W | HEEvapFanRICoolCase2 | 1 | High-Efficiency Evaporator Fans- | Walk-In | Freezer | SP | >36W | High-Efficiency Evaporator Fans-Walk-In Freezer, SP >36W | HEEvapFanMotor
| 15 ≤ V < 30 |  | Refrigeration |  | Glass |  | Line Item | Volume | Fridge | Freezer | Fridge | Freezer |  |  |  | Fridge |  |  |  | Freezer |  |  |  | Fridge |  |  |  | Freezer |  |  |  | Refrigeration | Evap Fan Motors | HEEvapFanRICoolCase3 | High-Efficiency Evaporator Fans-Reach in Cooler, SP >36W | HEEvapFanRICoolCase3 | 2 | High-Efficiency Evaporator Fans- | Reach in | Cooler | SP | >36W | High-Efficiency Evaporator Fans-Reach in Cooler, SP >36W | HEEvapFanRICoolCase3
| 30 ≤ V < 50 | [5 empty] | 1 | 13 | 2.16 | 6.72 | 2.01 | 4.24 |  | Line Item | Volume | V < 15 | 15 ≤ V < 30 | 30 ≤ V < 50 | 50 ≤ V | V < 15 | 15 ≤ V < 30 | 30 ≤ V < 50 | 50 ≤ V | V < 15 | 15 ≤ V < 30 | 30 ≤ V < 50 | 50 ≤ V | V < 15 | 15 ≤ V < 30 | 30 ≤ V < 50 | 50 ≤ V | Refrigeration | Evap Fan Motors | HEEvapFanRICoolCase4 | High-Efficiency Evaporator Fans-Reach in Cooler, PSC <16W | HEEvapFanRICoolCase4 | 3 | High-Efficiency Evaporator Fans- | Walk-In | Freezer | PSC | >36W | High-Efficiency Evaporator Fans-Walk-In Freezer, PSC >36W | HEEvapFanMotor
| 50 ≤ V | [5 empty] | 2 | 15 | 2.36 | 7.3 | 2.11 | 4.68 |  | 1 | 13 | 1.68 | 1.77 | 1.328 | 0.254 | 5.376 | 5.376 | 5.376 | 5.376 | 1.256 | 1.168 | 1.61 | 2.202 | 3.63 | 3.808 | 1.002 | 6.291 | Refrigeration | Evap Fan Motors | HEEvapFanRICoolCase5 | High-Efficiency Evaporator Fans-Reach in Cooler, PSC 16W-36W | HEEvapFanRICoolCase5 | 4 | High-Efficiency Evaporator Fans- | Reach in | Cooler | PSC | >36W | High-Efficiency Evaporator Fans-Reach in Cooler, PSC >36W | HEEvapFanRICoolCase6
[7 empty] | 3 | 45 | 5.36 | 16 | 3.61 | 11.28 |  | 2 | 15 | 1.87 | 1.87 | 1.48 | 0.464 | 5.84 | 5.84 | 5.84 | 5.84 | 1.3 | 1.3 | 1.69 | 2.25 | 4.05 | 4.048 | 1.572 | 6.575 | Refrigeration | Evap Fan Motors | HEEvapFanRICoolCase6 | High-Efficiency Evaporator Fans-Reach in Cooler, PSC >36W | HEEvapFanRICoolCase6 | 5 | High-Efficiency Evaporator Fans- | Reach in | Cooler | PSC | >36W | High-Efficiency Evaporator Fans-Reach in Cooler, PSC >36W | HEEvapFanRICoolCase6
| Table 7: Cooler Type | [5 empty] | 4 | 55 | 6.36 | 18.9 | 4.11 | 13.48 |  | 3 | 45 | 4.72 | 3.37 | 3.76 | 3.614 | 12.8 | 12.8 | 12.8 | 12.8 | 1.96 | 3.28 | 2.89 | 2.97 | 10.35 | 7.648 | 10.122 | 10.835 | Refrigeration | Evap Fan Motors | HEEvapFanRIFrzCase1 | High-Efficiency Evaporator Fans-Reach in Freezer, SP <16W | HEEvapFanRIFrzCase1 | 6 | High-Efficiency Evaporator Fans- | Walk-In | Freezer | SP | >36W | High-Efficiency Evaporator Fans-Walk-In Freezer, SP >36W | HEEvapFanMotor
| Walk In | [5 empty] | 5 | 13 | 2.16 | 6.72 | 2.01 | 4.24 |  | 4 | 55 | 5.67 | 3.87 | 4.52 | 4.664 | 15.12 | 15.12 | 15.12 | 15.12 | 2.18 | 3.94 | 3.29 | 3.21 | 12.45 | 8.848 | 12.972 | 12.255 | Refrigeration | Evap Fan Motors | HEEvapFanRIFrzCase2 | High-Efficiency Evaporator Fans-Reach in Freezer, SP 16W-36W | HEEvapFanRIFrzCase2 | 7 | High-Efficiency Evaporator Fans- | Reach in | Cooler | SP | >36W | High-Efficiency Evaporator Fans-Reach in Cooler, SP >36W | HEEvapFanRICoolCase3
| Reach In | [5 empty] | 6 | 15 | 2.36 | 7.3 | 2.11 | 4.68 |  | 5 | 13 | 1.68 | 1.77 | 1.328 | 0.254 | 5.376 | 5.376 | 5.376 | 5.376 | 1.256 | 1.168 | 1.61 | 2.202 | 3.63 | 3.808 | 1.002 | 6.291 | Refrigeration | Evap Fan Motors | HEEvapFanRIFrzCase3 | High-Efficiency Evaporator Fans-Reach in Freezer, SP >36W | HEEvapFanRIFrzCase3 | 8 | High-Efficiency Evaporator Fans- | Reach in | Freezer | SP | >36W | High-Efficiency Evaporator Fans-Reach in Freezer, SP >36W | HEEvapFanRIFrzCase3
[7 empty] | 7 | 40 | 4.86 | 14.55 | 3.36 | 10.18 |  | 6 | 15 | 1.87 | 1.87 | 1.48 | 0.464 | 5.84 | 5.84 | 5.84 | 5.84 | 1.3 | 1.3 | 1.69 | 2.25 | 4.05 | 4.048 | 1.572 | 6.575 | Refrigeration | Evap Fan Motors | HEEvapFanRIFrzCase4 | High-Efficiency Evaporator Fans-Reach in Freezer, PSC <16W | HEEvapFanRIFrzCase4 | 9 | High-Efficiency Evaporator Fans- | Reach in | Freezer | SP | >36W | High-Efficiency Evaporator Fans-Reach in Freezer, SP >36W | HEEvapFanRIFrzCase3
[7 empty] | 8 | 50 | 5.86 | 17.45 | 3.86 | 12.38 |  | 7 | 40 | 4.245 | 3.12 | 3.38 | 3.089 | 11.64 | 11.64 | 11.64 | 11.64 | 1.85 | 2.95 | 2.69 | 2.85 | 9.3 | 7.048 | 8.697 | 10.125 | Refrigeration | Evap Fan Motors | HEEvapFanRIFrzCase5 | High-Efficiency Evaporator Fans-Reach in Freezer, PSC 16W-36W | HEEvapFanRIFrzCase5 | 10 | High-Efficiency Evaporator Fans- | Walk-In | Freezer | SP | >36W | High-Efficiency Evaporator Fans-Walk-In Freezer, SP >36W | HEEvapFanMotor
[7 empty] | 9 | 0 | 0 | 0 | 0 | 0 |  | 8 | 50 | 5.195 | 3.62 | 4.14 | 4.139 | 13.96 | 13.96 | 13.96 | 13.96 | 2.07 | 3.61 | 3.09 | 3.09 | 11.4 | 8.248 | 11.547 | 11.545 | Refrigeration | Evap Fan Motors | HEEvapFanRIFrzCase6 | High-Efficiency Evaporator Fans-Reach in Freezer, PSC >36W | HEEvapFanRIFrzCase6
[7 empty] | 10 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0.445 | 1.12 | 0.34 | -1.111 | 2.36 | 2.36 | 2.36 | 2.36 | 0.97 | 0.31 | 1.09 | 1.89 | 0.9 | 2.248 | -2.703 | 4.445 | Refrigeration | Evap Fan Motors | HEEvapFanWICoolCase1 | High-Efficiency Evaporator Fans-Walk-In Cooler, SP <14W | HEEvapFanWICoolCase1
[14 empty] | 10 | 0 | 0.445 | 1.12 | 0.34 | -1.111 | 2.36 | 2.36 | 2.36 | 2.36 | 0.97 | 0.31 | 1.09 | 1.89 | 0.9 | 2.248 | -2.703 | 4.445 | Refrigeration | Evap Fan Motors | HEEvapFanWICoolCase2 | High-Efficiency Evaporator Fans-Walk-In Cooler, SP 16W-23W | HEEvapFanWICoolCase2
[32 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWICoolCase3 | High-Efficiency Evaporator Fans-Walk-In Cooler, SP 1/20 HP 37 Watt | HEEvapFanWICoolCase3
| Calculation 3: kWh to Use 3.5.1 | [30 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWICoolCase4 | High-Efficiency Evaporator Fans-Walk-In Cooler, SP 1/15 HP 49 Watt | HEEvapFanWICoolCase4
| Values |  |  |  | Baseline |  |  | ECM | [23 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWICoolCase5 | High-Efficiency Evaporator Fans-Walk-In Cooler, PSC <14W | HEEvapFanWICoolCase5
[8 empty] | Fridge kWh |  |  |  | Freezer kWh |  |  |  | Final Check | [15 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWICoolCase6 | High-Efficiency Evaporator Fans-Walk-In Cooler, PSC 16W-23W | HEEvapFanWICoolCase6
| Line Item | Door Type | Volume Cat | Cooling Type | Fridge kWh | Freezer kWh | Actual kWh | V < 15 | 15 ≤ V < 30 | 30 ≤ V < 50 | 50 ≤ V | V < 15 | 15 ≤ V < 30 | 30 ≤ V < 50 | 50 ≤ V | V < 15 | 15 ≤ V < 30 | 30 ≤ V < 50 | 50 ≤ V | Actual kWh | [11 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWICoolCase7 | High-Efficiency Evaporator Fans-Walk-In Cooler, PSC 1/20 HP 37 Watt | HEEvapFanWICoolCase7
| 1 | Solid | V < 15 | Freezer | 2.01 | 4.24 | 4.24 | 1.256 | 1.168 | 1.61 | 2.202 | 3.63 | 3.808 | 1.002 | 6.291 | 3.63 | 3.808 | 1.002 | 6.291 | 3.63 | [11 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWICoolCase8 | High-Efficiency Evaporator Fans-Walk-In Cooler, PSC 1/15 HP 49 Watt | HEEvapFanWICoolCase8
| 2 | Solid | 15 ≤ V < 30 | Freezer | 2.11 | 4.68 | 4.68 | 1.3 | 1.3 | 1.69 | 2.25 | 4.05 | 4.048 | 1.572 | 6.575 | 4.05 | 4.048 | 1.572 | 6.575 | 4.048 | [11 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWIFrzCase1 | High-Efficiency Evaporator Fans-Walk-In Freezer, SP <14W | HEEvapFanWIFrzCase1
| 3 | Solid | 30 ≤ V < 50 | Freezer | 3.61 | 11.28 | 11.28 | 1.96 | 3.28 | 2.89 | 2.97 | 10.35 | 7.648 | 10.122 | 10.835 | 10.35 | 7.648 | 10.122 | 10.835 | 10.122 | [11 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWIFrzCase2 | High-Efficiency Evaporator Fans-Walk-In Freezer, SP 16W-23W | HEEvapFanWIFrzCase2
| 4 | Solid | 50 ≤ V | Freezer | 4.11 | 13.48 | 13.48 | 2.18 | 3.94 | 3.29 | 3.21 | 12.45 | 8.848 | 12.972 | 12.255 | 12.45 | 8.848 | 12.972 | 12.255 | 12.255 | [11 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWIFrzCase3 | High-Efficiency Evaporator Fans-Walk-In Freezer, SP 1/20 HP 37 Watt | HEEvapFanWIFrzCase3
| 5 | Solid | V < 15 | Refrigeration | 2.01 | 4.24 | 2.01 | 1.256 | 1.168 | 1.61 | 2.202 | 3.63 | 3.808 | 1.002 | 6.291 | 1.256 | 1.168 | 1.61 | 2.202 | 1.256 | [11 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWIFrzCase4 | High-Efficiency Evaporator Fans-Walk-In Freezer, SP, 1/15 HP 49 Watt | HEEvapFanWIFrzCase4
| 6 | Solid | 15 ≤ V < 30 | Refrigeration | 2.11 | 4.68 | 2.11 | 1.3 | 1.3 | 1.69 | 2.25 | 4.05 | 4.048 | 1.572 | 6.575 | 1.3 | 1.3 | 1.69 | 2.25 | 1.3 | [11 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWIFrzCase5 | High-Efficiency Evaporator Fans-Walk-In Freezer, PSC <14W | HEEvapFanWIFrzCase5
| 7 | Solid | 30 ≤ V < 50 | Refrigeration | 3.36 | 10.18 | 3.36 | 1.85 | 2.95 | 2.69 | 2.85 | 9.3 | 7.048 | 8.697 | 10.125 | 1.85 | 2.95 | 2.69 | 2.85 | 2.69 | [11 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWIFrzCase6 | High-Efficiency Evaporator Fans-Walk-In Freezer, PSC 16W-23W | HEEvapFanWIFrzCase6
| 8 | Solid | 50 ≤ V | Refrigeration | 3.86 | 12.38 | 3.86 | 2.07 | 3.61 | 3.09 | 3.09 | 11.4 | 8.248 | 11.547 | 11.545 | 2.07 | 3.61 | 3.09 | 3.09 | 3.09 | [11 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWIFrzCase7 | High-Efficiency Evaporator Fans-Walk-In Freezer, PSC, 1/20 HP 37 Watt | HEEvapFanWIFrzCase7
| 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0.445 | 1.12 | 0.34 | -1.111 | 2.36 | 2.36 | 2.36 | 2.36 | 0.445 | 1.12 | 0.34 | -1.111 | 0 | [11 empty] | Refrigeration | Evap Fan Motors | HEEvapFanWIFrzCase8 | High-Efficiency Evaporator Fans-Walk-In Freezer, PSC 1/15 HP 49 Watt | HEEvapFanWIFrzCase8
| 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.445 | 1.12 | 0.34 | -1.111 | 2.36 | 2.36 | 2.36 | 2.36 | 0.445 | 1.12 | 0.34 | -1.111 | 0 | [11 empty] | Refrigeration | Anti Sweat Control | ASHTRCntrlUnknownCool | Anti-Sweat Heater Controls Cooler Unknown control | ASHTRCntrlUnknownCool
[32 empty] | Refrigeration | Anti Sweat Control | ASHTRCntrlOnOffCool | Anti-Sweat Heater Controls Cooler On/Off control | ASHTRCntrlOnOffCool
| Table 4: Motor Type | Table 4.1: Motor Type 2 | Table 5: Wattage |  | Table 6: Project Type | [26 empty] | Refrigeration | Anti Sweat Control | ASHTRCntrlMPCool | Anti-Sweat Heater Controls Cooler Micropulse control | ASHTRCntrlMPCool
| SP | SP | 1-14 |  | Retrofit | [26 empty] | Refrigeration | Anti Sweat Control | ASHTRCntrlUnknownFrz | Anti-Sweat Heater Controls Freezer Unknown control | ASHTRCntrlUnknownFrz
| PSC | ECM | 16-23 |  | New Construction | [26 empty] | Refrigeration | Anti Sweat Control | ASHTRCntrlOnOffFrz | Anti-Sweat Heater Controls Freezer On/Off control | ASHTRCntrlOnOffFrz
| ECM |  | 1/20 HP 37 Watt | [28 empty] | Refrigeration | Anti Sweat Control | ASHTRCntrlMPFrz | Anti-Sweat Heater Controls Freezer Micropulse control | ASHTRCntrlMPFrz
| PMS |  | 1/15 HP 49 Watt | [28 empty] | Refrigeration | Auto Close | DoorCloseWICooler | Auto Closers for Walk-In Cooler/Unknown Doors | DoorCloseWICooler
[32 empty] | Refrigeration | Auto Close | DoorCloseWIFreez | Auto Closers for Walk-In Freezer Doors | DoorCloseWIFreez
| Waste Heat Factor |  |  |  | Table 9: Deemed Savings Freezer Reach In |  |  |  | Table 10: Deemed Savings Cooler Walk In |  |  |  | Table 11: Deemed Savings Freezer Walk In |  |  |  | Table 3-97 | [14 empty] | Refrigeration | Door Gaskets | DoorGasketRICool | Door Gaskets for Reach-in Coolers | DoorGasketRICool
[5 empty] | Wattage | PSC | SP |  | Wattage | PSC | SP |  | Wattage | PSC | SP |  | Fan control Style | %On | CF | [12 empty] | Refrigeration | Door Gaskets | DoorGasketRIFrz | Door Gaskets for Reach-in Freezers | DoorGasketRIFrz
| SP Freezer | 1.76 |  |  | 1-14 | 110 | 483 |  | 1-14 | 84 | 377 |  | 1-14 | 100 | 452 |  | On/Off | 63.6% | 0.087 | [12 empty] | Refrigeration | Door Gaskets | DoorGasketWICool | Door Gaskets for Walk-in Coolers | DoorGasketWICool
| PSC Freezer | 1.38 |  |  | 16-23 | 239 | 841 |  | 16-23 | 189 | 661 |  | 16-23 | 226 | 790 |  | Micropulse | 69.2% | 0.102 | [12 empty] | Refrigeration | Door Gaskets | DoorGasketWIFrz | Door Gaskets for Walk-in Freezers | DoorGasketWIFrz
| SP Refrigeration | 1.38 |  |  | 1/20HP (37 Watts) | 454 | 1146 |  | 1/20HP (37 Watts) | 356 | 902 |  | 1/20HP (37 Watts) | 427 | 1079 |  | Unknown | 66.5% | 0.094 | [12 empty] | Refrigeration | Door Gaskets | DoorGasketRestCool |  | DoorGasketRestCool
| PSC Refrigeration | 1.19 |  |  | 1/15 HP (49 Watt) | 0 | 0 |  | 1/15 HP (49 Watt) | 472 | 1216 |  | 1/15 HP (49 Watt) | 565 | 1455 | [16 empty] | Refrigeration | Door Gaskets | DoorGasketRestFrz |  | DoorGasketRestFrz
[32 empty] | Refrigeration | Door Gaskets | DoorGasketSmallGroceryCool |  | DoorGasketSmallGroceryCool
| Table 12: Deemed kW Cooler Reach In |  |  |  | Table 13: Deemed kW Freezer Reach In |  |  |  | Table 14: Deemed kW Cooler Walk In |  |  |  | Table 15: Deemed kW Freezer Walk In | [18 empty] | Refrigeration | Door Gaskets | DoorGasketSmallGroceryFrz |  | DoorGasketSmallGroceryFrz
| Wattage | PSC | SP |  | Wattage | PSC | SP |  | Wattage | PSC | SP |  | Wattage | PSC | SP | [16 empty] | Refrigeration | Door Gaskets | DoorGasketMLGroceryCool |  | DoorGasketMLGroceryCool
| 1-14 | 0.0105 | 0.0461 |  | 1-14 | 0.0126 | 0.0551 |  | 1-14 | 0.0101 | 0.0456 |  | 1-14 | 0.0121 | 0.0546 | [16 empty] | Refrigeration | Door Gaskets | DoorGasketMLGroceryFrz |  | DoorGasketMLGroceryFrz
| 16-23 | 0.0228 | 0.0802 |  | 16-23 | 0.0273 | 0.096 |  | 16-23 | 0.0228 | 0.0798 |  | 16-23 | 0.0273 | 0.0955 | [16 empty] | Refrigeration | Door Gaskets | DoorGasketConCool |  | DoorGasketConCool
| 1/20HP (37 Watts) | 0.0433 | 0.1093 |  | 1/20HP (37 Watts) | 0.0518 | 0.1308 |  | 1/20HP (37 Watts) | 0.0431 | 0.109 |  | 1/20HP (37 Watts) | 0.0516 | 0.1304 | [16 empty] | Refrigeration | Door Gaskets | DoorGasketConFrz |  | DoorGasketConFrz
| 1/15 HP (49 Watt) | 0 | 0 |  | 1/15 HP (49 Watt) | 0 | 0 |  | 1/15 HP (49 Watt) | 0.057 | 0.147 |  | 1/15 HP (49 Watt) | 0.0682 | 0.1759 | [16 empty] | Refrigeration | Door Gaskets | DoorGasketSuperCool |  | DoorGasketSuperCool
[32 empty] | Refrigeration | Door Gaskets | DoorGasketSuperFrz |  | DoorGasketSuperFrz
| Table 16: Unit Type/COP 3.5.5 |  |  | Table 17: Location |  | Table 18: Facility Type |  | Table 19: Column Number | [23 empty] | Refrigeration | Evaporator Fan Controllers | EvapFanCntrl | Evaporator Fan Controllers | EvapFanCntrl
| Type | COP |  | Allentown |  | Education - College/University |  | Condesing Unit - Refrigerator | 2 | [22 empty] | Refrigeration | Floating Head Pressure Control-HP | FloatHeadPresCntrlHP | Floating Head Pressure Control-HP | FloatHeadPresCntrlHP
| Condesing Unit - Refrigerator | 2.51 |  | Binghamton |  | Education - Other |  | Condesing Unit - Freezer | 3 | [22 empty] | Refrigeration | Floating Head Pressure Control-Ton | FloatHeadPresCntrlTon | Floating Head Pressure Control-Ton | FloatHeadPresCntrlTon
| Condesing Unit - Freezer | 1.3 |  | Bradford |  | Grocery |  | Remote Condeser - Refrigerator | 4 | [22 empty] | Refrigeration | Evaporator Coil Defrost Control | EvapCoilDefCntrlCool | Evaporator Coil Defrost Control Cooler | EvapCoilDefCntrlCool
| Remote Condeser - Refrigerator | 2.5 |  | Erie |  | Health - Hospital |  | Remote Condeser - Freezer | 5 | [22 empty] | Refrigeration | Evaporator Coil Defrost Control | EvapCoilDefCntrlFreez | Evaporator Coil Defrost Control Freezer | EvapCoilDefCntrlFreez
| Remote Condeser - Freezer | 1.46 |  | Harrisburg |  | Health - Other | [25 empty] | Refrigeration | Existing Ref Display Cases | AntiSweatHtrDoor | Add Door to Existing Ref Display Cases without anti-sweat heaters | AntiSweatHtrDoor
|  |  |  | Philidelphia |  | Industrial Manufacturing | [25 empty] | Refrigeration | Existing Ref Display Cases | ZeroSweatDoor | Add Door to Existing Ref Display Cases with anti-sweat heaters | ZeroSweatDoor
| Table 22: 2.5.4 Definition |  |  | Pittsburgh |  | Institutional/Public Service | [25 empty] | Refrigeration | Zero Heat Door | ZeroEnergyDoor | Refrigerated display cases with doors replacing open cases | ZeroEnergyDoor
| Estimator Term | Catalyst Term |  | Scranton |  | Lodging | [25 empty] | Refrigeration | Air-Cooled Refrigeration Condenser |  | Air-Cooled Refrigeration Condenser
| Voltage of Compressor | motorwattage |  | Williamsburg |  | Multifamily (Common Areas) | [25 empty] | Refrigeration | Refrigeration economizers |  | Refrigeration economizers
| Amperage of Compressor | rate |  |  |  | Office | [25 empty] | Refrigeration | Night Covers | NightCover | Night Covers for Display Cases | NightCover
| Voltage of Fan | newwattage |  |  |  | Restaurant | [25 empty] | Refrigeration | Strip Curtains | StripCurtain | Strip curtains for walk-in freezers and coolers | StripCurtain
| Amperage of Fan | wattage |  |  |  | Retail |  | Door Gasket Savings - Table 3-113 | [23 empty] | Refrigeration | Strip Curtains | StripCurtain | Strip Curtains Grocery Cooler | StripCurtain
[6 empty] | Warehouse - Other |  | Door Type | Cooler | Freezers | Cooler | Freezers | [19 empty] | Refrigeration | Strip Curtains | StripCurtain | Strip Curtains Grocery freeezer | StripCurtain
[6 empty] | Warehouse - Refrigerated |  |  | kW/Door | kW/Door | kWh/Door | kWh/Door | [19 empty] | Refrigeration | Strip Curtains | StripCurtain | Strip Curtains convenience store cooler | StripCurtain
| Table 24: Answer | [6 empty] | Reach-In | 0.032 | 0.032 | 248 | 243 | [19 empty] | Refrigeration | Strip Curtains | StripCurtain | Strip Curtains convenience store freezer | StripCurtain
| Yes | [6 empty] | Walk-In | 0.027 | 0.045 | 204 | 347 | [19 empty] | Refrigeration | Strip Curtains | StripCurtain | Strip Curtains restaurant cooler | StripCurtain
| No | [30 empty] | Refrigeration | Strip Curtains | StripCurtain | Strip Curtains Restaurant freezer | StripCurtain
[32 empty] | Refrigeration | Strip Curtains | StripCurtain | Strip Curtains refrigerated warehouse cooler | StripCurtain
[32 empty] | Refrigeration | Suction Pipe Insulation | SucPipeInsulMedTemp | Suction Pipe Insulation Medium Temp | SucPipeInsulMedTemp
| Table 20: kWh/Ton | [30 empty] | Refrigeration | Suction Pipe Insulation | SucPipeInsulLowTemp | Suction Pipe Insulation Low Temp | SucPipeInsulLowTemp
| City | Condesing Unit - Refrigerator | Condesing Unit - Freezer | Remote Condeser - Refrigerator | Remote Condeser - Freezer | [26 empty] | Refrigeration | Refrigerated Display Cases |  | Refrigerated display cases with doors replacing open cases | CaseDoor
| Allentown | 630 | 767 | 467 | 639 | [26 empty] | Refrigeration | High Efficiency Cases | HECoolCase | HE Cooler Cases | HECoolCase
| Binghamton | 728 | 835 | 495 | 674 |  | Table 21: 3.5.5 | [6 empty] | Table 23: 3.5.7 BF | [17 empty] | Refrigeration | High Efficiency Cases | HEFrzCase | HE Freezer Cases | HEFrzCase
| Bradford | 765 | 860 | 511 | 686 |  | Type | Freezer kWh | Refrigeration kWh | Freezer kW | Refrigeration kW |  |  | Freezer | 1.67 | [16 empty] | Refrigeration | VSD Refrigeration Compressor-Ton | VSRefComTon | Variable Speed Ref Compressor Tons | VSRefComTon
| Erie | 681 | 802 | 482 | 657 |  | Unknown | 770 | 642 | 0.086 | 0.072 |  |  | Refrigeration | 1.3 | [16 empty] | Refrigeration | VSD Refrigeration Compressor-HP | VSRefComHP | Variable Speed Ref Compressor HP | VSRefComHP
| Harrisburg | 585 | 737 | 440 | 623 |  | On/Off | 543 | 453 | 0.062 | 0.052 | [20 empty] | Refrigeration | Special Doors | SpecDoors | Special Doors | SpecDoors
| Philidelphia | 546 | 710 | 435 | 609 |  | Micropulse | 818 | 682 | 0.088 | 0.073
| Pittsburgh | 617 | 759 | 470 | 634
| Scranton | 686 | 806 | 479 | 659
| Williamsburg | 663 | 790 | 468 | 651
| Table 25: 3.5.9 ES/DS w/ Pre Exist Curtain |  |  |  | Table 26: 3.5.8 - Table - 3-107 |  |  |  | Table 27: 3.5.10 SF
| Type | ES | DS |  | Type | ES | DS |  | Low Temperature (-35F to -5F) | 0.03
| Supermarket - Cooler | 37 | 0.0042 |  | Supermarket - Cooler | 123 | 0.016 |  | Medium Temperature (0F to 30F) | 0.02
| Supermarket - Freezer | 119 | 0.0136 |  | Supermarket - Freezer | 535 | 0.0659 |  | High Temperature (35F - 55F) | 0.01
| Convenience Store - Cooler | 5 | 0.0006 |  | Convenience Store - Cooler | 19 | 0.0025
| Convenience Store - Freezer | 8 | 0.0009 |  | Convenience Store - Freezer | 31 | 0.0038
| Restaurant - Cooler | 8 | 0.0009 |  | Restaurant - Cooler | 24 | 0.0031
| Restaurant - Freezer | 34 | 0.0039 |  | Restaurant - Freezer | 129 | 0.0158
| Warehouse - Refrigerated | 254 | 0.029 |  | Warehouse - Refrigerated | 410 | 0.0532
| Table 28: 3.5.12 ESF/DSF |  |  |  | Table 29: 3.5.14 ESF/DSF
| Facility | ESF | DSF |  | Type | DSF | ESF
| Restaurant - Cooler | 18 | 0.000886 |  | Medium Temperature - Walk In Cooler | 0.005 | 24.8
| Restaurant - Freezer | 63 | 0.001871 |  | Low Temperature Walk In Freezer | 0.016 | 85.5
| Small Grocery Store - Cooler | 15 | 0.000658
| Small Grocery Store - Freezer | 64 | 0.00162
| Convenience Store - Cooler | 15 | 0.000658
| Convenience Store - Freezer | 64 | 0.00162
| Large Grocery Store - Cooler | 15 | 0.0006425
| Large Grocery Store - Freezer | 91 | 0.001593
Table 30: 3.5.16 ESF/DSF
| Type | ESF | DSF
| Doors with Anti Sweat Heaters | 87% | 0.0223
| No Sweat Doors | 52% | 0.0418
Evap Fan Motors
| kWbase | kWee | HPbase | HPee | HP/W | ηbase | ηee | LF | %ON Uncontrolled | Hours/Year | WHFe | kWh savings
1 | 0.27975 | 0.23979 | 0.25 | 0.25 | 0.746 | 0.6 | 0.7 | 0.9 | 97.8% | 8760 | 1.76 | 602.598
2 | 0.36927 | 0.23979 | 0.33 | 0.25 | 0.746 | 0.6 | 0.7 | 0.9 | 97.8% | 8760 | 1.38 | 1530.8728
3 | 0.1119 | 0.045986 | 0.05 | 0.05 | 0.746 | 0.3 | 0.73 | 0.9 | 97.8% | 8760 | 1.38 | 779.2875
4 | 0.3357 | 0.13796 | 0.15 | 0.15 | 0.746 | 0.3 | 0.73 | 0.9 | 97.8% | 8760 | 1.19 | 2015.983
5 | 0.3357 | 0.14387 | 0.15 | 0.15 | 0.746 | 0.3 | 0.7 | 0.9 | 97.8% | 8760 | 1.19 | 1955.7044
6 | 0.16785 | 0.14387 | 0.15 | 0.15 | 0.746 | 0.6 | 0.7 | 0.9 | 97.8% | 8760 | 1.76 | 361.5588
7 | 0.16785 | 0.13796 | 0.15 | 0.15 | 0.746 | 0.6 | 0.73 | 0.9 | 97.8% | 8760 | 1.38 | 353.3978
8 | 0.16785 | 0.13796 | 0.15 | 0.15 | 0.746 | 0.6 | 0.73 | 0.9 | 97.8% | 8760 | 1.76 | 450.7103
9 | 0.16785 | 0.14387 | 0.15 | 0.15 | 0.746 | 0.6 | 0.7 | 0.9 | 97.8% | 8760 | 1.76 | 361.5588
10 | 0.16785 | 0.14387 | 0.15 | 0.15 | 0.746 | 0.6 | 0.7 | 0.9 | 97.8% | 8760 | 1.76 | 361.5588
Evap Fan Controllers
1 | kW | HP | HP/W | η | %ON Uncontrolled | %ON Controlled | Hours/Year | WHFe | LF | CF | kWh savings | kW savings
1 | 0.5595 | 0.25 | 0.746 | 0.3 | 97.8% | 66.5% | 8760 | 1.76 | 0.9 | 0.094 | 2699.9841 | 0
2 | 0.5595 | 0.25 | 0.746 | 0.3 | 97.8% | 66.5% | 8760 | 1.38 | 0.9 | 0.094 | 2117.033 | 0
3 | 0.23979 | 0.25 | 0.746 | 0.7 | 97.8% | 66.5% | 8760 | 1.76 | 0.9 | 0.094 | 1157.136 | 0
4 | 0.23979 | 0.25 | 0.746 | 0.7 | 97.8% | 66.5% | 8760 | 1.38 | 0.9 | 0.094 | 907.2998 | 0
5 | 0 | 0 | 0.746 | 0.3 | 97.8% | 66.5% | 8760 | 1.76 | 0.9 | 0.094 | 0 | 0
6 | 0 | 0 | 0.746 | 0.3 | 97.8% | 66.5% | 8760 | 1.76 | 0.9 | 0.094 | 0 | 0
7 | 0 | 0 | 0.746 | 0.3 | 97.8% | 66.5% | 8760 | 1.76 | 0.9 | 0.094 | 0 | 0
8 | 0 | 0 | 0.746 | 0.3 | 97.8% | 66.5% | 8760 | 1.76 | 0.9 | 0.094 | 0 | 0
9 | 0 | 0 | 0.746 | 0.3 | 97.8% | 66.5% | 8760 | 1.76 | 0.9 | 0.094 | 0 | 0
10 | 0 | 0 | 0.746 | 0.3 | 97.8% | 66.5% | 8760 | 1.76 | 0.9 | 0.094 | 0 | 0
Table 3‑120: Default Savings for Air-Cooled Refrigeration Condensers
| City | Annual Energy Savings per Ton of Capacity (ΔkWh/ton) | Peak Demand Savings per Ton of Capacity (ΔkW/ton)
| Allentown | 1307 | 0.1252
| Binghamton | 1290 | 0.143
| Bradford | 1296 | 0.1429
| Erie | 1318 | 0.1244
| Harrisburg | 1318 | 0.1171
| Philadelphia | 1312 | 0.1204
| Pittsburgh | 1308 | 0.1245
| Scranton | 1318 | 0.1164
| Williamsport | 1323 | 0.1167
| City | Hours | Condensing unit savings, per HP
|  |  | Hermetic / Semi-Hermetic | Scroll | Discus/Unknown
| Allentown | 1674 | 835 | 737 | 698 |  | Condenser Type
| Binghamton | 2254 | 1098 | 969 | 918 |  | Hermetic / Semi-Hermetic
| Bradford | 2721 | 1306 | 1153 | 1092 |  | Scroll
| Eerie | 1931 | 955 | 842 | 799 |  | Discus/Unknown
| Harrisburg | 1458 | 766 | 676 | 641
| Philadelphia | 1223 | 625 | 551 | 523
| Pittsburg | 1614 | 819 | 723 | 685
| Scranton | 1860 | 924 | 816 | 773
| Williamsport | 1741 | 852 | 752 | 713
Note on M128: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Theres a problem with this calculation in the TRM. We need to address with PPL/Cadmus. I'm defaulting to 0 for now.

## Version Log (hidden)
Version Log
Original Author: |  | Raven Jones | QA/QC Engineer(s): | Priyam Parikh
Primary Developer: |  | Raven Jones | Senior Engineer Approval:
Version | Date | Reason for Change | Change Description | Contact, Department
0.1 | 2016-04-18 | PPL Calcs | First TRM Calculator for program | Raven Jones, National Engineering
1 | 2016-05-31 | Updates for Mktg, Compliance to Measure config | Formatting, added financial summary, updated tables to match measure configs | Priyam Parikh
1.1 | 2016-06-03 | Prep for PPL website upload | Final formatting updates from mktg, locking cells | Priyam Parikh
2 | 2017-03-28 | TRM Errata | High-Efficiency Refrigerator/Freezer Cases – Remove CF from kW Savings equation | Mary Clayton, Core Engineering
3 | 2018-08-06 | Update format | Updating format to match standard PPL format | Ryan Novosedliak, Engineering
3 | 2018-11-30 | PPl Branding |  | Tom Cosgro, Engineering
4 | 2021-06-01 | Phase IV Update | Update for Phase IV | Michael Stevenson