## Instructions
PPL Calculator for Compressed Air
Note: This Estimator is used for estimating savings and does not guarantee the estimated incentive. The methodology presented in this Estimator is deemed acceptable for the PPL Electric Utilities Non-Residential Energy Efficiency Program. However, the assumptions used by the applicant to calculate the annual savings will be reviewed by the Program Team, which is solely responsible for the final determination of the annual energy savings to be used in calculating the incentive amount. The Program also reserves the right to require the applicant to conduct specific measurement and verification activities, including monitoring both before and after the retrofit, and to base the incentive payment on the results of these activities. For any questions, or assistance using this Estimator, please call 1-866-432-5501 or email us at pplbusiness@clearesult.com.
Input Instructions
Yellow cells indicate that user input is required. Cells with a * are required.
Grey cells are calculated values.
Worksheet Summary
Methodology
Summary of Methodology Worksheet
Calculator
Summary of required inputs and outputs of the Calculator
Calculations
Summary of Calculations Worksheet
Version Log
The Version Log Worksheet tracks updates and changes made to the workbook.
Glossary of Inputs
Cycling Dryer - HP of Compressors | Nominal HP rating of the air compressor
Cycling Dryer - Quantity of Dryers Installed | Total number of qualifying dryers installed
Cycling Dryer - Rated Capacity | Rated capacity of installed dryer
Air Nozzle - Compressor Control type | Control type of compressor
Air Nozzle - Nozzle Diameter | Diameter or nozzle in inches
Air Nozzle - Number of Nozzles Installed | Quantity of nozzles installed
Condensate Drain - Drain Orifice Size | Size of the drain orifice in inches
Condensate Drain - Compressor Control Type | Control type of compressor
Condensate Drain - System Pressure | System operating pressure in PSIG
Condensate Drain - Number or Drains installed | Quanitity of condensate drains installed
Air Tanks - Rated Compressor HP | Nameplate horsepower of compressor
Air Tanks - Number of Tanks | Quantity of air tanks installed
VFD Compressors - New Compressor HP | Horsepower of the New Compressor
Compressor Controller - Total Compressor Horsepower | Total horsepower of compressor
Low Pressure Drop Filters - Total Compressor Horsepower | Total horsepower of compressor
Mist Eliminators - Total Compressor Horsepower | Total horsepower of compressor
Operating Schedule | Operation schedule of the facility
Total Equipment Cost | Total Equipment Cost of Installed Measure
Manufacturer | Manufacturer of Installed Equipment
Model # | Model # of Installed Equipment
Glossary of Outputs
kW | Peak Demand Reduction | kWh
kWh | Annual Energy Reduction | $/year
Incentive | One time payment of Eligible Incentive | kWh

## Methodology (hidden)
Calculator Methodologies - From 2021 PA TRM 2-4-21
Cycling Refrigerated Thermal Mass Dryer | Air-Entraining Air Nozzle | Variable Speed Drive Compressor (<=40 HP)
Eligibility: This measure applies to the installation of a cycling refrigerated thermal mass dryer with a capacity of 600 CFM or below replacing a non-cycling (continuous) refrigerated air dryer in a compressed air system. This measure does not apply to the replacement of other types of dryers. Methodology: The energy savings are obtained through the following equations - | Eligibility: Air-entraining air nozzles must replace an open copper tube (of 1/8” or 1/4" orifice diameter) with an energy efficient air-entraining air nozzle that uses less than 15 CFM at 100 psi. Methodology: The energy savings are obtained through the following equations - | Eligibility: This measure relates to the installation of an air compressor with a variable speed drive (VSD), either by replacing an existing unit at the end of its useful life, or the installation of a new system in a new building. The new air compressor must be 40 HP or less.
Methodology: The energy savings are obtained through the following equations -
No-Loss Condensate Drains | Air Tanks for Load/No Load Compressors | Compressor Controller
Eligibility: To be eligible, no-loss condensate drains must replace standard condensate drains operated by a timer-controlled solenoid valve. Methodology: The energy savings are obtained through the following equations - | Eligibility: To be eligible, the new air receivers must have a minimum storage ratio of 4 gallons of storage per cfm of airflow capacity. The system should replace a load/no load compressor (having 1 gallon of storage per cfm or less) or a modulating compressor with blowdown. Methodology: The energy savings are obtained through the following equations - | Eligibility: To be eligible, the controller must be new (no existing pressure/flow controller exists) and the system must have a compressor motor capacity >= 40 hp. The system must have a minimum storage capacity of 3 gal/cfm. This measure is not replacing drop-line regulators or filter-regulator lubricators. Methodology: The energy savings are obtained through the following equations -
Low Pressure Drop Filters | Mist Eliminators
Eligibility: To be eligible, filters must not have a pressure drop exceeding 1 psi when new and 3 psi at element change. Methodology: The energy savings are obtained through the following equations - | Eligibility: To be eligible, the compressed air system must be greater than 50 HP and the mist eliminator must have less than a 1 psig pressure drop and replace a coalescing filter. Methodology: The energy savings are obtained through the following equations -

## Summary
|  |  |  | Version: | 4.2
|  |  |  | Last Updated: | 2022-05-31
Date | Measure Name | Equipment Cost | Savings |  | Incentive
Project Name |  |  | kW | kWh
Site Address | Cycling Dryer | 0 | 0 | 0 | 0
Project Number | Air Nozzle | 0 | 0 | 0 | 0
Prepared by | Condensate Drains | 0 | 0 | 0 | 0
Electric Rate ($/kWh) | Air Tanks | 0 | 0 | 0 | 0
Demand Rate ($/kW) | VFD Compressor (<=40HP) | 0 | 0 | 0 | 0
| Compressor Controller | 0 | 0 | 0 | 0
| Low Pressure Drop Filters | 0 | 0 | 0 | 0
| Mist Eliminators | 0 | 0 | 0 | 0
| Total | 0 | 0 | 0 | 0

## Printable Report (hidden)
PPL Direct Discount Program
Customer Name:
Prepared by:
| Customer Acknowledgement (please initial): _______________ Contractor Acknowledgement (please initial): _______________ |  | Date: _______________ Date: _______________
| Summary Table |  |  | This project's annual electric savings are equivalent to:
| Project Cost: | 0 |  |  | 0 | acres of forest saved
| Energy Savings (kWh): | 0
| Annual Cost Savings: | 0
| Available Utility Incentive: | 0 |  |  | 0 | miles driven by an average car
| Cost to Customer: | 0
Simple Pay Back (Yrs.)
[5 empty] | 0 | tons of waste recycled instead of landfilled
| BY THE NUMBERS | COST OF WAITING
| 0 | 0
[5 empty] | 0 | gallons of gasoline consumed
| Available Utility Incentive | Monthly
| 0% | 0 |  |  | 0 | pounds of coal burned
| Return on Investment | Annually
Factors from US EPA GHG Equivalencies Calculator
Measure List row | Measure | Measure Details | Quantity | Project Cost ($) | Energy Savings (kWh) | Utility Cost Savings ($) | Incentive ($) | Cost to Customer

## Measure List (hidden)
Row | Measure | Measure Details | Quantity |  | Project Cost | Energy Savings (kWh) | Demand Savings (kW) | Utility Cost Savings ($) | Incentive ($) | Cost to Customer
2 | Cycling Refrigerated Thermal Mass Dryer | Model #: Total Compressor Horsepower: | 0 | dryer(s) | 0 | 0 | 0 | 0 | 0 | 0
3 | Air-Entraining Nozzles | Compressor Type: Nozzle Diameter: in | 0 | nozzle(s) | 0 | 0 | 0 | 0 | 0 | 0
4 | Air-Entraining Nozzles | Compressor Type: Nozzle Diameter: in | 0 | nozzle(s) | 0 | 0 | 0 | 0 | 0 | 0
5 | Air-Entraining Nozzles | Compressor Type: Nozzle Diameter: in | 0 | nozzle(s) | 0 | 0 | 0 | 0 | 0 | 0
6 | Air-Entraining Nozzles | Compressor Type: Nozzle Diameter: in | 0 | nozzle(s) | 0 | 0 | 0 | 0 | 0 | 0
7 | No-Loss Condensate Drains | Compressor Type: Drain Size: 44569/1 in | 0 | drain(s) | 0 | 0 | 0 | 0 | 0 | 0
8 | No-Loss Condensate Drains | Compressor Type: Drain Size: 44569/1 in | 0 | drain(s) | 0 | 0 | 0 | 0 | 0 | 0
9 | No-Loss Condensate Drains | Compressor Type: Drain Size: 44569/1 in | 0 | drain(s) | 0 | 0 | 0 | 0 | 0 | 0
10 | No-Loss Condensate Drains | Compressor Type: Drain Size: 44569/1 in | 0 | drain(s) | 0 | 0 | 0 | 0 | 0 | 0
11 | Air Tanks for Load/No Load Compressors | Compressor Size: HP | 0 | tank(s) | 0 | 0 | 0 | 0 | 0 | 0
12 | VFD Compressor <= 40HP | Model #: Compressor Size: HP | 1 | compressor | 0 | 0 | 0 | 0 | 0 | 0
13 | Compressor Controller | Total Compressor Horsepower: | 1 | controller | 0 | 0 | 0 | 0 | 0 | 0
14 | Low Pressure Drop Air Filters | Total Compressor Horsepower: | 0 | filter(s) | 0 | 0 | 0 | 0 | 0 | 0
15 | Mist Eliminator Air Filters | Total Compressor Horsepower: | 0 | filter(s) | 0 | 0 | 0 | 0 | 0 | 0

## Cycling Dryer
Cycling Dryer |  |  | ELIGIBILITY This measure is targeted to non-residential customers whose equipment is a non-cycling refrigerated air dryer with a capacity of 600 cfm or below. Acceptable baseline conditions are a non-cycling (e.g., continuous) air dryer with a capacity of 600 cfm or below. The replacement of desiccant, deliquescent, heat-of-compression, membrane, or other types of dryers does not qualify under this measure. Efficient conditions are a cycling thermal mass dryer with a capacity of 600 cfm or below.
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Manufacturer*
Model #*
Quantity of Dryers Installed*
Rated Capacity* |  | Eligibility check
Operating Schedule*
HP of Compressors* |  | Must be 150 or less
Total Equipment Cost*
Annual kWh Savings | 0
Annual kW Savings | 0
Incentive | 0

## Air Nozzle
Air Nozzles |  |  |  |  | ELIGIBILITY This measure is targeted to non-residential customers whose compressed air equipment uses stationary air nozzles in a production application with an open copper tube of 1/8” or 1/4” orifice diameter. Energy efficient conditions require replacement of an inefficient, non-air entraining air nozzle with an energy efficient air-entraining air nozzle that use less than 15 CFM at 100 psi for industrial applications.
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| 1 | 2 | 3 | 4
Operating Schedule*
Compressor Control Type*
Nozzle Diameter* (Inches)*
Number of Nozzles Installed*
Manufacturer*
Model #*
Total Equipment Cost*
Annual kWh Savings | 0 | 0 | 0 | 0
Annual kW Savings | 0 | 0 | 0 | 0
Incentive | 0 | 0 | 0 | 0

## Calculations (hidden)
User Inputs
Cycling Dryer - HP of Compressor | 0 | Qty |  | Incentive Rate Selection: | Downstream |  |  | Downstream | DD 5/31/22 and before | DD 6/1/22 and after
Cycling Dryer - Proposed quantity of Dryers | 0 | Qty |  | $/kWh | 0.075 |  | $/kWh | 0.075 | 0.15 | 0.16
Cycling Dryer - Total Equipment Cost | 0 | $ |  | $/kW | 215 |  | $/kW | 215 | 215 | 250
Air Nozzle -Nozzle Diameter | 0 | Inches |  | Project Cost Cap | 0.5 |  | Project Cost Cap | 0.5 | 0.8 | 0.8
Air Nozzle - Compressor Control Type | 0
Air Nozzle - Number or Nozzles Installed | 0 | Qty
Air Nozzle - Total Equipment Cost | 0 | $
Condensate Drains - Drain Orifice Diameter | 1/8 | Inches
Condensate Drains - System Pressure | 0 | PSIG
Condensate Drains - Compressor Control Type | 0
Condensate Drains - Number or Drains | 0 | Qty
Condensate Drains - Total Equipment Cost | 0 | $
Air Tanks - Rated Air Compressor Horsepower | 0 | HP
Air Tanks - Number or Tanks | 0 | Qty
Air Tanks - Total Equipment Cost | 0 | $
VFD Compressors - Operating Hours | 0
VFD Compressors (<=75HP) - Incemental Cost | 0 | $
VFD Compressors (<=75HP) - New Compressor HP | 0 | HP
Compressor Controller - Total Compressor HP | 0 | HP
Compressor Controller - Operating Hours | 0
Compressor Controller - Total Equipment Cost | 0
Low Pressure Drop Filters - Total Compressor HP | 0
Low Pressure Drop Filters - Operating Hours | 0
Low Pressure Drop Filters - Total Equipment Cost | 0
Low Pressure Drop Filters - Quantity | 0
Mist Eliminators - Quantity | 0
Mist Eliminators - Total Compressor HP | 0
Mist Eliminators - Operating Hours | 0
Mist Eliminators - Total Equipment Cost | 0
Constants
Cycling Dryer- Compressor Output per HP | 4 | CFM/HP
Cycling Dryer - kWdryer/CFMcomp | 0.0087 | kW/CFM
Cycling Dryer - Chilled Coil Response Time Derate | 0.925 | Hours
Cycling Dryer - Average Compressor Operating Capacity | 0.65 | %
Air Nozzle - Percent of Hours when Nozzle is in Use | 5% | %
Condensate Drains - Hours per year Drain is Open | 146 | Hours
Condensate Drains - Percent Not Condensate | 75% | %
Air Tanks - Load Factor | 0.92
Air Tanks - Load Reduction | 0.1
Air Tanks - Efficiency of Compressor Motor | 0.91 | %
VFD Compressors - Baseline Compressor Factor | 0.89
VFD Compressor - Efficient Compressor Factor | 0.705
VFD Compressor - Compressor HP to Full Load kW | 0.9
Compressor Controller - kW to HP conversion factor | 0.746
Compressor Controller - Load Factor | 0.92
Compressor Controller - Comp Motor Efficiency @ FL | 0.91
Compressor Controller - % decrease in power input | 0.05
Low Pressure Drop Filters - kW to HP conversion factor | 0.746
Low Pressure Drop Filters - reduced filter pressure loss | 2
Low Pressure Drop Filters - Load Factor | 0.92
Low Pressure Drop Filters - Savings Factor | 0.005
Mist Eliminators - kW to HP conversion factor | 0.746
Mist Eliminators - Comp Motor Efficiency @ FL | 0.91
Mist Eliminators - Load Factor | 0.92
Mist Eliminators - Percentage of Energy Saved | 0.02
Mist Eliminators - Total Pressure Reduction | 4 | psig
Mist Eliminators - Percentage of Energy Saved for each psi reduced | 0.005
Look-Up Table 1: Annual Hours of Operation |  |  | Look-Up Table 2: Coincidence Factor |  |  | Look-Up Table 3: Baseline Nozzle Mass Flow | [5 empty] | Look-Up Table 7: Average Compressor kW/CFM |  | Look-Up Table 8: Average Air Loss Rates | [6 empty] | Look-Up Table 9:Annual Hours of Compressor Operation
Building Schedule | Hours |  | Building Schedule | % |  | Nozzle Diameter | Air Mass Flow |  |  |  |  | Compressor Control Type | Average Compressor kW/CFM | Pressure (psig) | Orifice Diameter (Inches) | [5 empty] | Min Size | Max Size | Hours | CF
Single Shift (8/5) | 1976 |  | Single Shift (8/5) | 0.24 |  | 1/8 | 21 |  |  |  |  | Modulating w/ Blowdown | 0.32 |  | 1/64 | 1/32 | 1/16 | 1/8 | 1/4 | 3/8 | 1 | 5 | 1257 | 0.667
2-Shift (16/5) | 3952 |  | 2-Shift (16/5) | 0.95 |  | 1/4 | 58 |  |  |  |  | Load/No load w/ 1 gal/CFM Storage | 0.32 | 70 | 0.29 | 1.16 | 4.66 | 18.62 | 74.4 | 167.8 | 6 | 20 | 2131 | 0.667
3-Shift (24/5) | 5928 |  | 3-Shift (24/5) | 0.95 | [7 empty] | Load/No load w/ 3 gal/CFM Storage | 0.3 | 80 | 0.32 | 1.26 | 5.24 | 20.76 | 83.1 | 187.2 | 21 | 50 | 3528 | 0.667
4 Shift (24/7) | 8320 |  | 4 Shift (24/7) | 0.95 | [7 empty] | Load/No Load w/ 5 gal/CFM Storage | 0.28 | 90 | 0.36 | 1.46 | 5.72 | 23.1 | 92 | 206.6 | 51 | 100 | 4520 | 1
[12 empty] | Variable Speed w/ Unloading | 0.23 | 95 | 0.38 | 1.51 | 6.02 | 24.16 | 96.5 | 216.8 | 101 | 200 | 4685 | 1
[12 empty] | Unknown | 0.27 | 100 | 0.4 | 1.55 | 6.31 | 25.22 | 100.9 | 227 | 201 | 500 | 6148 | 1
Look-Up Table 4: Adjustment Factor |  |  | Look-Up Table 5: VFD Energy Savings Factor (ESF) |  |  | Look-Up Table 6: Air Entraining Nozzle Mass Flow | [7 empty] | 105 | 0.42 | 1.63 | 6.58 | 26.31 | 105.2 | 236.7 | 501 | 1000 | 6156 | 1
Building Schedule | Adjustment Factor |  | Post-retrofit control | ESF |  | Nozzle Diameter | Air Mass Flow | [6 empty] | 110 | 0.43 | 1.71 | 6.85 | 27.39 | 109.4 | 246.4 | 1001 | 100000 | 7485 | 1
Single Shift (8/5) | 0.62 |  | Variable Fequency Drive (VFD) | 0.26 |  | 1/8 | 6 | [6 empty] | 115 | 0.45 | 1.78 | 7.12 | 28.48 | 113.7 | 256.1
2-Shift (16/5) | 0.74 |  |  |  |  | 1/4 | 11 | [6 empty] | 120 | 0.46 | 1.86 | 7.39 | 29.56 | 117.9 | 265.8
3-Shift (24/5) | 0.86 | [12 empty] | 125 | 0.48 | 1.94 | 7.66 | 30.65 | 122.2 | 275.5
4 Shift (24/7) | 0.97
Calculations
| Hours of Use | Coincidence Factor | Comprssor Output per HP | kWdryer/CFMcomp | Chilled Coil Response Time Derate | Average Compressor Operating Capacity | Annual Savings (kWh) | Annual Savings (kW) | Incremental Measure Cost | Incentive
Cycling Dryer | #N/A | #N/A | 4 | 0.0087 | 0.925 | 0.65 | 0 | 0 | 0 | 0
| Hours of Use | Coincidence Factor | Baseline Nozzle Air Mass Flow | Energy Efficient Nozzle Air Mass Flow | Ratio of Compressor KW/CFM | Percent of Hours the Nozzle is in Use | Annual Savings (kWh) | Annual Savings (kW) | Incremental Measure Cost | Incentive
Air- Entraining Air Nozzle | #N/A | #N/A |  |  |  | 5% | 0 | 0 | 0 | 0
Air- Entraining Air Nozzle | #N/A | #N/A |  |  |  | 5% | 0 | 0 | 0 | 0
Air- Entraining Air Nozzle | #N/A | #N/A |  |  |  | 5% | 0 | 0 | 0 | 0
Air- Entraining Air Nozzle | #N/A | #N/A |  |  |  | 5% | 0 | 0 | 0 | 0
| Hours of Use | Coincidence Factor | Air Loss Rate - From Table 3-161 | Multiplication Factor | Air Loss Rate | Ratio of Compresser kW/CFM | Hours Per Year Drain is Open | Adjustment Factor | Percentage Not Condensate | Annual kWh Savings | Annual kW Savings | Incentive
No-Loss Condensate Drains | #N/A | #N/A |  | 0.97 | #VALUE! |  | 146 |  | 75% | 0 | 0 | 0
No-Loss Condensate Drains | #N/A | #N/A |  | 0.97 | #VALUE! |  | 146 |  | 75% | 0 | 0 | 0
No-Loss Condensate Drains | #N/A | #N/A |  | 0.97 | #VALUE! |  | 146 |  | 75% | 0 | 0 | 0
No-Loss Condensate Drains | #N/A | #N/A |  | 0.97 | #VALUE! |  | 146 |  | 75% | 0 | 0 | 0
| Coincidence Factor | Hours of Use | Load Factor | Load Reduction | Efficiency of Compressor Motor | Annual Savings (kWh) | Annual Savings (kW) | Incremental Measure Cost | Incentive
Air Tanks for Load / No load Compressors | #N/A | #N/A | 0.92 | 0.1 | 0.91 | 0 | 0 | 0 | 0
| Compressor HP | Hours of Use | Coincidence Factor | Baseline Compressor Factor | Efficient Compressor Factor | Comp Motor Nominal HP to Full Load kW | Average Compressor Operating Capacity | Annual Savings (kWh) | Annual Savings (kW) | Incremental Measure Cost | Incentive
VFD Compressors (<=40HP) | 0 | #N/A | #N/A | 0.89 | 0.705 | 0.9 | 0.05 | 0 |  | 0
| Compressor HP | Hours of Use | Coincidence Factor | kW to HP Conversion Factor | Load Factor | Comp Motor Efficiency @ Full Load | % Decrease in Input Power | Annual Savings (kWh) | Annual Savings (kW) | Incremental Measure Cost | Incentive
Compressor Controller | 0 | #N/A | #N/A | 0.746 | 0.92 | 0.91 | 0.05 | 0 | 0 | 0 | Custom Project
| Quantity | Compressor HP | Hours of Use | Coincidence Factor | kW to HP Conversion Factor | Load Factor | Reduced Filter Pressure Loss | Savings Factor | Annual Savings (kWh) | Annual Savings (kW) | Incremental Measure Cost | Incentive
Low Pressure Drop Filters | 0 | 0 | #N/A | #N/A | 0.746 | 0.92 | 2 | 0.005 | 0 | 0 | 0 | 0
| Quantity | Compressor HP | Hours of Use | Coincidence Factor | kW to HP Conversion Factor | Comp Motor Efficiency @ Full Load | Load Factor | Percentage of Energy Saved | Annual Savings (kWh) | Annual Savings (kW) | Incremental Measure Cost | Incentive
Mist Eliminators | 0 | 0 | #N/A | #N/A | 0.746 | 0.91 | 0.92 | 0.02 | 0 | 0 | 0 | 0

## Condensate Drains
Condensate Drains |  |  |  |  | ELIGIBILITY This measure is targeted to non-residential customers whose equipment is a timed drain that operates on a pre-set schedule. Acceptable baseline conditions are compressed air systems with standard condensate drains operated by a solenoid and timer. Energy efficient conditions are systems retrofitted with new No-loss Condensate Drains properly sized for the compressed air system.
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
| 1 | 2 | 3 | 4
Operating Schedule*
Drain Orifice Diameter* | 1/8 | 1/8 | 1/8 | 1/8
Compressor Control Type*
System Pressure* (PSIG)
Number of Drains Installed*
Manufacturer*
Model #*
Total Equipment Cost*
Annual kWh Savings | 0 | 0 | 0 | 0
Annual kW Savings | 0 | 0 | 0 | 0
Incentive | 0 | 0 | 0 | 0

## Air Tanks
Air Tanks |  | ELIGIBILITY This measure applies to the installation of new air receivers with pressure/flow controls to load/no load compressors. The high efficiency equipment is a load/no load compressor with a minimum storage ratio of 4 gallons of storage per cfm.
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Operating Schedule*
Rated Compressor Horsepower*
Number of Tanks*
Manufacturer*
Model #*
Total Equipment Cost*
Annual kWh Savings | 0
Annual kW Savings | 0
Incentive | 0

## VFD Compressor (<=40HP)
VFD Compressor (<=40HP) |  | ELIGIBILITY To qualify for this measure, a participating commercial or industrial establishment must install or retrofit a ≤ 40 HP compressor with variable speed control. Projects involving compressors larger than 40 HP should be treated as custom projects.
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Operating Schedule*
New Compressor Horsepower (<=40 HP)*
Manufacturer*
Model #*
Total Equipment Cost*
Annual kWh Savings | 0
Annual kW Savings | 0
Incentive | 0

## Compressor Controller
Compressor Controller |  | ELIGIBILITY The following protocol for the measurement of energy and demand savings applies to the installation of a compressed air pressure or flow controller for compressed air systems in commercial or industrial facilities. A pressure/flow controller can greatly increase the control of an air storage system. These units, also called demand valves, precision flow controllers, or pilot‐operated regulators, are precision pressure regulators that allow the airflow to fluctuate while maintaining a constant pressure to the facility’s air distribution piping network. Installing a pressure/flow controller on the downstream side of an air storage receiver creates a pressure differential entering and leaving the vessel. This pressure differential stores energy in the form of readily available compressed air, which can be used to supply the peak air demand for short duration events, in place of using more compressor horsepower to feed this peak demand. The benefits of having a pressure/flow controller include: • Reducing the kilowatts of peak demand, especially with multiple compressor configurations. • Saving kilowatt‐hours by allowing the compressor to run at most efficient loads, then turn itself off in low demand and no demand periods. | • Saving kilowatt‐hours by reducing plant air pressure to the minimum allowable. This leads to reduced loads on the electric motors and greater system efficiency. For every 2 psi reduced in the system, 1% of energy is saved. • Maintaining a reduced, constant pressure in the facility wastes less air due to leakage, and less volume is required by the compressor. • Ensuring quality control of the process by the constant pressure: machines can produce an enhanced product quality when the pressure is allowed to fluctuate. The baseline condition is having no existing pressure/flow controller and an existing compressed air system with a total compressor motor capacity ≥ 40 hp. This measure requires a minimum storage of 3gal/cfm. This protocol is not applicable for compressed air systems with total motor nameplate capacity < 40 hp. This measure is not replacing drop‐line regulators or filter‐regulator lubricators.
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Operating Schedule*
Total Compressor Horsepower (>=40 HP)*
Manufacturer*
Model #*
Total Equipment Cost*
Annual kWh Savings | 0
Annual kW Savings | 0
Incentive | 0

## Low Pressure Drop Filters
Low Pressure Drop Filters |  | ELIGIBILITY The following protocol for the measurement of energy and demand savings applies to the installation of low pressure drop air filters for compressed air systems in commercial and industrial facilities. Low pressure drop filters remove solids and aerosols from compressed air systems with a longer life and lower pressure drop than standard coalescing filters, resulting in better efficiencies. The baseline condition is a standard coalescing filter with a pressure drop of 3 psi when new and 5 psi or more at element change. The efficient condition is a low pressure drop filter with pressure drop not exceeding 1 psi when new and 3 psi at element change.
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Quantity*
Operating Schedule*
Total Compressor Horsepower*
Manufacturer*
Model #*
Total Equipment Cost*
Annual kWh Savings | 0
Annual kW Savings | 0
Incentive | 0

## Mist Eliminators
Mist Eliminators |  | ELIGIBILITY The following protocol for the measurement of energy and demand savings applies to the installation of mist eliminator air filters for compressed air systems in commercial and industrial facilities. Large compressed air systems require air filtration for proper operation. These filters remove oil mist from the supply air of lubricated compressors, protecting the distribution system and end‐use devices. While these filters are important to the operation of the system, they do have a pressure drop across them, and thus require a slightly higher operating pressure. Typical coalescing oil filters will operate with a 2 psig to 10 psig pressure drop. Mist eliminator air filters operate at a 0.5 psig pressure drop that increases to 3 psig over time before replacement is recommended. | This reduction in pressure drop allows the compressed air system to operate at a reduced pressure and, in turn, reduces the energy consumption of the system. In general, the energy consumption will decrease by 1% for every 2 psig the operating pressure is reduced.Source 2 Lowering the operating pressure has the secondary benefit of decreasing the demand of all unregulated usage, such as leaks and open blowing. The equipment is mist eliminator air filters. The compressed air system must be greater than 50 HP to qualify, and the mist eliminator must have less than a 1 psig pressure drop and replace a coalescing filter. The baseline condition is a standard coalescing filter. The efficient condition is a mist eliminator air filter that replaces a standard coalescing filter. This protocol is not applicable for compressed air systems with total air compressor nameplate horsepower < 40 HP or mist eliminators with ≥ 1 psig pressure drop
Instructions: Enter the project information in the yellow cells below. Cells with a * are required. See Instructions Worksheet for more information.
Quantity*
Operating Schedule*
Total Compressor Horsepower*
Manufacturer*
Model #*
Total Equipment Cost*
Annual kWh Savings | 0
Annual kW Savings | 0
Incentive | 0

## Data Export (hidden)
Measure Type | Measure Code | Quantity | Per Unit Incentive | Non PPL Incentive Amount Received | Total PPL Incentive | Manufacturer | Model # | Nozzle Size | Compressor Control Type | Motor Rated Horsepower (HP) | Motor Type | ηmotor | Annual Run Hours of Motor (RHRS) | PSIG - Orifice Diameter | HVAC Fan/Pump Control Type | Total kW Savings | Total kWh savings | Facility schedule | Pressure | Space Type | Pump Type | Baseline Watts | Energy Efficient Watts
Prescriptive | ThermMassDryer | 0 | #DIV/0! |  | 0 | 0 | 0 |  |  | 0 | [5 empty] | 0 | 0 | 0
Prescriptive | ThermMassDryer | 1 | #DIV/0! |  | 0 | 0 | 0 |  |  | 0 | [5 empty] | 0 | 0 | 0
Prescriptive | ThermMassDryer | 1 | #DIV/0! |  | 0 | 0 | 0 |  |  | 0 | [5 empty] | 0 | 0 | 0
Prescriptive | ThermMassDryer | 0 | #DIV/0! |  | 0 | 0 | 0 |  |  | 0 | [5 empty] | 0 | 0 | 0
Prescriptive | ThermMassDryer | 0 | #DIV/0! |  | 0 | 0 | 0 |  |  | 0 | [5 empty] | 0 | 0 | 0

## Version Log (hidden)
Version Log
Original Author: |  | Alex Nissley | QA/QC Engineer(s): | Tom Cosgro, Engineering
Primary Developer: |  | Alex Nissley | Senior Engineer Approval: | Tom Cosgro, Engineering | Current Version: | 4.2
[5 empty] | Date Updated: | 2022-05-31
Version | Date | Reason for Change | Change Description | Contact, Department
1 | 2018-06-07 | Genesis | Created calculator tabs for MD Compressor from PA TRM | Alex Nissley
3 | 2018-11-30 | PPL Branding |  | Tom Cosgro, Engineering | Directions on updating this tool:
4 | 2021-06-01 | Update for Phase IV | Updated all measures to 2021 PA TRM 2/4/21 and Phase IV incentive structure. Created Data Export to enable import to DSMT. | Michael Stevenson, Engineering | These tools - Downstream and Direct Discount compressed air - were recently combined to help with version control and to create a QC lighting tool that would work with both calculators. If you are updating this tool, please follow the directions below: - Start by finding the most recent version of the Direct Discount calculator on Teams - Make the necessary updates to the Direct Discount tool first - Once updates are complete, update the Version Log with a new version number and description - Lock all tabs and workbook with PPLC@LC$ password and Save new Direct Discount version to Teams - Then, to update the Downstream calculator, take the new version of the Direct Discount calculator and hide the Printable Report - Change incentive rate on 'Calculations' tab to "Downstream" to update incentive rates and project cost caps - Lock all tabs and workbook with PPLC@LC$ password and Save new Downstream version to Teams - Email Angelique with copies of new calculators to be uploaded to the website Reach out to Nick Momenee or Conor McGrail with any questions.
4.1 | 2021-12-27 | 2022 Incentives | Updated to 2022 incentive levels | Conor McGrail, Engineering
4.2 | 2022-05-31 | Various updates | Combined DD and Downstream tools. Follow directions to the right for updating this tool. Added 6/1/22 incentive rate updates for DD Bug fixes on Air Nozzles Fixed orifice diameter to 1/8" on condensate drains | Conor McGrail, Engineering